## Model Inputs
No. | Type | Parameter | Value | Units | Description
1 | General Description | Site Location | MSD Brinny | - | Site reference
2 |  | Building | Building 21 | - | Building reference
3 |  | AHU | Multiple Combined | - | Air Handling Unit Reference
4 | Room | Room Area | 3000 | m2
5 |  | Room Height | 2.5 | m
7 | HVAC Modules | HVAC Module 1 | Mixing Box | -
8 |  | HVAC Module 2 | Cooling Coil | -
9 |  | HVAC Module 3 | Heating Coil | -
10 |  | HVAC Module 4 |  | -
11 |  | HVAC Module 5 |  | -
12 |  | HVAC Module 6 |  | -
13 |  | HVAC Module 7 |  | -
14 |  | HVAC Module 8 |  | -
15 |  | HVAC Module 9 |  | -
16 |  | HVAC Module 10 |  | -
17 | Air Flow | Supply Airflow | 27.787 | m3/s
18 |  | Return Airflow | 27.787 | m3/s
19 |  | Air Changes | 13.3378 |  | Air Changes per Hour calculated
21 | Mixing | Minimum Fresh Air Percentage | 30%
22 |  | Active Mixing | No |  | See Note 1
23 | Heat Recovery | Heat Recovery Efficiency (S) | 70% | Sensible | See Note 2
27 | Fan Power | Supply Fan Total Static Pressure | 1100 | Pascals | See Note 3
28 |  | Supply Fan Efficiency | 70% |  | See Note 4
29 |  | Return Fan Total Static Pressure | 900 | Pascals | See Note 3
30 |  | Return Fan Efficiency | 70% |  | See Note 4
31 | Settings | Preheat Temperature Setpoint - Tdb | 15 | oC dry bulb | See Note 5
34 |  | Average Cooling Coil Temperature - Tdb | 9 | oC dry bulb | See Note 6
40 | Setpoint no. 1 | Room Temperature Setpoint | 22 | The setpoint no. 1 values are applied to times where "1" is specified in the set point profile
41 |  | Room Temperature Lower Band | 20
42 |  | Room Temperature Upper Band | 24
43 |  | Room Humidity Setpoint | 50%
44 |  | Room Humidity Lower Band | 30%
45 |  | Room Humidity Upper Band | 100%
46 | Setpoint no. 2 | Room Temperature Setpoint |  | The setpoint no. 2 values are applied to times where "2" is specified in the set point profile
47 |  | Room Temperature Lower Band
48 |  | Room Temperature Upper Band
49 |  | Room Humidity Setpoint
50 |  | Room Humidity Lower Band
51 |  | Room Humidity Upper Band
52 | Setpoint no. 3 | Room Temperature Setpoint |  | The setpoint no. 3 values are applied to times where "3" is specified in the set point profile
53 |  | Room Temperature Lower Band
54 |  | Room Temperature Upper Band
55 |  | Room Humidity Setpoint
56 |  | Room Humidity Lower Band
57 |  | Room Humidity Upper Band
Notes
Note 1 | Active mixing is a function only applicable when a mixing box is specified, if active mixing is set to yes the mixing box will modulate between the minimum fresh air % and 100% fresh air
Note 2 | Where heat recovery is specified the efficiency of the heat recovery must be specified. Typical values are as follows, thermal wheel = 79%, plate heat exchanger = 79%, run arund coils = 69%
Note 3 | The fan total static pressure is the system total static pressure i.e. total static pressure = (the pressure drop in the AHU + pressure drop of the ductwork)
Note 4 | The fan efficiency is used with the pressure drop to estimate fan power. A typical fan efficiency would be 70%
Note 5 | Where a preheat coil is specified as a module in the system this is the temperature to which the preheat coil will preheat
Note 6 | Used to determine the Apparatus dew point, this will be the average coil temperature i.e. chilled water flow 6oC and chilled water return 6oC would result in an average coil temperature of 9oC
Note 7
Note 8
Note 9
Note 10
List
Blank
Thermal Wheel
Mixing Box
Run Around Coil
Plate Heat Exchanger
Preheating Coil
Heating Coil
Cooling Coil
Humidifier (Steam)
Humidifier (Spray)

## Weather Data
Location |  | Cork Airport
Hour | Dry_Bulb_Temperature(°C) | Relative_Humidity(%)
1 | 8.5 | 0.81
2 | 8.5 | 0.81
3 | 8.4 | 0.83
4 | 8.5 | 0.75
5 | 8.5 | 0.75
6 | 8.2 | 0.78
7 | 8 | 0.78
8 | 7.9 | 0.76
9 | 8 | 0.74
10 | 7.9 | 0.78
11 | 8 | 0.75
12 | 8.2 | 0.77
13 | 8.4 | 0.75
14 | 8.4 | 0.77
15 | 8.5 | 0.75
16 | 8.3 | 0.78
17 | 8.3 | 0.78
18 | 8.1 | 0.81
19 | 8.1 | 0.79
20 | 8.1 | 0.78
21 | 8 | 0.8
22 | 7.8 | 0.82
23 | 7.6 | 0.87
24 | 7.3 | 0.93
25 | 7.5 | 0.97
26 | 7.3 | 0.97
27 | 7.3 | 0.97
28 | 7.2 | 0.97
29 | 7 | 0.97
30 | 7 | 0.99
31 | 7.2 | 0.99
32 | 7 | 1
33 | 6.9 | 0.99
34 | 7 | 1
35 | 7.3 | 1
36 | 7.2 | 0.99
37 | 7.2 | 1
38 | 7 | 0.99
39 | 6.7 | 0.97
40 | 6.6 | 0.97
41 | 6.9 | 0.88
42 | 6.4 | 0.91
43 | 6.8 | 0.87
44 | 6.9 | 0.88
45 | 6.9 | 0.91
46 | 6.6 | 0.94
47 | 6.8 | 0.93
48 | 6.6 | 0.95
49 | 6.3 | 0.98
50 | 6.5 | 0.98
51 | 6.4 | 0.97
52 | 6.7 | 0.97
53 | 7.4 | 0.99
54 | 7.2 | 0.97
55 | 7.2 | 0.99
56 | 7.2 | 0.97
57 | 7.2 | 0.97
58 | 7.4 | 0.93
59 | 7.3 | 0.88
60 | 7.4 | 0.84
61 | 7.4 | 0.8
62 | 7.4 | 0.79
63 | 7.1 | 0.75
64 | 6.6 | 0.76
65 | 6.6 | 0.79
66 | 6.7 | 0.79
67 | 6.8 | 0.77
68 | 6.7 | 0.78
69 | 6.6 | 0.76
70 | 6.4 | 0.75
71 | 6.5 | 0.76
72 | 6.5 | 0.76
73 | 6.4 | 0.75
74 | 6.5 | 0.78
75 | 6.4 | 0.78
76 | 6.4 | 0.78
77 | 6.3 | 0.75
78 | 6.4 | 0.76
79 | 6.2 | 0.8
80 | 6.4 | 0.76
81 | 6.6 | 0.72
82 | 6.3 | 0.82
83 | 6.4 | 0.85
84 | 6.9 | 0.77
85 | 7.3 | 0.77
86 | 7.4 | 0.73
87 | 7.4 | 0.8
88 | 7.2 | 0.8
89 | 6.7 | 0.76
90 | 6.4 | 0.76
91 | 6.2 | 0.8
92 | 6.2 | 0.8
93 | 6.1 | 0.79
94 | 6.3 | 0.8
95 | 6.3 | 0.79
96 | 6.3 | 0.79
97 | 6.3 | 0.8
98 | 6.2 | 0.82
99 | 6.4 | 0.81
100 | 6.4 | 0.81
101 | 6.4 | 0.82
102 | 6.5 | 0.84
103 | 6.6 | 0.76
104 | 6.9 | 0.82
105 | 6.9 | 0.81
106 | 7.1 | 0.81
107 | 7.4 | 0.8
108 | 7.7 | 0.79
109 | 7.9 | 0.82
110 | 8.1 | 0.81
111 | 8.3 | 0.83
112 | 8.2 | 0.86
113 | 8.2 | 0.87
114 | 8 | 0.89
115 | 8 | 0.89
116 | 8 | 0.9
117 | 8.1 | 0.92
118 | 8.1 | 0.93
119 | 8.1 | 0.93
120 | 8.2 | 0.92
121 | 8.1 | 0.92
122 | 8 | 0.92
123 | 8.1 | 0.86
124 | 8.3 | 0.83
125 | 8 | 0.86
126 | 8.1 | 0.86
127 | 8.2 | 0.86
128 | 8 | 0.87
129 | 7.9 | 0.9
130 | 7.1 | 0.91
131 | 7.8 | 0.93
132 | 9 | 0.89
133 | 9.5 | 0.89
134 | 9.7 | 0.89
135 | 9.9 | 0.88
136 | 9.7 | 0.91
137 | 9.6 | 0.91
138 | 9.1 | 0.91
139 | 8.9 | 0.93
140 | 8.9 | 0.9
141 | 8.7 | 0.9
142 | 8.3 | 0.92
143 | 8.6 | 0.93
144 | 8.9 | 0.93
145 | 9.1 | 0.99
146 | 9.3 | 0.99
147 | 9.4 | 1
148 | 9.6 | 1
149 | 9.8 | 1
150 | 9.5 | 0.97
151 | 9.8 | 0.97
152 | 9.9 | 0.95
153 | 9.9 | 0.92
154 | 9.9 | 0.87
155 | 10 | 0.87
156 | 10.1 | 0.86
157 | 10 | 0.82
158 | 10.1 | 0.81
159 | 10.2 | 0.82
160 | 10.1 | 0.84
161 | 10.4 | 0.85
162 | 10.3 | 0.86
163 | 10.2 | 0.88
164 | 10.5 | 0.9
165 | 10.5 | 0.91
166 | 10.5 | 0.92
167 | 10.9 | 0.9
168 | 10.9 | 0.9
169 | 10.1 | 0.93
170 | 9.4 | 0.95
171 | 8.8 | 0.92
172 | 8.1 | 0.89
173 | 7.9 | 0.91
174 | 8 | 0.9
175 | 7.9 | 0.9
176 | 7.8 | 0.9
177 | 7.8 | 0.89
178 | 7.9 | 0.87
179 | 7.8 | 0.87
180 | 8.2 | 0.86
181 | 8.2 | 0.86
182 | 8.6 | 0.84
183 | 8.9 | 0.82
184 | 8.8 | 0.78
185 | 8.8 | 0.8
186 | 8.1 | 0.83
187 | 7.6 | 0.87
188 | 7.3 | 0.9
189 | 7.6 | 0.91
190 | 7.5 | 0.93
191 | 7.6 | 0.91
192 | 7.7 | 0.91
193 | 7.8 | 0.97
194 | 7.8 | 0.99
195 | 7.9 | 0.99
196 | 8 | 0.99
197 | 7.9 | 1
198 | 7.8 | 1
199 | 7.9 | 0.99
200 | 8.6 | 1
201 | 9 | 0.99
202 | 9.2 | 0.97
203 | 9.3 | 0.97
204 | 9.3 | 0.99
205 | 9.4 | 0.99
206 | 9.7 | 0.99
207 | 10 | 1
208 | 10.2 | 0.99
209 | 9.5 | 0.99
210 | 9.6 | 0.99
211 | 9.1 | 1
212 | 8.4 | 0.99
213 | 8.5 | 1
214 | 8.4 | 1
215 | 8.2 | 1
216 | 8.1 | 1
217 | 8.3 | 1
218 | 8.3 | 1
219 | 8.5 | 1
220 | 8.8 | 1
221 | 8.8 | 1
222 | 9.1 | 1
223 | 8.9 | 1
224 | 8.7 | 1
225 | 8.7 | 0.99
226 | 8.9 | 0.99
227 | 9.1 | 0.99
228 | 9.2 | 0.99
229 | 9.8 | 0.97
230 | 10 | 0.92
231 | 9.9 | 0.96
232 | 10.5 | 0.91
233 | 10.6 | 0.9
234 | 10.2 | 0.91
235 | 9.7 | 0.92
236 | 9.3 | 0.96
237 | 9.1 | 0.96
238 | 8.9 | 0.97
239 | 8.9 | 0.97
240 | 8.9 | 0.99
241 | 8.9 | 0.96
242 | 8.8 | 0.97
243 | 8.6 | 0.97
244 | 8.6 | 0.97
245 | 8.5 | 0.99
246 | 8.6 | 0.96
247 | 8.6 | 0.97
248 | 8 | 0.97
249 | 8.2 | 0.97
250 | 8.4 | 0.96
251 | 8.7 | 0.94
252 | 9.2 | 0.92
253 | 9.2 | 0.91
254 | 10.2 | 0.83
255 | 9.8 | 0.87
256 | 9.6 | 0.85
257 | 9.6 | 0.85
258 | 9.3 | 0.88
259 | 8.7 | 0.92
260 | 8.4 | 0.93
261 | 8.3 | 0.92
262 | 8.3 | 0.92
263 | 7.8 | 0.97
264 | 8.3 | 0.92
265 | 8.1 | 0.94
266 | 7.8 | 0.94
267 | 7.9 | 0.94
268 | 8.4 | 0.94
269 | 8.2 | 0.97
270 | 8.6 | 0.97
271 | 9 | 0.96
272 | 8.6 | 0.93
273 | 8.1 | 0.87
274 | 7.9 | 0.84
275 | 8.3 | 0.86
276 | 9.1 | 0.84
277 | 9.1 | 0.88
278 | 9.5 | 0.87
279 | 9.6 | 0.85
280 | 9.7 | 0.87
281 | 9.5 | 0.88
282 | 9.2 | 0.92
283 | 9.2 | 0.91
284 | 8.7 | 0.92
285 | 8.7 | 0.92
286 | 8.7 | 0.93
287 | 8.8 | 0.92
288 | 8.6 | 0.92
289 | 8.6 | 0.85
290 | 8 | 0.86
291 | 8.1 | 0.86
292 | 7.8 | 0.89
293 | 8.4 | 0.85
294 | 8.6 | 0.84
295 | 8.4 | 0.86
296 | 8 | 0.87
297 | 8.8 | 0.84
298 | 8.2 | 0.86
299 | 8.2 | 0.86
300 | 9.1 | 0.84
301 | 9.8 | 0.84
302 | 10.6 | 0.85
303 | 10.4 | 0.87
304 | 10.6 | 0.87
305 | 10.6 | 0.82
306 | 9.8 | 0.87
307 | 9.6 | 0.84
308 | 9.4 | 0.79
309 | 9.1 | 0.76
310 | 8.1 | 0.76
311 | 8.1 | 0.72
312 | 7.9 | 0.75
313 | 7.7 | 0.71
314 | 7.8 | 0.72
315 | 7.8 | 0.71
316 | 7.7 | 0.75
317 | 7.4 | 0.79
318 | 7.3 | 0.8
319 | 7.5 | 0.74
320 | 7.3 | 0.76
321 | 6.3 | 0.79
322 | 4.6 | 0.87
323 | 6.6 | 0.82
324 | 7.7 | 0.77
325 | 8 | 0.76
326 | 8.3 | 0.74
327 | 8.5 | 0.71
328 | 8.4 | 0.74
329 | 8 | 0.79
330 | 7.6 | 0.84
331 | 6.6 | 0.88
332 | 7.3 | 0.9
333 | 7.3 | 0.93
334 | 7.5 | 0.99
335 | 7.6 | 1
336 | 7.3 | 1
337 | 6.1 | 0.98
338 | 5.1 | 0.98
339 | 6.5 | 1
340 | 7 | 1
341 | 7 | 1
342 | 6.9 | 1
343 | 6 | 0.98
344 | 6.2 | 1
345 | 7 | 1
346 | 7 | 1
347 | 7.3 | 1
348 | 7.8 | 0.99
349 | 8.5 | 0.97
350 | 9 | 0.93
351 | 8.9 | 0.92
352 | 8.9 | 0.95
353 | 8.5 | 0.96
354 | 8.2 | 0.93
355 | 7.9 | 0.94
356 | 7.9 | 0.94
357 | 8.3 | 0.96
358 | 8.4 | 0.99
359 | 8.2 | 0.97
360 | 8.2 | 0.97
361 | 7.3 | 0.99
362 | 7.8 | 0.97
363 | 8.1 | 0.97
364 | 5.3 | 0.97
365 | 4.8 | 0.95
366 | 4.7 | 0.97
367 | 4.9 | 0.94
368 | 4.5 | 0.97
369 | 4.5 | 0.93
370 | 2.9 | 0.96
371 | 3.9 | 0.97
372 | 5.7 | 0.88
373 | 6.7 | 0.81
374 | 7.5 | 0.77
375 | 7.2 | 0.77
376 | 7.2 | 0.73
377 | 5.7 | 0.88
378 | 4.8 | 0.86
379 | 4.4 | 0.87
380 | 3.8 | 0.85
381 | 3.5 | 0.83
382 | 3.3 | 0.85
383 | 3.3 | 0.88
384 | 4.2 | 0.85
385 | 4.2 | 0.85
386 | 5 | 0.81
387 | 5.5 | 0.83
388 | 4.9 | 0.81
389 | 3.8 | 0.82
390 | 3.7 | 0.8
391 | 2.7 | 0.84
392 | 1.8 | 0.85
393 | 1.8 | 0.83
394 | 1.2 | 0.85
395 | 2.1 | 0.75
396 | 2.7 | 0.75
397 | 3 | 0.76
398 | 4.2 | 0.71
399 | 4.8 | 0.65
400 | 3.9 | 0.73
401 | 3.2 | 0.78
402 | 2.5 | 0.8
403 | 2.4 | 0.77
404 | 2.7 | 0.77
405 | 3.4 | 0.73
406 | 3.8 | 0.77
407 | 4.4 | 0.8
408 | 4.9 | 0.84
409 | 5 | 0.9
410 | 5.2 | 0.98
411 | 6 | 0.98
412 | 6.7 | 0.98
413 | 7.3 | 0.99
414 | 6 | 0.98
415 | 4 | 0.97
416 | 3.6 | 0.97
417 | 2.8 | 1
418 | 2.9 | 0.98
419 | 4.9 | 0.97
420 | 6.6 | 0.94
421 | 7.5 | 0.91
422 | 7.5 | 0.88
423 | 7.4 | 0.88
424 | 6.8 | 0.93
425 | 7 | 0.91
426 | 6.8 | 0.96
427 | 6.6 | 0.94
428 | 6.2 | 0.95
429 | 6 | 0.95
430 | 5.7 | 0.95
431 | 5.5 | 0.95
432 | 4.9 | 0.95
433 | 4.5 | 0.97
434 | 4.5 | 0.97
435 | 4.8 | 0.98
436 | 4.7 | 0.97
437 | 4.6 | 0.97
438 | 4.9 | 0.95
439 | 4.7 | 0.95
440 | 4.6 | 0.97
441 | 4.4 | 0.97
442 | 4.1 | 0.98
443 | 4.6 | 0.95
444 | 6.1 | 0.91
445 | 7.1 | 0.88
446 | 7.8 | 0.87
447 | 7.4 | 0.88
448 | 7.9 | 0.87
449 | 8.1 | 0.85
450 | 7.6 | 0.9
451 | 7.1 | 0.97
452 | 6.8 | 0.94
453 | 6.6 | 0.94
454 | 6.3 | 0.94
455 | 6.4 | 0.95
456 | 6.3 | 0.97
457 | 6.3 | 0.95
458 | 6.5 | 0.94
459 | 6.6 | 0.98
460 | 6.5 | 0.94
461 | 6.4 | 0.95
462 | 6.7 | 0.97
463 | 6.8 | 0.99
464 | 6.4 | 0.95
465 | 6.1 | 0.94
466 | 6 | 0.86
467 | 5.9 | 0.83
468 | 6.6 | 0.76
469 | 6.6 | 0.78
470 | 6.7 | 0.75
471 | 7.1 | 0.73
472 | 6.8 | 0.72
473 | 6.4 | 0.72
474 | 5.3 | 0.77
475 | 4.9 | 0.75
476 | 4.8 | 0.76
477 | 3.7 | 0.8
478 | 2.8 | 0.84
479 | 2.5 | 0.87
480 | 2.4 | 0.87
481 | 2.1 | 0.89
482 | 2.1 | 0.87
483 | 1.4 | 0.91
484 | 1.3 | 0.89
485 | 2.1 | 0.84
486 | 2.6 | 0.81
487 | 1.6 | 0.85
488 | 0.5 | 0.88
489 | 0.6 | 0.9
490 | 1.2 | 0.94
491 | 3.2 | 0.88
492 | 4.9 | 0.87
493 | 5.3 | 0.91
494 | 6.1 | 0.92
495 | 6.5 | 0.88
496 | 6.3 | 0.92
497 | 6.4 | 0.95
498 | 5.3 | 0.89
499 | 3.9 | 0.9
500 | 3.7 | 0.83
501 | 3.4 | 0.76
502 | 2.9 | 0.81
503 | 1.9 | 0.91
504 | 1.5 | 0.94
505 | 2 | 0.93
506 | 1.1 | 0.92
507 | 0.8 | 0.92
508 | 0.2 | 0.88
509 | 1 | 0.9
510 | 1.3 | 0.91
511 | 2.1 | 0.91
512 | 1.5 | 0.94
513 | 1.6 | 0.94
514 | 1.2 | 0.96
515 | 1.8 | 0.96
516 | 2.9 | 0.91
517 | 3.7 | 0.92
518 | 3.7 | 0.92
519 | 4.2 | 0.92
520 | 3.9 | 0.92
521 | 3.9 | 0.9
522 | 3.8 | 0.93
523 | 4.1 | 0.93
524 | 4 | 0.95
525 | 3.9 | 0.93
526 | 4.1 | 0.92
527 | 3.7 | 0.9
528 | 4.3 | 0.87
529 | 3.6 | 0.9
530 | 4.3 | 0.87
531 | 4.4 | 0.87
532 | 4.1 | 0.9
533 | 4 | 0.87
534 | 3.8 | 0.88
535 | 4.1 | 0.87
536 | 4.1 | 0.83
537 | 4.1 | 0.85
538 | 4.6 | 0.85
539 | 5.1 | 0.86
540 | 5.6 | 0.84
541 | 6.1 | 0.86
542 | 6.3 | 0.92
543 | 6.1 | 0.95
544 | 6 | 0.98
545 | 6.6 | 0.98
546 | 6.4 | 0.98
547 | 6.3 | 0.98
548 | 6.3 | 0.98
549 | 6.4 | 1
550 | 6.8 | 0.99
551 | 6.7 | 1
552 | 6.7 | 1
553 | 8.7 | 1
554 | 8.9 | 0.97
555 | 9.1 | 0.97
556 | 9.3 | 0.95
557 | 9.1 | 0.97
558 | 9.1 | 0.95
559 | 8.9 | 0.99
560 | 9.1 | 0.97
561 | 9.3 | 0.97
562 | 9.5 | 0.99
563 | 9.7 | 0.83
564 | 9.7 | 0.89
565 | 10.3 | 0.91
566 | 10.1 | 0.93
567 | 10.4 | 0.91
568 | 10.6 | 0.87
569 | 10.2 | 0.87
570 | 9.8 | 0.93
571 | 9.9 | 0.93
572 | 10 | 0.92
573 | 9.8 | 0.92
574 | 9.7 | 0.91
575 | 9.8 | 0.89
576 | 9.7 | 0.88
577 | 9.6 | 0.91
578 | 9.7 | 0.91
579 | 9.4 | 0.92
580 | 9.5 | 0.91
581 | 9.5 | 0.89
582 | 9.2 | 0.92
583 | 8.5 | 0.93
584 | 9.1 | 0.89
585 | 8.8 | 0.93
586 | 8.5 | 0.97
587 | 8.6 | 0.97
588 | 9.2 | 0.91
589 | 9.5 | 0.88
590 | 10.2 | 0.82
591 | 10.5 | 0.8
592 | 10.4 | 0.78
593 | 9.6 | 0.83
594 | 8.7 | 0.89
595 | 7.7 | 0.94
596 | 7.1 | 0.93
597 | 7.3 | 0.9
598 | 5.5 | 0.95
599 | 6.6 | 0.95
600 | 6.3 | 0.98
601 | 7.1 | 0.99
602 | 7.7 | 1
603 | 8.1 | 1
604 | 8 | 0.99
605 | 7.8 | 0.97
606 | 7.7 | 0.97
607 | 7.9 | 0.97
608 | 8.2 | 0.96
609 | 8.5 | 0.97
610 | 8.9 | 0.97
611 | 9.5 | 0.96
612 | 8.6 | 0.97
613 | 8.5 | 0.86
614 | 8.2 | 0.82
615 | 7.8 | 0.91
616 | 8.3 | 0.89
617 | 8.4 | 0.81
618 | 7.7 | 0.87
619 | 7.5 | 0.9
620 | 7.5 | 0.87
621 | 7.7 | 0.86
622 | 7.4 | 0.86
623 | 6.2 | 0.79
624 | 5.4 | 0.78
625 | 4 | 0.87
626 | 4 | 0.72
627 | 3.9 | 0.67
628 | 3.6 | 0.7
629 | 3.4 | 0.71
630 | 3.2 | 0.71
631 | 3.2 | 0.73
632 | 3.5 | 0.68
633 | 3.2 | 0.73
634 | 3.5 | 0.75
635 | 3.8 | 0.78
636 | 4.8 | 0.74
637 | 5.9 | 0.71
638 | 6.2 | 0.67
639 | 5.5 | 0.77
640 | 5.3 | 0.8
641 | 4.8 | 0.81
642 | 4.2 | 0.87
643 | 3.8 | 0.9
644 | 3.3 | 0.97
645 | 3.1 | 0.96
646 | 3.1 | 0.96
647 | 3.1 | 0.98
648 | 3.1 | 0.98
649 | 3.2 | 1
650 | 3.9 | 0.97
651 | 5.2 | 0.95
652 | 5.4 | 0.87
653 | 5.2 | 0.83
654 | 4.9 | 0.86
655 | 4.9 | 0.84
656 | 5.2 | 0.86
657 | 5.6 | 0.81
658 | 6 | 0.82
659 | 5.8 | 0.89
660 | 5.3 | 0.83
661 | 5.2 | 0.83
662 | 5.6 | 0.77
663 | 5.8 | 0.76
664 | 5.7 | 0.85
665 | 5.7 | 0.83
666 | 4.3 | 0.87
667 | 2.6 | 0.93
668 | 3 | 0.88
669 | 2.9 | 0.88
670 | 3 | 0.88
671 | 3.8 | 0.85
672 | 4 | 0.85
673 | 3.4 | 0.91
674 | 3.7 | 0.9
675 | 3.3 | 0.97
676 | 3.2 | 0.97
677 | 3.1 | 0.96
678 | 3.1 | 0.98
679 | 2.8 | 0.98
680 | 2.5 | 0.96
681 | 2.6 | 0.93
682 | 2.1 | 0.93
683 | 2.2 | 0.93
684 | 2.8 | 0.84
685 | 1.1 | 0.94
686 | 3.1 | 0.79
687 | 1.3 | 0.92
688 | 2.4 | 0.82
689 | 2.3 | 0.78
690 | 0 | 0.98
691 | 0.2 | 0.96
692 | 0.1 | 0.96
693 | 0.1 | 0.98
694 | -0.1 | 0.98
695 | -0.7 | 0.98
696 | 0 | 0.98
697 | -1.8 | 0.98
698 | -1.1 | 0.96
699 | -0.8 | 0.96
700 | -0.5 | 0.98
701 | -1.1 | 0.96
702 | -0.5 | 0.96
703 | -0.2 | 0.96
704 | -0.5 | 0.96
705 | -0.2 | 0.96
706 | 0.3 | 0.92
707 | 0.5 | 0.9
708 | 1.4 | 0.89
709 | 1.5 | 0.87
710 | 2.2 | 0.87
711 | 2.6 | 0.82
712 | 3.4 | 0.8
713 | 3.1 | 0.84
714 | 2.7 | 0.81
715 | 1 | 0.88
716 | 0 | 0.92
717 | -0.1 | 0.94
718 | -0.1 | 0.94
719 | -0.3 | 0.92
720 | 0.5 | 0.92
721 | 1.5 | 0.89
722 | 1.4 | 0.89
723 | 2.3 | 0.87
724 | 2.5 | 0.87
725 | 3.2 | 0.86
726 | 3.5 | 0.88
727 | 3.8 | 0.9
728 | 3.9 | 0.9
729 | 4 | 0.93
730 | 3.8 | 0.97
731 | 3.8 | 0.95
732 | 3.6 | 0.97
733 | 4.7 | 0.92
734 | 5.9 | 0.86
735 | 4.6 | 0.9
736 | 6 | 0.7
737 | 5.2 | 0.7
738 | 3.6 | 0.75
739 | 2.7 | 0.82
740 | 2.5 | 0.95
741 | 2.7 | 0.96
742 | 3.1 | 0.96
743 | 2.8 | 0.96
744 | 2.6 | 0.98
745 | 4.1 | 0.92
746 | 0.5 | 0.98
747 | 1.2 | 0.96
748 | 1.1 | 0.94
749 | 0.9 | 0.9
750 | 0.9 | 0.9
751 | 0.8 | 0.9
752 | 0.7 | 0.82
753 | 0.3 | 0.86
754 | 0.5 | 0.82
755 | 1.3 | 0.79
756 | 1.8 | 0.74
757 | 1.9 | 0.76
758 | 2.2 | 0.78
759 | 3.2 | 0.73
760 | 3.5 | 0.66
761 | 2.8 | 0.7
762 | 2 | 0.73
763 | 1.2 | 0.75
764 | 1 | 0.77
765 | 0.8 | 0.79
766 | 0.8 | 0.79
767 | 0.5 | 0.8
768 | 0.8 | 0.79
769 | 1 | 0.75
770 | -0.1 | 0.82
771 | -0.1 | 0.84
772 | -0.4 | 0.86
773 | -0.1 | 0.84
774 | -0.2 | 0.84
775 | -0.1 | 0.82
776 | -0.4 | 0.84
777 | 0.2 | 0.78
778 | 0.3 | 0.76
779 | 1.4 | 0.74
780 | 3.2 | 0.73
781 | 4.3 | 0.71
782 | 5.1 | 0.7
783 | 5.7 | 0.68
784 | 4.6 | 0.74
785 | 4.5 | 0.74
786 | 4 | 0.78
787 | 2.2 | 0.87
788 | 2.4 | 0.84
789 | 2 | 0.84
790 | 2.3 | 0.84
791 | 2.1 | 0.82
792 | 2.3 | 0.82
793 | 1.7 | 0.85
794 | 1.6 | 0.87
795 | 1.3 | 0.91
796 | 1.5 | 0.92
797 | 1.9 | 0.93
798 | 2.1 | 0.95
799 | 3.1 | 0.93
800 | 2.8 | 0.96
801 | 3.3 | 0.95
802 | 4.1 | 0.93
803 | 5.6 | 0.88
804 | 7.7 | 0.84
805 | 8.7 | 0.77
806 | 8.5 | 0.78
807 | 8.4 | 0.78
808 | 8.3 | 0.82
809 | 8.1 | 0.86
810 | 8.1 | 0.86
811 | 7.9 | 0.89
812 | 7.7 | 0.96
813 | 7.8 | 0.99
814 | 7.6 | 0.99
815 | 8.1 | 0.99
816 | 8.9 | 1
817 | 9.3 | 1
818 | 9 | 1
819 | 8.7 | 1
820 | 8.6 | 0.94
821 | 8 | 0.87
822 | 7.4 | 0.9
823 | 7.2 | 0.87
824 | 6.7 | 0.87
825 | 6.1 | 0.88
826 | 5.8 | 0.88
827 | 7.5 | 0.79
828 | 8.3 | 0.79
829 | 8.9 | 0.77
830 | 9.4 | 0.7
831 | 10.2 | 0.66
832 | 10.1 | 0.63
833 | 9.8 | 0.68
834 | 6.2 | 0.89
835 | 5.6 | 0.92
836 | 4.8 | 0.95
837 | 4.6 | 0.97
838 | 3.6 | 0.97
839 | 3.7 | 0.97
840 | 6.2 | 0.95
841 | 6.7 | 0.93
842 | 6.9 | 0.93
843 | 7.1 | 0.97
844 | 7.3 | 0.99
845 | 7.4 | 1
846 | 7.7 | 1
847 | 8.5 | 1
848 | 9.4 | 0.99
849 | 9.7 | 1
850 | 10 | 1
851 | 10.4 | 1
852 | 10.4 | 1
853 | 10.6 | 1
854 | 10.6 | 1
855 | 10.8 | 0.99
856 | 10.8 | 0.99
857 | 9.2 | 0.95
858 | 9.4 | 0.92
859 | 7.9 | 0.89
860 | 6.1 | 0.91
861 | 5.4 | 0.87
862 | 3.2 | 0.93
863 | 2.7 | 0.93
864 | 3 | 0.91
865 | 2.7 | 0.91
866 | 2.5 | 0.95
867 | 3.3 | 0.91
868 | 3.3 | 0.93
869 | 4.8 | 0.92
870 | 5.3 | 0.92
871 | 6.6 | 0.91
872 | 6.1 | 0.89
873 | 6.7 | 0.9
874 | 6.6 | 0.91
875 | 7.4 | 0.9
876 | 8.8 | 0.85
877 | 9.1 | 0.8
878 | 9.5 | 0.78
879 | 9 | 0.88
880 | 9 | 0.86
881 | 8.1 | 0.87
882 | 7.9 | 0.93
883 | 7.6 | 0.91
884 | 7.2 | 0.94
885 | 6.7 | 0.94
886 | 5.4 | 0.95
887 | 2.3 | 0.91
888 | 3.2 | 0.9
889 | 3 | 0.89
890 | 3.5 | 0.86
891 | 3.7 | 0.88
892 | 2.6 | 0.96
893 | 3.9 | 0.85
894 | 2.7 | 0.91
895 | 4.1 | 0.85
896 | 3.6 | 0.88
897 | 3.6 | 0.88
898 | 3.7 | 0.88
899 | 4.7 | 0.85
900 | 6.1 | 0.82
901 | 6.6 | 0.82
902 | 6.9 | 0.82
903 | 7 | 0.8
904 | 6.6 | 0.87
905 | 6.7 | 0.91
906 | 7.3 | 0.88
907 | 7 | 0.96
908 | 7.3 | 0.99
909 | 8 | 0.99
910 | 8.4 | 0.94
911 | 8.5 | 0.96
912 | 8.5 | 0.97
913 | 8.8 | 0.97
914 | 8.9 | 0.95
915 | 9.1 | 0.97
916 | 9.3 | 0.97
917 | 9.6 | 0.99
918 | 9.7 | 0.99
919 | 9.8 | 0.96
920 | 8.9 | 0.9
921 | 7.8 | 0.8
922 | 7.3 | 0.83
923 | 7.2 | 0.85
924 | 8.5 | 0.78
925 | 8 | 0.76
926 | 8.7 | 0.74
927 | 8.8 | 0.74
928 | 7.6 | 0.77
929 | 6.2 | 0.83
930 | 5.9 | 0.79
931 | 6.1 | 0.77
932 | 5.7 | 0.75
933 | 5.1 | 0.78
934 | 4.7 | 0.76
935 | 5.2 | 0.66
936 | 4.8 | 0.65
937 | 3.9 | 0.83
938 | 4.8 | 0.73
939 | 5.3 | 0.64
940 | 5.1 | 0.72
941 | 5.4 | 0.63
942 | 4.9 | 0.72
943 | 5.4 | 0.63
944 | 5 | 0.76
945 | 5 | 0.73
946 | 5.7 | 0.74
947 | 5.8 | 0.73
948 | 7.6 | 0.72
949 | 7.5 | 0.77
950 | 7.9 | 0.75
951 | 7.2 | 0.77
952 | 7.4 | 0.81
953 | 6.4 | 0.81
954 | 5.2 | 0.83
955 | 2.8 | 0.91
956 | 2.7 | 0.95
957 | 2.8 | 0.96
958 | 4.4 | 0.87
959 | 3.8 | 0.9
960 | 3.4 | 0.91
961 | 2.6 | 0.91
962 | 2.8 | 0.95
963 | 2.9 | 0.93
964 | 2.4 | 0.91
965 | 2.8 | 0.91
966 | 3 | 0.88
967 | 2.9 | 0.88
968 | 2.5 | 0.87
969 | 2.8 | 0.86
970 | 3 | 0.84
971 | 3.9 | 0.8
972 | 3.1 | 0.88
973 | 4.1 | 0.87
974 | 5.8 | 0.8
975 | 6.6 | 0.69
976 | 6.2 | 0.64
977 | 5.9 | 0.71
978 | 6 | 0.64
979 | 5.5 | 0.66
980 | 4.8 | 0.68
981 | 5.4 | 0.68
982 | 5.9 | 0.67
983 | 6.2 | 0.69
984 | 6.5 | 0.75
985 | 6.4 | 0.81
986 | 6.2 | 0.83
987 | 6 | 0.86
988 | 6.1 | 0.86
989 | 5.9 | 0.88
990 | 5.6 | 0.86
991 | 5.8 | 0.83
992 | 4.5 | 0.87
993 | 5.1 | 0.84
994 | 5.2 | 0.83
995 | 6.2 | 0.79
996 | 6.9 | 0.8
997 | 8 | 0.76
998 | 8.9 | 0.77
999 | 9.3 | 0.79
1000 | 9.3 | 0.83
1001 | 8.9 | 0.86
1002 | 8.4 | 0.9
1003 | 7.8 | 0.94
1004 | 7.2 | 0.96
1005 | 7.1 | 0.97
1006 | 7.5 | 0.97
1007 | 8.1 | 0.96
1008 | 8.4 | 0.96
1009 | 8.6 | 0.96
1010 | 8.7 | 0.93
1011 | 8 | 0.97
1012 | 8.2 | 0.97
1013 | 8.2 | 0.99
1014 | 8.4 | 0.99
1015 | 8.7 | 0.99
1016 | 8.9 | 1
1017 | 9.1 | 1
1018 | 9.2 | 1
1019 | 9.6 | 0.99
1020 | 9.5 | 0.97
1021 | 9.8 | 0.99
1022 | 9.9 | 0.99
1023 | 9.9 | 0.99
1024 | 10 | 1
1025 | 9.8 | 0.99
1026 | 9.6 | 1
1027 | 9.4 | 0.99
1028 | 9.3 | 0.99
1029 | 9.1 | 0.99
1030 | 9 | 0.99
1031 | 8.9 | 0.99
1032 | 8.9 | 0.97
1033 | 8.8 | 0.95
1034 | 8.8 | 0.95
1035 | 8.7 | 0.93
1036 | 8.5 | 0.93
1037 | 8.5 | 0.93
1038 | 8.6 | 0.96
1039 | 8.6 | 0.93
1040 | 8.6 | 0.93
1041 | 8.6 | 0.92
1042 | 8.8 | 0.93
1043 | 9.1 | 0.91
1044 | 9.2 | 0.89
1045 | 9.4 | 0.89
1046 | 9.5 | 0.88
1047 | 9.5 | 0.88
1048 | 9.3 | 0.91
1049 | 9.3 | 0.89
1050 | 9 | 0.89
1051 | 8.6 | 0.92
1052 | 8.8 | 0.9
1053 | 8.7 | 0.9
1054 | 8.5 | 0.93
1055 | 8.8 | 0.9
1056 | 8.7 | 0.9
1057 | 8.6 | 0.92
1058 | 8.9 | 0.89
1059 | 8.9 | 0.89
1060 | 8.8 | 0.88
1061 | 8.9 | 0.89
1062 | 8.8 | 0.86
1063 | 8.6 | 0.89
1064 | 8.5 | 0.9
1065 | 8.3 | 0.92
1066 | 8.3 | 0.9
1067 | 8.5 | 0.88
1068 | 8.5 | 0.9
1069 | 8.5 | 0.89
1070 | 8.5 | 0.9
1071 | 8.6 | 0.92
1072 | 8.6 | 0.9
1073 | 8.5 | 0.92
1074 | 8.1 | 0.93
1075 | 7.9 | 0.93
1076 | 7.7 | 0.94
1077 | 7.7 | 0.93
1078 | 7.5 | 0.91
1079 | 7.4 | 0.93
1080 | 7.4 | 0.93
1081 | 7.5 | 0.96
1082 | 7.8 | 0.96
1083 | 8.1 | 0.97
1084 | 8.2 | 0.96
1085 | 8.2 | 0.99
1086 | 7.7 | 0.97
1087 | 7.9 | 0.99
1088 | 7.6 | 0.99
1089 | 7.6 | 0.97
1090 | 9.2 | 0.93
1091 | 9.7 | 0.91
1092 | 10 | 0.88
1093 | 10.7 | 0.89
1094 | 10.5 | 0.9
1095 | 10.3 | 0.95
1096 | 10.3 | 0.99
1097 | 10.5 | 1
1098 | 10.4 | 0.99
1099 | 9.6 | 0.92
1100 | 9.3 | 0.91
1101 | 9.1 | 0.93
1102 | 9 | 0.93
1103 | 8.8 | 0.93
1104 | 8.1 | 0.92
1105 | 7.8 | 0.93
1106 | 7.3 | 0.96
1107 | 6.7 | 0.94
1108 | 6.3 | 0.92
1109 | 6 | 0.92
1110 | 6.9 | 0.94
1111 | 7 | 0.99
1112 | 7 | 0.94
1113 | 7.2 | 0.87
1114 | 8.2 | 0.92
1115 | 8.6 | 0.92
1116 | 9.4 | 0.89
1117 | 9.8 | 0.89
1118 | 9.9 | 0.91
1119 | 10.1 | 0.92
1120 | 9.9 | 0.95
1121 | 10 | 0.95
1122 | 10.1 | 0.96
1123 | 9.8 | 0.99
1124 | 9.7 | 0.99
1125 | 9.7 | 0.99
1126 | 9.9 | 0.97
1127 | 9.9 | 0.97
1128 | 9.7 | 0.97
1129 | 9.8 | 0.96
1130 | 9.6 | 0.99
1131 | 8.6 | 0.99
1132 | 8.4 | 0.97
1133 | 8.3 | 0.99
1134 | 8.5 | 0.97
1135 | 8.6 | 0.96
1136 | 7.1 | 0.9
1137 | 6.6 | 0.84
1138 | 7.4 | 0.86
1139 | 8.6 | 0.8
1140 | 9.2 | 0.75
1141 | 9.2 | 0.8
1142 | 8.9 | 0.84
1143 | 8.6 | 0.93
1144 | 9.8 | 0.86
1145 | 8.5 | 0.86
1146 | 8.5 | 0.84
1147 | 7.6 | 0.86
1148 | 7.8 | 0.86
1149 | 6.8 | 0.88
1150 | 7 | 0.87
1151 | 7.3 | 0.88
1152 | 6.2 | 0.88
1153 | 5.6 | 0.94
1154 | 4.6 | 0.97
1155 | 3.6 | 0.95
1156 | 3.2 | 0.95
1157 | 2.8 | 0.95
1158 | 2.8 | 0.91
1159 | 3.2 | 0.9
1160 | 4.4 | 0.87
1161 | 4.9 | 0.89
1162 | 5 | 0.89
1163 | 6.9 | 0.85
1164 | 7.5 | 0.81
1165 | 8.3 | 0.78
1166 | 8.5 | 0.73
1167 | 9.4 | 0.67
1168 | 9.1 | 0.7
1169 | 8.7 | 0.7
1170 | 7.9 | 0.72
1171 | 6.7 | 0.79
1172 | 5.1 | 0.84
1173 | 4.5 | 0.84
1174 | 3.1 | 0.91
1175 | 2.2 | 0.93
1176 | 2.2 | 0.91
1177 | 2.6 | 0.91
1178 | 1.6 | 0.93
1179 | 3 | 0.91
1180 | 2.9 | 0.98
1181 | 3.2 | 0.95
1182 | 5 | 0.94
1183 | 5.7 | 0.86
1184 | 6.1 | 0.91
1185 | 6.9 | 0.88
1186 | 7.5 | 0.9
1187 | 8 | 0.86
1188 | 8.2 | 0.86
1189 | 7.8 | 0.93
1190 | 7.7 | 0.99
1191 | 7.9 | 0.99
1192 | 8.1 | 0.99
1193 | 8.4 | 0.99
1194 | 8.4 | 0.99
1195 | 8.6 | 0.99
1196 | 8.9 | 0.99
1197 | 9 | 0.99
1198 | 9.1 | 0.99
1199 | 9.2 | 0.97
1200 | 9.1 | 0.99
1201 | 9.2 | 0.97
1202 | 9.2 | 0.97
1203 | 9.2 | 0.96
1204 | 9.3 | 0.96
1205 | 9.3 | 0.97
1206 | 9.2 | 1
1207 | 9.3 | 0.99
1208 | 9.4 | 0.99
1209 | 9.5 | 1
1210 | 9.8 | 0.99
1211 | 10 | 0.99
1212 | 10.3 | 1
1213 | 10.5 | 0.99
1214 | 10.5 | 1
1215 | 10.7 | 0.99
1216 | 10.3 | 1
1217 | 10.2 | 1
1218 | 10.2 | 1
1219 | 10.2 | 1
1220 | 10.2 | 1
1221 | 10.3 | 1
1222 | 10.3 | 1
1223 | 10.4 | 1
1224 | 10.4 | 1
1225 | 10.4 | 1
1226 | 10.3 | 1
1227 | 10.1 | 1
1228 | 9.9 | 0.99
1229 | 9.8 | 1
1230 | 9.9 | 0.97
1231 | 9.9 | 0.97
1232 | 9.9 | 0.95
1233 | 9.9 | 0.93
1234 | 9.9 | 0.93
1235 | 10.5 | 0.91
1236 | 10.6 | 0.9
1237 | 10.8 | 0.89
1238 | 10.4 | 0.9
1239 | 10 | 0.92
1240 | 9.8 | 0.92
1241 | 9.7 | 0.95
1242 | 9.6 | 0.96
1243 | 9.6 | 0.96
1244 | 9.4 | 0.96
1245 | 9.5 | 0.95
1246 | 9.9 | 0.91
1247 | 10.4 | 0.86
1248 | 10.6 | 0.85
1249 | 10.8 | 0.85
1250 | 10.7 | 0.85
1251 | 10.2 | 0.92
1252 | 9.8 | 0.97
1253 | 10.1 | 0.96
1254 | 10.1 | 0.97
1255 | 10 | 0.97
1256 | 10 | 0.96
1257 | 9.9 | 0.96
1258 | 10.1 | 0.96
1259 | 10.1 | 0.96
1260 | 10.1 | 0.97
1261 | 10.3 | 0.97
1262 | 10.7 | 0.95
1263 | 10.9 | 0.94
1264 | 11.1 | 0.91
1265 | 10.5 | 0.92
1266 | 10.3 | 0.91
1267 | 9.7 | 0.92
1268 | 9.7 | 0.89
1269 | 9.6 | 0.89
1270 | 9.6 | 0.88
1271 | 9.6 | 0.87
1272 | 9.7 | 0.87
1273 | 9.7 | 0.87
1274 | 9.8 | 0.86
1275 | 10.1 | 0.84
1276 | 10.2 | 0.85
1277 | 10.2 | 0.85
1278 | 10.4 | 0.86
1279 | 9.6 | 0.97
1280 | 9.8 | 0.99
1281 | 9.9 | 0.99
1282 | 10.3 | 1
1283 | 10.6 | 0.99
1284 | 11.1 | 0.94
1285 | 11.3 | 0.91
1286 | 11.4 | 0.89
1287 | 12.2 | 0.86
1288 | 13.1 | 0.74
1289 | 13.1 | 0.69
1290 | 11.4 | 0.8
1291 | 8.3 | 0.92
1292 | 7.2 | 0.96
1293 | 7.5 | 0.99
1294 | 7 | 1
1295 | 6.2 | 1
1296 | 7 | 1
1297 | 8.3 | 1
1298 | 8.4 | 1
1299 | 8.4 | 1
1300 | 8.3 | 1
1301 | 8.4 | 1
1302 | 7.6 | 1
1303 | 8.8 | 1
1304 | 9 | 1
1305 | 9.1 | 0.99
1306 | 9.3 | 1
1307 | 9.3 | 1
1308 | 9.2 | 1
1309 | 9.2 | 1
1310 | 9.1 | 1
1311 | 9.1 | 1
1312 | 9.1 | 1
1313 | 8.9 | 1
1314 | 8.6 | 1
1315 | 8.4 | 1
1316 | 8.3 | 0.99
1317 | 8.4 | 1
1318 | 8.1 | 1
1319 | 8.1 | 1
1320 | 8.1 | 0.99
1321 | 8.2 | 1
1322 | 8.4 | 1
1323 | 8.4 | 1
1324 | 8.8 | 1
1325 | 8.6 | 1
1326 | 8.7 | 1
1327 | 8.6 | 1
1328 | 8.4 | 1
1329 | 8.2 | 1
1330 | 8.6 | 1
1331 | 9.4 | 0.99
1332 | 10.5 | 0.88
1333 | 10.7 | 0.86
1334 | 11.2 | 0.84
1335 | 11 | 0.85
1336 | 10.5 | 0.85
1337 | 10 | 0.86
1338 | 9.6 | 0.87
1339 | 8.2 | 0.96
1340 | 7.8 | 0.97
1341 | 8.2 | 0.99
1342 | 8.1 | 0.99
1343 | 8.3 | 0.99
1344 | 8.2 | 0.99
1345 | 7.7 | 1
1346 | 7.6 | 1
1347 | 7.8 | 1
1348 | 7.1 | 1
1349 | 7.8 | 1
1350 | 7.9 | 1
1351 | 7.8 | 1
1352 | 7.9 | 1
1353 | 7.2 | 1
1354 | 7.6 | 1
1355 | 8 | 0.99
1356 | 8.8 | 0.96
1357 | 11.1 | 0.77
1358 | 11.5 | 0.7
1359 | 12.2 | 0.62
1360 | 10.8 | 0.73
1361 | 10.1 | 0.81
1362 | 9.1 | 0.88
1363 | 7.9 | 0.96
1364 | 7.8 | 0.99
1365 | 7.6 | 0.99
1366 | 7.6 | 1
1367 | 7.6 | 1
1368 | 6.9 | 1
1369 | 7.8 | 0.99
1370 | 8.2 | 1
1371 | 7.8 | 0.96
1372 | 7.9 | 0.96
1373 | 7.9 | 0.97
1374 | 7.7 | 0.93
1375 | 7.7 | 0.93
1376 | 7.6 | 0.94
1377 | 7.6 | 0.93
1378 | 7.9 | 0.93
1379 | 8 | 0.92
1380 | 8.6 | 0.92
1381 | 8.8 | 0.9
1382 | 8.9 | 0.9
1383 | 8.8 | 0.9
1384 | 8.5 | 0.9
1385 | 8.1 | 0.93
1386 | 7.5 | 0.94
1387 | 7.2 | 0.96
1388 | 6.8 | 0.96
1389 | 6.7 | 0.97
1390 | 6.8 | 0.97
1391 | 6.9 | 1
1392 | 7.1 | 0.99
1393 | 7.4 | 1
1394 | 7.7 | 1
1395 | 8.2 | 1
1396 | 8.9 | 1
1397 | 8.8 | 1
1398 | 8.6 | 1
1399 | 8.6 | 0.99
1400 | 8.2 | 0.97
1401 | 7.6 | 0.96
1402 | 8.3 | 0.96
1403 | 9.9 | 0.87
1404 | 10.8 | 0.82
1405 | 11.9 | 0.78
1406 | 11.7 | 0.83
1407 | 12.1 | 0.79
1408 | 11.6 | 0.81
1409 | 11.4 | 0.85
1410 | 10.4 | 0.78
1411 | 9.6 | 0.85
1412 | 9.9 | 0.84
1413 | 9.2 | 0.85
1414 | 8.7 | 0.89
1415 | 8.1 | 0.89
1416 | 6.6 | 0.94
1417 | 5.3 | 0.95
1418 | 4.4 | 0.95
1419 | 3.9 | 0.97
1420 | 4.3 | 0.98
1421 | 5.4 | 0.97
1422 | 5.8 | 0.97
1423 | 7.1 | 1
1424 | 7.8 | 1
1425 | 7 | 1
1426 | 8.2 | 0.99
1427 | 8.7 | 0.99
1428 | 9 | 1
1429 | 9.1 | 1
1430 | 9.6 | 1
1431 | 9.6 | 1
1432 | 9.9 | 0.99
1433 | 9.9 | 0.99
1434 | 9.4 | 1
1435 | 8.9 | 1
1436 | 8.9 | 0.99
1437 | 9.4 | 1
1438 | 8.9 | 1
1439 | 8.6 | 0.99
1440 | 7.7 | 0.99
1441 | 6.9 | 0.97
1442 | 6.6 | 0.94
1443 | 4.6 | 0.97
1444 | 4 | 0.98
1445 | 5 | 0.98
1446 | 5.4 | 1
1447 | 6.5 | 0.97
1448 | 7.9 | 0.97
1449 | 8.4 | 0.99
1450 | 9.1 | 0.99
1451 | 9.8 | 0.96
1452 | 10.1 | 0.95
1453 | 10.1 | 0.99
1454 | 10.5 | 0.99
1455 | 9.5 | 0.93
1456 | 9.2 | 0.85
1457 | 9.2 | 0.76
1458 | 8.7 | 0.69
1459 | 7.4 | 0.73
1460 | 6.4 | 0.76
1461 | 6.2 | 0.8
1462 | 5.9 | 0.8
1463 | 5.7 | 0.8
1464 | 5.8 | 0.85
1465 | 5.8 | 0.83
1466 | 5.7 | 0.78
1467 | 5.8 | 0.79
1468 | 5.4 | 0.81
1469 | 4.9 | 0.86
1470 | 4.9 | 0.89
1471 | 5.3 | 0.86
1472 | 5.1 | 0.9
1473 | 4.8 | 0.94
1474 | 5.2 | 0.98
1475 | 4.9 | 0.98
1476 | 5.4 | 0.98
1477 | 6.5 | 1
1478 | 7 | 0.99
1479 | 3.5 | 0.98
1480 | 2.2 | 0.96
1481 | 1.9 | 0.94
1482 | 1.8 | 0.96
1483 | 2 | 0.94
1484 | 1.1 | 0.94
1485 | 1.6 | 0.93
1486 | 1.4 | 0.94
1487 | 0.6 | 0.92
1488 | -0.1 | 0.96
1489 | 1.9 | 0.89
1490 | 1.6 | 0.91
1491 | 2 | 0.89
1492 | 2 | 0.91
1493 | 2.1 | 0.95
1494 | 3.3 | 0.93
1495 | 2.3 | 0.93
1496 | 2.5 | 0.93
1497 | 4.1 | 0.88
1498 | 4.5 | 0.84
1499 | 5.7 | 0.75
1500 | 5.6 | 0.75
1501 | 6.6 | 0.66
1502 | 7 | 0.61
1503 | 5.1 | 0.78
1504 | 5.9 | 0.76
1505 | 5.2 | 0.81
1506 | 5.6 | 0.78
1507 | 3.8 | 0.82
1508 | 3.5 | 0.88
1509 | 2.2 | 0.89
1510 | 3 | 0.88
1511 | 2.9 | 0.89
1512 | 2.1 | 0.91
1513 | 3.6 | 0.86
1514 | 3.5 | 0.88
1515 | 3.1 | 0.9
1516 | 4 | 0.88
1517 | 4 | 0.87
1518 | 4.2 | 0.88
1519 | 4.1 | 0.87
1520 | 3.5 | 0.88
1521 | 4.4 | 0.82
1522 | 5.7 | 0.8
1523 | 7.8 | 0.76
1524 | 8.1 | 0.74
1525 | 8.1 | 0.79
1526 | 8.1 | 0.79
1527 | 8 | 0.89
1528 | 7.6 | 0.94
1529 | 7.8 | 0.99
1530 | 8 | 0.97
1531 | 7.5 | 0.99
1532 | 7.8 | 0.99
1533 | 9.5 | 0.99
1534 | 10 | 0.99
1535 | 9.7 | 1
1536 | 9.7 | 1
1537 | 9.8 | 1
1538 | 9.3 | 1
1539 | 9.1 | 0.99
1540 | 8.9 | 0.99
1541 | 8.9 | 0.97
1542 | 8.9 | 0.97
1543 | 8.9 | 0.96
1544 | 8.9 | 0.97
1545 | 6 | 0.95
1546 | 4.7 | 0.95
1547 | 4.8 | 0.9
1548 | 5.5 | 0.86
1549 | 6.7 | 0.78
1550 | 7.5 | 0.79
1551 | 8.5 | 0.69
1552 | 8.8 | 0.63
1553 | 8.1 | 0.72
1554 | 6.9 | 0.82
1555 | 6.4 | 0.84
1556 | 5.9 | 0.86
1557 | 5.2 | 0.89
1558 | 5.2 | 0.84
1559 | 4.4 | 0.87
1560 | 4.6 | 0.89
1561 | 4.5 | 0.85
1562 | 4.5 | 0.84
1563 | 5.1 | 0.89
1564 | 5.2 | 0.89
1565 | 4.5 | 0.89
1566 | 4.8 | 0.84
1567 | 4.6 | 0.85
1568 | 4.6 | 0.87
1569 | 5.2 | 0.84
1570 | 6.5 | 0.79
1571 | 7.3 | 0.73
1572 | 7.8 | 0.72
1573 | 9 | 0.67
1574 | 9.3 | 0.65
1575 | 9.2 | 0.63
1576 | 10.3 | 0.55
1577 | 10.1 | 0.55
1578 | 9.1 | 0.53
1579 | 7.9 | 0.63
1580 | 6.8 | 0.67
1581 | 3.8 | 0.8
1582 | 5.7 | 0.77
1583 | 5 | 0.81
1584 | 3.9 | 0.83
1585 | 3.3 | 0.85
1586 | 3.5 | 0.81
1587 | 3.1 | 0.86
1588 | 3.1 | 0.9
1589 | 3.6 | 0.93
1590 | 3.5 | 0.95
1591 | 4.4 | 0.95
1592 | 5.4 | 0.91
1593 | 6.3 | 0.88
1594 | 6.8 | 0.93
1595 | 7.1 | 0.96
1596 | 7.7 | 0.99
1597 | 8.4 | 0.99
1598 | 9.2 | 0.99
1599 | 10.6 | 0.99
1600 | 12.9 | 0.84
1601 | 11.5 | 0.68
1602 | 10.3 | 0.61
1603 | 9 | 0.64
1604 | 7.9 | 0.75
1605 | 7.5 | 0.74
1606 | 6.5 | 0.78
1607 | 5.5 | 0.84
1608 | 5 | 0.87
1609 | 4.2 | 0.93
1610 | 5.3 | 0.92
1611 | 7.1 | 0.91
1612 | 7.6 | 0.91
1613 | 8.4 | 0.88
1614 | 8.1 | 0.76
1615 | 7.8 | 0.79
1616 | 7.4 | 0.74
1617 | 7.6 | 0.61
1618 | 7.9 | 0.57
1619 | 8.6 | 0.52
1620 | 8.5 | 0.56
1621 | 9.1 | 0.56
1622 | 9.1 | 0.51
1623 | 8.6 | 0.52
1624 | 8.5 | 0.6
1625 | 7.7 | 0.68
1626 | 7.3 | 0.71
1627 | 6 | 0.88
1628 | 5.3 | 0.95
1629 | 4.9 | 0.97
1630 | 5.3 | 0.98
1631 | 5.4 | 0.98
1632 | 5.8 | 1
1633 | 7.4 | 0.99
1634 | 8.2 | 0.99
1635 | 1.9 | 0.96
1636 | 2 | 0.94
1637 | 2.1 | 0.95
1638 | 4.8 | 0.86
1639 | 4.8 | 0.59
1640 | 4.1 | 0.72
1641 | 4 | 0.69
1642 | 4 | 0.74
1643 | 5.7 | 0.64
1644 | 7.1 | 0.55
1645 | 7.1 | 0.62
1646 | 4.4 | 0.9
1647 | 5.7 | 0.82
1648 | 7.6 | 0.53
1649 | 5 | 0.75
1650 | 4.5 | 0.76
1651 | 3.7 | 0.76
1652 | 3.3 | 0.73
1653 | 2.8 | 0.82
1654 | 2.3 | 0.91
1655 | 2 | 0.89
1656 | 2.2 | 0.93
1657 | 2.7 | 0.84
1658 | 3.4 | 0.71
1659 | 2.2 | 0.78
1660 | 2.6 | 0.84
1661 | 1.3 | 0.87
1662 | 2.7 | 0.81
1663 | 2.1 | 0.84
1664 | 2.4 | 0.86
1665 | 2.5 | 0.89
1666 | 5.7 | 0.85
1667 | 7.2 | 0.81
1668 | 7.9 | 0.83
1669 | 8.8 | 0.77
1670 | 8.6 | 0.77
1671 | 9.1 | 0.73
1672 | 8.1 | 0.83
1673 | 8.1 | 0.83
1674 | 7.4 | 0.94
1675 | 7.3 | 0.97
1676 | 7.6 | 0.99
1677 | 8.3 | 0.99
1678 | 8.9 | 0.99
1679 | 9.4 | 0.99
1680 | 9.9 | 0.99
1681 | 10.1 | 0.99
1682 | 9.8 | 0.97
1683 | 7.6 | 0.94
1684 | 5 | 0.89
1685 | 4.7 | 0.85
1686 | 4.5 | 0.87
1687 | 4.1 | 0.9
1688 | 4.1 | 0.9
1689 | 3.7 | 0.86
1690 | 3.6 | 0.88
1691 | 3.3 | 0.86
1692 | 4 | 0.9
1693 | 6.1 | 0.82
1694 | 7 | 0.73
1695 | 6.1 | 0.64
1696 | 7.4 | 0.65
1697 | 4.9 | 0.76
1698 | 6 | 0.7
1699 | 5.1 | 0.75
1700 | 4.4 | 0.77
1701 | 4.7 | 0.76
1702 | 4.7 | 0.79
1703 | 4.7 | 0.78
1704 | 4.3 | 0.82
1705 | 4.5 | 0.77
1706 | 5 | 0.76
1707 | 5.5 | 0.74
1708 | 5.4 | 0.78
1709 | 5.1 | 0.78
1710 | 5.7 | 0.68
1711 | 4.8 | 0.78
1712 | 5 | 0.75
1713 | 5.4 | 0.8
1714 | 6.5 | 0.75
1715 | 7.1 | 0.73
1716 | 8.6 | 0.61
1717 | 7.8 | 0.72
1718 | 6.9 | 0.85
1719 | 8.6 | 0.7
1720 | 8.6 | 0.68
1721 | 8.6 | 0.65
1722 | 7.6 | 0.82
1723 | 7.6 | 0.82
1724 | 7 | 0.85
1725 | 7 | 0.85
1726 | 7.1 | 0.88
1727 | 7.3 | 0.88
1728 | 7.7 | 0.89
1729 | 8.4 | 0.85
1730 | 8.5 | 0.89
1731 | 8.9 | 0.89
1732 | 9.3 | 0.89
1733 | 9.8 | 0.88
1734 | 9.9 | 0.9
1735 | 10.1 | 0.92
1736 | 10.1 | 0.93
1737 | 10.2 | 0.95
1738 | 10.8 | 0.91
1739 | 11.7 | 0.85
1740 | 9.8 | 0.96
1741 | 10.6 | 0.89
1742 | 11.8 | 0.82
1743 | 11.6 | 0.82
1744 | 11.4 | 0.88
1745 | 11.8 | 0.88
1746 | 11.9 | 0.87
1747 | 11.8 | 0.88
1748 | 11.1 | 0.9
1749 | 11.2 | 0.9
1750 | 11.4 | 0.89
1751 | 11.1 | 0.91
1752 | 11.1 | 0.91
1753 | 11 | 0.89
1754 | 10.9 | 0.91
1755 | 11 | 0.9
1756 | 11 | 0.91
1757 | 11.3 | 0.89
1758 | 11.2 | 0.9
1759 | 11 | 0.92
1760 | 11 | 0.92
1761 | 9.7 | 0.95
1762 | 9.3 | 0.91
1763 | 9.3 | 0.88
1764 | 9 | 0.85
1765 | 9.1 | 0.81
1766 | 10.1 | 0.83
1767 | 10.1 | 0.81
1768 | 10.3 | 0.77
1769 | 9.7 | 0.87
1770 | 8.9 | 0.95
1771 | 8.2 | 0.99
1772 | 8.2 | 1
1773 | 9.7 | 0.99
1774 | 10.4 | 0.97
1775 | 10.4 | 0.96
1776 | 10.3 | 0.96
1777 | 10.2 | 0.93
1778 | 10.3 | 0.91
1779 | 10.1 | 0.92
1780 | 10 | 0.88
1781 | 9.8 | 0.92
1782 | 9.8 | 0.93
1783 | 9.8 | 0.96
1784 | 9.7 | 0.97
1785 | 9.7 | 0.97
1786 | 10 | 0.97
1787 | 10.1 | 0.96
1788 | 10.2 | 0.96
1789 | 9.6 | 0.91
1790 | 8.8 | 0.89
1791 | 7 | 0.85
1792 | 5.9 | 0.88
1793 | 6.3 | 0.82
1794 | 5 | 0.84
1795 | 5.1 | 0.79
1796 | 3.5 | 0.86
1797 | 2.4 | 0.91
1798 | 2.3 | 0.91
1799 | 1.5 | 0.92
1800 | 1.3 | 0.92
1801 | 1.2 | 0.92
1802 | 1.2 | 0.89
1803 | 1.2 | 0.9
1804 | 1.3 | 0.91
1805 | 1.4 | 0.92
1806 | 1.4 | 0.92
1807 | 2 | 0.91
1808 | 1.5 | 0.94
1809 | 2.1 | 0.91
1810 | 4 | 0.85
1811 | 5.9 | 0.76
1812 | 7.6 | 0.66
1813 | 7.8 | 0.69
1814 | 8.8 | 0.64
1815 | 9.2 | 0.65
1816 | 9.1 | 0.63
1817 | 7.7 | 0.77
1818 | 8.7 | 0.65
1819 | 8 | 0.67
1820 | 6.7 | 0.74
1821 | 6 | 0.74
1822 | 5.7 | 0.8
1823 | 5.1 | 0.84
1824 | 5.3 | 0.84
1825 | 5.5 | 0.83
1826 | 5 | 0.86
1827 | 4.9 | 0.81
1828 | 5.3 | 0.84
1829 | 4.9 | 0.89
1830 | 4.5 | 0.9
1831 | 5 | 0.87
1832 | 4.8 | 0.92
1833 | 5.5 | 0.92
1834 | 6.5 | 0.91
1835 | 7.4 | 0.87
1836 | 8.4 | 0.81
1837 | 7.8 | 0.91
1838 | 8.3 | 0.92
1839 | 9.1 | 0.81
1840 | 9.7 | 0.77
1841 | 9.6 | 0.8
1842 | 9.8 | 0.75
1843 | 9.4 | 0.75
1844 | 8.8 | 0.77
1845 | 8.3 | 0.79
1846 | 7.9 | 0.83
1847 | 7.6 | 0.87
1848 | 6.9 | 0.9
1849 | 7.3 | 0.88
1850 | 6 | 0.92
1851 | 4.1 | 0.93
1852 | 5.3 | 0.97
1853 | 6.5 | 0.95
1854 | 6.7 | 0.98
1855 | 7.1 | 0.99
1856 | 7.5 | 0.99
1857 | 8.3 | 0.99
1858 | 9.1 | 1
1859 | 9.9 | 1
1860 | 11.8 | 0.94
1861 | 13 | 0.8
1862 | 14 | 0.69
1863 | 15.2 | 0.67
1864 | 15.4 | 0.67
1865 | 16.3 | 0.62
1866 | 15.6 | 0.67
1867 | 14.4 | 0.72
1868 | 12 | 0.82
1869 | 10.6 | 0.89
1870 | 9.4 | 0.92
1871 | 8.7 | 0.94
1872 | 8.1 | 0.96
1873 | 8 | 0.96
1874 | 7.5 | 0.97
1875 | 7 | 0.99
1876 | 5.3 | 0.98
1877 | 5.6 | 1
1878 | 4.3 | 1
1879 | 4.6 | 1
1880 | 3.9 | 1
1881 | 5.4 | 1
1882 | 7.9 | 1
1883 | 9 | 1
1884 | 10.7 | 0.99
1885 | 11.2 | 0.97
1886 | 12 | 0.96
1887 | 13.2 | 0.9
1888 | 13.6 | 0.87
1889 | 12.5 | 0.95
1890 | 12.3 | 0.95
1891 | 11.6 | 0.96
1892 | 11.1 | 0.96
1893 | 10.4 | 0.96
1894 | 10.2 | 0.95
1895 | 9.5 | 0.96
1896 | 9.4 | 0.95
1897 | 9.3 | 0.97
1898 | 9.2 | 0.97
1899 | 9.1 | 0.99
1900 | 9 | 0.97
1901 | 8.8 | 0.96
1902 | 8.6 | 0.97
1903 | 8.6 | 0.99
1904 | 8.5 | 1
1905 | 9 | 0.96
1906 | 9.5 | 0.92
1907 | 10.2 | 0.92
1908 | 10.1 | 0.92
1909 | 10.8 | 0.91
1910 | 10.9 | 0.91
1911 | 11.1 | 0.86
1912 | 10.7 | 0.92
1913 | 10.3 | 0.95
1914 | 9.6 | 0.93
1915 | 8.8 | 1
1916 | 8.8 | 1
1917 | 9 | 1
1918 | 9.1 | 1
1919 | 9.4 | 1
1920 | 9.4 | 1
1921 | 9.2 | 1
1922 | 9.2 | 0.99
1923 | 8.9 | 0.97
1924 | 8.6 | 0.99
1925 | 8.3 | 0.96
1926 | 8.7 | 0.92
1927 | 8.4 | 0.93
1928 | 8.7 | 0.92
1929 | 8.9 | 0.93
1930 | 9.4 | 0.93
1931 | 9.2 | 0.97
1932 | 9.3 | 0.99
1933 | 9.7 | 0.99
1934 | 10.5 | 0.96
1935 | 9.1 | 0.96
1936 | 9.4 | 0.8
1937 | 10.1 | 0.68
1938 | 9.8 | 0.67
1939 | 8.6 | 0.63
1940 | 7.8 | 0.69
1941 | 6.9 | 0.72
1942 | 6.5 | 0.71
1943 | 6 | 0.73
1944 | 5.3 | 0.78
1945 | 4.8 | 0.81
1946 | 4.3 | 0.85
1947 | 4.9 | 0.81
1948 | 4.1 | 0.87
1949 | 4 | 0.83
1950 | 3.9 | 0.83
1951 | 3.7 | 0.83
1952 | 4 | 0.8
1953 | 4.3 | 0.8
1954 | 5.2 | 0.8
1955 | 6.5 | 0.73
1956 | 7.5 | 0.66
1957 | 8.1 | 0.5
1958 | 8.6 | 0.55
1959 | 8.8 | 0.54
1960 | 8 | 0.62
1961 | 7 | 0.64
1962 | 6.8 | 0.67
1963 | 6.3 | 0.7
1964 | 6.5 | 0.65
1965 | 6.5 | 0.63
1966 | 6.4 | 0.63
1967 | 6 | 0.7
1968 | 5.5 | 0.74
1969 | 4.7 | 0.79
1970 | 4.3 | 0.82
1971 | 3.9 | 0.82
1972 | 3.6 | 0.81
1973 | 3.4 | 0.83
1974 | 2.7 | 0.86
1975 | 2.5 | 0.86
1976 | 2.7 | 0.84
1977 | 3.5 | 0.83
1978 | 5.7 | 0.75
1979 | 7 | 0.71
1980 | 8.5 | 0.6
1981 | 9.1 | 0.58
1982 | 9.2 | 0.57
1983 | 9.4 | 0.59
1984 | 9.1 | 0.62
1985 | 9.6 | 0.58
1986 | 8.9 | 0.6
1987 | 8.8 | 0.65
1988 | 7.2 | 0.76
1989 | 6.5 | 0.81
1990 | 6.6 | 0.81
1991 | 6.3 | 0.82
1992 | 6.5 | 0.84
1993 | 6.6 | 0.84
1994 | 6 | 0.83
1995 | 6.2 | 0.86
1996 | 5.6 | 0.89
1997 | 5.4 | 0.91
1998 | 6 | 0.86
1999 | 6 | 0.88
2000 | 5.7 | 0.89
2001 | 6.2 | 0.89
2002 | 7.7 | 0.83
2003 | 9.3 | 0.71
2004 | 10.6 | 0.63
2005 | 11.3 | 0.55
2006 | 12 | 0.53
2007 | 12.9 | 0.51
2008 | 12.8 | 0.57
2009 | 10.8 | 0.66
2010 | 10.3 | 0.65
2011 | 8 | 0.75
2012 | 6.8 | 0.79
2013 | 6.6 | 0.85
2014 | 6.3 | 0.85
2015 | 7.7 | 0.73
2016 | 7.6 | 0.77
2017 | 6.8 | 0.79
2018 | 6.3 | 0.8
2019 | 5.8 | 0.8
2020 | 4.8 | 0.86
2021 | 5.2 | 0.81
2022 | 4.6 | 0.89
2023 | 4.4 | 0.85
2024 | 4.9 | 0.81
2025 | 6.8 | 0.75
2026 | 7.6 | 0.76
2027 | 9 | 0.71
2028 | 10.5 | 0.6
2029 | 11.6 | 0.64
2030 | 12.2 | 0.58
2031 | 11.8 | 0.65
2032 | 12.1 | 0.65
2033 | 11.5 | 0.65
2034 | 10.8 | 0.66
2035 | 9.4 | 0.7
2036 | 6.7 | 0.79
2037 | 7.6 | 0.8
2038 | 8.6 | 0.78
2039 | 8.2 | 0.79
2040 | 7.7 | 0.79
2041 | 6.8 | 0.82
2042 | 6.4 | 0.84
2043 | 6.2 | 0.82
2044 | 5.5 | 0.87
2045 | 5.5 | 0.84
2046 | 4.4 | 0.92
2047 | 4.4 | 0.9
2048 | 4.3 | 0.9
2049 | 7.8 | 0.78
2050 | 9.1 | 0.73
2051 | 10.1 | 0.73
2052 | 10.1 | 0.76
2053 | 11.4 | 0.7
2054 | 12.7 | 0.62
2055 | 12.6 | 0.67
2056 | 12.4 | 0.73
2057 | 12.2 | 0.73
2058 | 11.5 | 0.76
2059 | 10.2 | 0.8
2060 | 7.7 | 0.86
2061 | 6.1 | 0.91
2062 | 5.7 | 0.91
2063 | 6.8 | 0.87
2064 | 6.8 | 0.85
2065 | 6.2 | 0.86
2066 | 6 | 0.86
2067 | 5.2 | 0.89
2068 | 3.9 | 0.95
2069 | 4 | 0.95
2070 | 3.8 | 0.95
2071 | 2 | 0.96
2072 | 1.2 | 0.98
2073 | 5.1 | 0.97
2074 | 7.8 | 0.91
2075 | 8.6 | 0.88
2076 | 9.7 | 0.82
2077 | 10.9 | 0.76
2078 | 11.1 | 0.74
2079 | 11.2 | 0.73
2080 | 10.8 | 0.74
2081 | 10.8 | 0.76
2082 | 10 | 0.79
2083 | 8.9 | 0.84
2084 | 6.8 | 0.9
2085 | 5.5 | 0.94
2086 | 5.5 | 0.94
2087 | 4.3 | 0.97
2088 | 5.9 | 0.95
2089 | 6.6 | 0.94
2090 | 6.5 | 0.94
2091 | 6.1 | 0.94
2092 | 6.4 | 0.94
2093 | 6.1 | 0.94
2094 | 6.2 | 0.94
2095 | 6.5 | 0.94
2096 | 6.9 | 0.9
2097 | 7.4 | 0.88
2098 | 7.9 | 0.86
2099 | 8.9 | 0.82
2100 | 9.8 | 0.79
2101 | 10.8 | 0.76
2102 | 10.6 | 0.75
2103 | 11.2 | 0.73
2104 | 11.1 | 0.73
2105 | 10.5 | 0.74
2106 | 9.6 | 0.78
2107 | 8.5 | 0.81
2108 | 6.3 | 0.86
2109 | 4.7 | 0.9
2110 | 4.1 | 0.9
2111 | 4.5 | 0.89
2112 | 5 | 0.84
2113 | 6.5 | 0.81
2114 | 6.7 | 0.79
2115 | 6.7 | 0.79
2116 | 6.7 | 0.78
2117 | 6.7 | 0.76
2118 | 6.7 | 0.75
2119 | 6.8 | 0.72
2120 | 6.8 | 0.72
2121 | 7.1 | 0.71
2122 | 7.5 | 0.7
2123 | 8.3 | 0.66
2124 | 8.8 | 0.62
2125 | 9.3 | 0.62
2126 | 10.1 | 0.6
2127 | 10.6 | 0.59
2128 | 10.8 | 0.6
2129 | 11.6 | 0.61
2130 | 11.4 | 0.58
2131 | 11.3 | 0.62
2132 | 10.8 | 0.67
2133 | 10.1 | 0.72
2134 | 8.3 | 0.75
2135 | 8.5 | 0.78
2136 | 8.5 | 0.79
2137 | 7.9 | 0.83
2138 | 7.2 | 0.83
2139 | 7.5 | 0.84
2140 | 6.2 | 0.86
2141 | 5.4 | 0.86
2142 | 4.1 | 0.83
2143 | 3.7 | 0.81
2144 | 4.2 | 0.75
2145 | 5.3 | 0.74
2146 | 6.9 | 0.68
2147 | 8.3 | 0.61
2148 | 9.5 | 0.56
2149 | 10.4 | 0.56
2150 | 11.7 | 0.55
2151 | 11.1 | 0.67
2152 | 10.9 | 0.7
2153 | 9.6 | 0.76
2154 | 9.4 | 0.75
2155 | 8.2 | 0.79
2156 | 7.4 | 0.86
2157 | 6.8 | 0.9
2158 | 6.4 | 0.89
2159 | 6.2 | 0.91
2160 | 5.9 | 0.94
2161 | 5.6 | 0.94
2162 | 5.3 | 0.92
2163 | 5.2 | 0.92
2164 | 5.3 | 0.92
2165 | 5.2 | 0.94
2166 | 5.1 | 0.92
2167 | 5.6 | 0.92
2168 | 6.4 | 0.92
2169 | 6.7 | 0.91
2170 | 6.6 | 0.93
2171 | 7.5 | 0.9
2172 | 7.8 | 0.89
2173 | 8.3 | 0.87
2174 | 9.1 | 0.89
2175 | 10.4 | 0.85
2176 | 10.2 | 0.86
2177 | 10 | 0.84
2178 | 10.2 | 0.72
2179 | 9.4 | 0.7
2180 | 8.5 | 0.68
2181 | 7.7 | 0.79
2182 | 6.3 | 0.86
2183 | 5.5 | 0.83
2184 | 4.8 | 0.81
2185 | 4.2 | 0.85
2186 | 3.8 | 0.87
2187 | 3.7 | 0.81
2188 | 3.2 | 0.84
2189 | 2.9 | 0.86
2190 | 2.2 | 0.89
2191 | 0.4 | 0.92
2192 | 2.5 | 0.89
2193 | 2.3 | 0.93
2194 | 4.5 | 0.79
2195 | 3.8 | 0.82
2196 | 3.5 | 0.86
2197 | 3.4 | 0.93
2198 | 3.5 | 0.83
2199 | 4.8 | 0.76
2200 | 5.1 | 0.73
2201 | 4.2 | 0.85
2202 | 3.5 | 0.86
2203 | 2.8 | 0.89
2204 | 2.9 | 0.81
2205 | 2.2 | 0.91
2206 | 2.1 | 0.89
2207 | 2.3 | 0.89
2208 | 3.2 | 0.83
2209 | 3.1 | 0.84
2210 | 2.9 | 0.86
2211 | 2.4 | 0.87
2212 | 2.2 | 0.87
2213 | 2.4 | 0.87
2214 | 2.4 | 0.86
2215 | 2.8 | 0.86
2216 | 3.1 | 0.86
2217 | 4 | 0.82
2218 | 5 | 0.73
2219 | 5 | 0.75
2220 | 5.9 | 0.65
2221 | 4.8 | 0.76
2222 | 5.7 | 0.68
2223 | 6 | 0.7
2224 | 7.7 | 0.62
2225 | 7.1 | 0.62
2226 | 6.8 | 0.65
2227 | 6.6 | 0.62
2228 | 5.9 | 0.68
2229 | 5.3 | 0.67
2230 | 4.7 | 0.73
2231 | 4.6 | 0.77
2232 | 5 | 0.79
2233 | 5 | 0.83
2234 | 4.8 | 0.89
2235 | 5 | 0.9
2236 | 4.5 | 0.9
2237 | 4 | 0.9
2238 | 3.6 | 0.9
2239 | 3.2 | 0.86
2240 | 2.5 | 0.89
2241 | 3.6 | 0.85
2242 | 4.3 | 0.8
2243 | 5.2 | 0.73
2244 | 6.2 | 0.66
2245 | 7.3 | 0.55
2246 | 7.2 | 0.58
2247 | 7.7 | 0.51
2248 | 7.8 | 0.61
2249 | 4.7 | 0.73
2250 | 6.9 | 0.63
2251 | 6.6 | 0.61
2252 | 5 | 0.69
2253 | 4.3 | 0.72
2254 | 3.3 | 0.79
2255 | 2.7 | 0.81
2256 | 2.1 | 0.84
2257 | 1.5 | 0.85
2258 | 0.5 | 0.86
2259 | 0.7 | 0.9
2260 | 0.8 | 0.9
2261 | 0.9 | 0.86
2262 | 0.2 | 0.9
2263 | 0.1 | 0.94
2264 | 1.1 | 0.9
2265 | 2 | 0.85
2266 | 4.4 | 0.82
2267 | 6.3 | 0.76
2268 | 7.6 | 0.72
2269 | 9.2 | 0.62
2270 | 9.5 | 0.58
2271 | 8.8 | 0.58
2272 | 9.3 | 0.59
2273 | 8.5 | 0.69
2274 | 8 | 0.75
2275 | 7.1 | 0.88
2276 | 7 | 0.85
2277 | 6.7 | 0.9
2278 | 6 | 0.94
2279 | 5.7 | 0.95
2280 | 5.5 | 0.95
2281 | 6 | 0.98
2282 | 6.6 | 0.97
2283 | 6.5 | 0.97
2284 | 6.4 | 0.97
2285 | 6.4 | 0.98
2286 | 6.7 | 0.98
2287 | 7 | 0.99
2288 | 7 | 0.97
2289 | 7.7 | 0.94
2290 | 8.1 | 0.9
2291 | 8.8 | 0.89
2292 | 9.2 | 0.81
2293 | 10.4 | 0.8
2294 | 9.6 | 0.83
2295 | 9.3 | 0.83
2296 | 9.6 | 0.82
2297 | 9.6 | 0.79
2298 | 9.6 | 0.78
2299 | 9.1 | 0.79
2300 | 8.4 | 0.81
2301 | 7.6 | 0.84
2302 | 8 | 0.82
2303 | 7.2 | 0.83
2304 | 6.8 | 0.79
2305 | 6.3 | 0.79
2306 | 5.8 | 0.74
2307 | 5.4 | 0.66
2308 | 4.8 | 0.68
2309 | 4.4 | 0.79
2310 | 3.3 | 0.83
2311 | 2.9 | 0.83
2312 | 3.7 | 0.75
2313 | 5.3 | 0.67
2314 | 7.1 | 0.7
2315 | 9.1 | 0.73
2316 | 9.4 | 0.76
2317 | 10.4 | 0.7
2318 | 10.9 | 0.7
2319 | 10 | 0.73
2320 | 9.1 | 0.79
2321 | 8.6 | 0.85
2322 | 8.6 | 0.82
2323 | 8.4 | 0.86
2324 | 8.1 | 0.89
2325 | 7.8 | 0.91
2326 | 7.7 | 0.93
2327 | 8.1 | 0.92
2328 | 8.2 | 0.94
2329 | 8.2 | 0.94
2330 | 8.2 | 0.94
2331 | 8.2 | 0.96
2332 | 8 | 0.96
2333 | 8.1 | 0.96
2334 | 8.1 | 0.97
2335 | 8.1 | 0.96
2336 | 8.3 | 0.96
2337 | 8.4 | 0.96
2338 | 8.7 | 0.97
2339 | 9.8 | 0.88
2340 | 9.9 | 0.87
2341 | 10.5 | 0.86
2342 | 10.5 | 0.83
2343 | 10.4 | 0.78
2344 | 10.3 | 0.81
2345 | 9.6 | 0.87
2346 | 9.6 | 0.84
2347 | 9.2 | 0.87
2348 | 8.7 | 0.94
2349 | 8.6 | 0.96
2350 | 8.6 | 0.96
2351 | 8.7 | 0.94
2352 | 8.4 | 0.96
2353 | 8 | 0.97
2354 | 7.6 | 0.96
2355 | 7.4 | 0.97
2356 | 7.4 | 0.99
2357 | 8 | 0.99
2358 | 7.9 | 0.97
2359 | 7.8 | 0.97
2360 | 7.8 | 0.97
2361 | 7.7 | 0.96
2362 | 8.9 | 0.9
2363 | 9.6 | 0.87
2364 | 10.3 | 0.83
2365 | 9.8 | 0.84
2366 | 10.8 | 0.79
2367 | 10.2 | 0.88
2368 | 9.4 | 0.95
2369 | 8.4 | 0.94
2370 | 8.3 | 0.93
2371 | 8.1 | 0.93
2372 | 7.9 | 0.93
2373 | 7.8 | 0.93
2374 | 7.6 | 0.91
2375 | 7.2 | 0.93
2376 | 7.5 | 0.9
2377 | 7.5 | 0.91
2378 | 7.4 | 0.93
2379 | 7.4 | 0.9
2380 | 7.3 | 0.93
2381 | 7.3 | 0.91
2382 | 7.1 | 0.94
2383 | 6.9 | 0.94
2384 | 7.2 | 0.93
2385 | 8 | 0.87
2386 | 8.8 | 0.8
2387 | 9.4 | 0.81
2388 | 10.1 | 0.78
2389 | 10.6 | 0.76
2390 | 8.7 | 0.85
2391 | 9.5 | 0.85
2392 | 9 | 0.86
2393 | 8.2 | 0.87
2394 | 8.1 | 0.82
2395 | 7.6 | 0.82
2396 | 7.2 | 0.84
2397 | 6.9 | 0.87
2398 | 6.9 | 0.87
2399 | 6.7 | 0.88
2400 | 6.7 | 0.88
2401 | 5.3 | 0.92
2402 | 6.4 | 0.89
2403 | 6.5 | 0.88
2404 | 6.5 | 0.88
2405 | 6.2 | 0.88
2406 | 6.2 | 0.86
2407 | 5.6 | 0.89
2408 | 6.5 | 0.87
2409 | 7.4 | 0.84
2410 | 8.8 | 0.77
2411 | 9.4 | 0.75
2412 | 10.2 | 0.72
2413 | 10.5 | 0.74
2414 | 10.4 | 0.75
2415 | 10.4 | 0.7
2416 | 10.4 | 0.72
2417 | 10.3 | 0.7
2418 | 9.6 | 0.71
2419 | 8.4 | 0.83
2420 | 8.1 | 0.86
2421 | 7 | 0.91
2422 | 6.7 | 0.91
2423 | 5.7 | 0.91
2424 | 5.5 | 0.91
2425 | 6.5 | 0.89
2426 | 7.4 | 0.88
2427 | 7.2 | 0.88
2428 | 7.7 | 0.9
2429 | 7.8 | 0.9
2430 | 8 | 0.92
2431 | 7.8 | 0.89
2432 | 7.8 | 0.84
2433 | 8.1 | 0.83
2434 | 8 | 0.79
2435 | 8.1 | 0.79
2436 | 8.9 | 0.72
2437 | 8.7 | 0.73
2438 | 9 | 0.72
2439 | 8.7 | 0.76
2440 | 8.4 | 0.78
2441 | 8.1 | 0.81
2442 | 8.2 | 0.77
2443 | 7.9 | 0.79
2444 | 7.6 | 0.8
2445 | 7.6 | 0.82
2446 | 6.9 | 0.82
2447 | 7.6 | 0.82
2448 | 7.5 | 0.81
2449 | 7.5 | 0.83
2450 | 7.3 | 0.81
2451 | 7.1 | 0.81
2452 | 7.4 | 0.84
2453 | 7.4 | 0.88
2454 | 7.7 | 0.87
2455 | 7.8 | 0.87
2456 | 7.9 | 0.84
2457 | 7.8 | 0.83
2458 | 8 | 0.8
2459 | 7.9 | 0.8
2460 | 8 | 0.8
2461 | 8 | 0.79
2462 | 8.1 | 0.79
2463 | 8.2 | 0.78
2464 | 8 | 0.79
2465 | 7.4 | 0.86
2466 | 7.1 | 0.87
2467 | 6.7 | 0.93
2468 | 6.6 | 0.93
2469 | 6.4 | 0.94
2470 | 6.3 | 0.94
2471 | 6.4 | 0.95
2472 | 6.3 | 0.94
2473 | 5.7 | 0.95
2474 | 5.6 | 0.95
2475 | 5.7 | 0.95
2476 | 5.9 | 0.95
2477 | 5.9 | 0.97
2478 | 5.7 | 0.97
2479 | 5.8 | 0.98
2480 | 6 | 0.97
2481 | 5.9 | 0.98
2482 | 5.7 | 0.97
2483 | 5.6 | 0.97
2484 | 5.7 | 0.98
2485 | 5.8 | 0.97
2486 | 5.7 | 0.98
2487 | 5.7 | 0.97
2488 | 5.6 | 0.97
2489 | 5.4 | 0.97
2490 | 5.6 | 0.97
2491 | 5.1 | 0.97
2492 | 5.1 | 0.97
2493 | 4.8 | 0.94
2494 | 5.1 | 0.95
2495 | 4.7 | 0.93
2496 | 4.8 | 0.95
2497 | 5.2 | 0.95
2498 | 5.5 | 0.98
2499 | 6 | 0.97
2500 | 6.5 | 0.97
2501 | 6.4 | 0.97
2502 | 6.6 | 0.98
2503 | 6.7 | 0.98
2504 | 7 | 0.99
2505 | 7 | 0.99
2506 | 7.2 | 0.99
2507 | 7.1 | 0.97
2508 | 6.9 | 0.97
2509 | 7 | 0.97
2510 | 7 | 0.96
2511 | 7 | 0.99
2512 | 7 | 0.97
2513 | 7.1 | 0.97
2514 | 7.3 | 0.99
2515 | 7.6 | 0.99
2516 | 8 | 1
2517 | 8.2 | 1
2518 | 8.3 | 0.99
2519 | 7.6 | 0.99
2520 | 6.3 | 1
2521 | 6.3 | 0.98
2522 | 6.5 | 1
2523 | 6.6 | 1
2524 | 7.2 | 1
2525 | 6.7 | 1
2526 | 6.6 | 1
2527 | 6.6 | 1
2528 | 6.7 | 0.98
2529 | 6.8 | 1
2530 | 8 | 1
2531 | 8.5 | 1
2532 | 10.4 | 0.95
2533 | 11 | 0.86
2534 | 11.7 | 0.83
2535 | 11.9 | 0.82
2536 | 11.1 | 0.81
2537 | 10.8 | 0.85
2538 | 10.8 | 0.89
2539 | 9.7 | 0.91
2540 | 9.3 | 0.95
2541 | 9.1 | 0.97
2542 | 8.9 | 0.97
2543 | 9 | 0.97
2544 | 8.9 | 0.97
2545 | 8.7 | 0.97
2546 | 8.9 | 0.97
2547 | 8.9 | 0.99
2548 | 8.8 | 0.99
2549 | 8.6 | 1
2550 | 8.8 | 0.99
2551 | 8.9 | 0.99
2552 | 8.9 | 1
2553 | 8.9 | 0.97
2554 | 8.9 | 0.97
2555 | 9.1 | 0.99
2556 | 9.4 | 0.96
2557 | 10.4 | 0.91
2558 | 11.8 | 0.79
2559 | 11.1 | 0.83
2560 | 10 | 0.88
2561 | 10 | 0.87
2562 | 10.7 | 0.84
2563 | 9.9 | 0.86
2564 | 9.6 | 0.85
2565 | 9.6 | 0.85
2566 | 9.6 | 0.83
2567 | 9 | 0.82
2568 | 9.2 | 0.83
2569 | 9 | 0.84
2570 | 9.2 | 0.87
2571 | 9.1 | 0.88
2572 | 9.3 | 0.88
2573 | 9.5 | 0.87
2574 | 9.2 | 0.88
2575 | 9.2 | 0.88
2576 | 9.6 | 0.87
2577 | 11.1 | 0.83
2578 | 12 | 0.8
2579 | 12.8 | 0.77
2580 | 13.3 | 0.75
2581 | 13.6 | 0.74
2582 | 14.1 | 0.72
2583 | 15 | 0.7
2584 | 14.3 | 0.72
2585 | 13.5 | 0.74
2586 | 13.7 | 0.72
2587 | 13 | 0.74
2588 | 11.9 | 0.77
2589 | 11.7 | 0.77
2590 | 11.1 | 0.8
2591 | 11.3 | 0.83
2592 | 11.1 | 0.84
2593 | 10.9 | 0.85
2594 | 10.2 | 0.87
2595 | 10.3 | 0.87
2596 | 10.1 | 0.87
2597 | 10.2 | 0.86
2598 | 10.1 | 0.88
2599 | 10.3 | 0.87
2600 | 11 | 0.87
2601 | 12.5 | 0.83
2602 | 13.9 | 0.8
2603 | 15.2 | 0.75
2604 | 16.6 | 0.7
2605 | 17.4 | 0.65
2606 | 16.5 | 0.67
2607 | 16.4 | 0.7
2608 | 17.4 | 0.63
2609 | 17.6 | 0.65
2610 | 15.8 | 0.61
2611 | 14.1 | 0.78
2612 | 12.1 | 0.81
2613 | 11.9 | 0.8
2614 | 10.7 | 0.84
2615 | 11.6 | 0.72
2616 | 10.4 | 0.83
2617 | 11.1 | 0.69
2618 | 10.6 | 0.75
2619 | 10.5 | 0.76
2620 | 9.6 | 0.88
2621 | 9.2 | 0.89
2622 | 9.1 | 0.89
2623 | 9.8 | 0.84
2624 | 11 | 0.78
2625 | 12.8 | 0.76
2626 | 15.5 | 0.61
2627 | 16.1 | 0.63
2628 | 17.1 | 0.52
2629 | 18.4 | 0.52
2630 | 18.9 | 0.53
2631 | 18.8 | 0.48
2632 | 17.5 | 0.57
2633 | 16.8 | 0.58
2634 | 16.6 | 0.58
2635 | 15.5 | 0.63
2636 | 13.6 | 0.72
2637 | 12.6 | 0.76
2638 | 12 | 0.75
2639 | 11 | 0.75
2640 | 11.5 | 0.7
2641 | 10.4 | 0.73
2642 | 10.1 | 0.79
2643 | 9.4 | 0.83
2644 | 9.2 | 0.84
2645 | 8.6 | 0.85
2646 | 7.3 | 0.93
2647 | 6.2 | 0.95
2648 | 6.5 | 0.98
2649 | 8.3 | 1
2650 | 8.5 | 1
2651 | 9.9 | 0.99
2652 | 11.8 | 0.95
2653 | 13.1 | 0.88
2654 | 12.8 | 0.89
2655 | 13.3 | 0.83
2656 | 13.5 | 0.77
2657 | 12.7 | 0.81
2658 | 11.5 | 0.85
2659 | 10.4 | 0.63
2660 | 9 | 0.95
2661 | 8.4 | 0.94
2662 | 8 | 0.96
2663 | 8.1 | 0.97
2664 | 7.9 | 0.96
2665 | 7.8 | 0.97
2666 | 7.4 | 0.97
2667 | 7.6 | 0.99
2668 | 8 | 0.99
2669 | 8.5 | 1
2670 | 8.4 | 0.99
2671 | 8.8 | 0.95
2672 | 10.4 | 0.87
2673 | 12 | 0.81
2674 | 13.2 | 0.78
2675 | 14.4 | 0.75
2676 | 14.4 | 0.73
2677 | 15.8 | 0.63
2678 | 15.7 | 0.62
2679 | 13.5 | 0.73
2680 | 14 | 0.72
2681 | 13.6 | 0.77
2682 | 11.7 | 0.89
2683 | 11.1 | 0.94
2684 | 10.8 | 0.96
2685 | 10.5 | 0.97
2686 | 10.4 | 0.99
2687 | 10.4 | 0.97
2688 | 10.1 | 0.97
2689 | 10 | 0.99
2690 | 9.9 | 0.99
2691 | 10 | 0.97
2692 | 10 | 0.96
2693 | 10.2 | 0.9
2694 | 10.6 | 0.87
2695 | 10.6 | 0.86
2696 | 10.9 | 0.86
2697 | 11.3 | 0.85
2698 | 12.2 | 0.83
2699 | 13.2 | 0.78
2700 | 13.5 | 0.76
2701 | 13.4 | 0.78
2702 | 14.3 | 0.78
2703 | 14 | 0.84
2704 | 14 | 0.83
2705 | 13.7 | 0.83
2706 | 13.6 | 0.84
2707 | 12.4 | 0.88
2708 | 11.3 | 0.91
2709 | 10.2 | 0.95
2710 | 10.5 | 0.96
2711 | 10.7 | 0.96
2712 | 10.5 | 0.96
2713 | 10.6 | 0.95
2714 | 10.7 | 0.99
2715 | 11 | 0.99
2716 | 11 | 1
2717 | 10.8 | 0.99
2718 | 10.4 | 1
2719 | 10.2 | 1
2720 | 10.1 | 0.99
2721 | 10.1 | 0.97
2722 | 10.4 | 0.94
2723 | 10.7 | 0.9
2724 | 10.5 | 0.92
2725 | 10.9 | 0.92
2726 | 11.1 | 0.92
2727 | 11.9 | 0.85
2728 | 11 | 0.87
2729 | 11.4 | 0.77
2730 | 10.2 | 0.82
2731 | 9.8 | 0.77
2732 | 9.1 | 0.84
2733 | 8.4 | 0.89
2734 | 7.5 | 0.93
2735 | 7.3 | 0.94
2736 | 7.4 | 0.96
2737 | 8.3 | 0.94
2738 | 7.9 | 0.96
2739 | 8 | 0.96
2740 | 8.6 | 0.94
2741 | 8.5 | 0.94
2742 | 7.7 | 0.97
2743 | 7.3 | 0.97
2744 | 8.4 | 0.96
2745 | 9.4 | 0.93
2746 | 10.3 | 0.85
2747 | 10.8 | 0.74
2748 | 11.3 | 0.77
2749 | 10.5 | 0.76
2750 | 12.6 | 0.68
2751 | 10.3 | 0.78
2752 | 10 | 0.82
2753 | 9 | 0.86
2754 | 11.8 | 0.82
2755 | 10.8 | 0.81
2756 | 9.2 | 0.87
2757 | 8.4 | 0.92
2758 | 7.9 | 0.94
2759 | 8.2 | 0.97
2760 | 8.2 | 0.97
2761 | 8.5 | 0.97
2762 | 8.9 | 0.97
2763 | 8.6 | 0.96
2764 | 8.3 | 0.94
2765 | 8 | 0.93
2766 | 7.7 | 0.9
2767 | 7.4 | 0.9
2768 | 7.3 | 0.87
2769 | 7.7 | 0.83
2770 | 7.8 | 0.8
2771 | 9.7 | 0.68
2772 | 9.2 | 0.72
2773 | 8.5 | 0.79
2774 | 8.1 | 0.93
2775 | 8.3 | 0.97
2776 | 9.9 | 0.88
2777 | 9.4 | 0.76
2778 | 7.8 | 0.8
2779 | 7 | 0.85
2780 | 6.3 | 0.89
2781 | 6.1 | 0.86
2782 | 5.9 | 0.85
2783 | 5.3 | 0.89
2784 | 4.7 | 0.84
2785 | 5.4 | 0.81
2786 | 5 | 0.75
2787 | 5.4 | 0.74
2788 | 3.9 | 0.85
2789 | 5 | 0.7
2790 | 4.7 | 0.79
2791 | 5 | 0.75
2792 | 6.2 | 0.7
2793 | 6.2 | 0.77
2794 | 7.1 | 0.73
2795 | 9.1 | 0.57
2796 | 9.6 | 0.57
2797 | 8.3 | 0.65
2798 | 10.5 | 0.51
2799 | 10.6 | 0.5
2800 | 10.5 | 0.53
2801 | 10.8 | 0.48
2802 | 9.8 | 0.61
2803 | 9.3 | 0.62
2804 | 8.7 | 0.61
2805 | 7.9 | 0.67
2806 | 5.9 | 0.79
2807 | 6.2 | 0.76
2808 | 7 | 0.77
2809 | 6.8 | 0.82
2810 | 6.7 | 0.84
2811 | 7 | 0.88
2812 | 7.1 | 0.96
2813 | 7.2 | 0.99
2814 | 7.6 | 1
2815 | 8.4 | 0.99
2816 | 9.6 | 1
2817 | 10.3 | 0.96
2818 | 12.3 | 0.87
2819 | 13.3 | 0.82
2820 | 14.3 | 0.75
2821 | 14.5 | 0.76
2822 | 14.7 | 0.75
2823 | 16.3 | 0.76
2824 | 14.9 | 0.8
2825 | 14.2 | 0.83
2826 | 13.7 | 0.83
2827 | 12.4 | 0.87
2828 | 11.2 | 0.89
2829 | 10.6 | 0.89
2830 | 10.3 | 0.95
2831 | 9.8 | 0.96
2832 | 9.9 | 0.99
2833 | 10.1 | 1
2834 | 10 | 0.99
2835 | 10.1 | 1
2836 | 10.1 | 1
2837 | 10.1 | 0.99
2838 | 9.7 | 0.99
2839 | 9.5 | 0.99
2840 | 9.9 | 0.99
2841 | 9.8 | 0.99
2842 | 9.4 | 0.99
2843 | 10.1 | 0.93
2844 | 9.9 | 0.93
2845 | 10.5 | 0.85
2846 | 11.2 | 0.8
2847 | 10.5 | 0.86
2848 | 10.3 | 0.9
2849 | 9.5 | 0.96
2850 | 9.5 | 0.96
2851 | 9.6 | 0.93
2852 | 9.3 | 0.97
2853 | 9.5 | 0.97
2854 | 9.6 | 0.97
2855 | 9.6 | 0.97
2856 | 9.6 | 0.97
2857 | 9.6 | 0.99
2858 | 9.7 | 0.99
2859 | 9.7 | 0.99
2860 | 9.8 | 0.99
2861 | 9.8 | 0.99
2862 | 9.8 | 1
2863 | 9.5 | 1
2864 | 9.7 | 0.99
2865 | 10 | 0.86
2866 | 10.9 | 0.8
2867 | 12.1 | 0.76
2868 | 12.4 | 0.73
2869 | 13.4 | 0.6
2870 | 14.4 | 0.63
2871 | 13.8 | 0.63
2872 | 15 | 0.61
2873 | 15.1 | 0.52
2874 | 13.6 | 0.51
2875 | 12.9 | 0.55
2876 | 11.6 | 0.53
2877 | 10.3 | 0.61
2878 | 9.4 | 0.74
2879 | 8.6 | 0.8
2880 | 7.8 | 0.82
2881 | 7.3 | 0.81
2882 | 6.8 | 0.84
2883 | 6.2 | 0.86
2884 | 5.7 | 0.91
2885 | 4.9 | 0.95
2886 | 5 | 0.9
2887 | 5.3 | 0.87
2888 | 6.4 | 0.84
2889 | 8.6 | 0.77
2890 | 10.2 | 0.68
2891 | 11.3 | 0.64
2892 | 11.9 | 0.65
2893 | 12.1 | 0.72
2894 | 11.9 | 0.67
2895 | 10.5 | 0.86
2896 | 12 | 0.75
2897 | 12.6 | 0.65
2898 | 13.6 | 0.57
2899 | 12 | 0.59
2900 | 10.8 | 0.7
2901 | 10 | 0.73
2902 | 9.1 | 0.79
2903 | 8.8 | 0.8
2904 | 8.5 | 0.81
2905 | 8.2 | 0.83
2906 | 7.7 | 0.86
2907 | 7.8 | 0.83
2908 | 7.3 | 0.86
2909 | 7 | 0.84
2910 | 7 | 0.84
2911 | 7.8 | 0.83
2912 | 8.2 | 0.79
2913 | 8.8 | 0.8
2914 | 9.2 | 0.83
2915 | 10.4 | 0.81
2916 | 10.3 | 0.75
2917 | 10.5 | 0.83
2918 | 10.1 | 0.88
2919 | 9.9 | 0.93
2920 | 9.9 | 0.96
2921 | 9.9 | 0.97
2922 | 10.1 | 0.97
2923 | 10.3 | 0.96
2924 | 10 | 0.96
2925 | 9.3 | 0.97
2926 | 9.1 | 0.97
2927 | 8.8 | 0.99
2928 | 9.1 | 0.99
2929 | 8.4 | 0.99
2930 | 8.3 | 1
2931 | 8.3 | 0.99
2932 | 8 | 0.99
2933 | 7.3 | 0.99
2934 | 6.8 | 0.99
2935 | 7.1 | 1
2936 | 7.4 | 0.97
2937 | 8.7 | 0.94
2938 | 9.6 | 0.82
2939 | 11.1 | 0.73
2940 | 11.7 | 0.66
2941 | 11.8 | 0.63
2942 | 12 | 0.61
2943 | 12.1 | 0.63
2944 | 12.2 | 0.62
2945 | 11.9 | 0.6
2946 | 11.8 | 0.54
2947 | 11.6 | 0.51
2948 | 11.1 | 0.56
2949 | 10.6 | 0.59
2950 | 10.1 | 0.6
2951 | 8.8 | 0.64
2952 | 7.1 | 0.74
2953 | 6 | 0.79
2954 | 5.4 | 0.83
2955 | 6 | 0.71
2956 | 4.8 | 0.73
2957 | 3.7 | 0.78
2958 | 2.9 | 0.79
2959 | 3.3 | 0.76
2960 | 4.4 | 0.72
2961 | 5.6 | 0.68
2962 | 6.7 | 0.62
2963 | 7.9 | 0.6
2964 | 9.4 | 0.54
2965 | 8.9 | 0.55
2966 | 9.9 | 0.55
2967 | 9.4 | 0.56
2968 | 10.3 | 0.62
2969 | 9.6 | 0.58
2970 | 9.7 | 0.6
2971 | 8.9 | 0.64
2972 | 7.6 | 0.7
2973 | 5.6 | 0.77
2974 | 5 | 0.73
2975 | 5.4 | 0.68
2976 | 5.4 | 0.65
2977 | 5.6 | 0.63
2978 | 5.6 | 0.66
2979 | 5.3 | 0.67
2980 | 4.8 | 0.71
2981 | 4.1 | 0.82
2982 | 3.9 | 0.83
2983 | 5 | 0.81
2984 | 6 | 0.77
2985 | 7.3 | 0.73
2986 | 9.8 | 0.61
2987 | 11 | 0.47
2988 | 12.3 | 0.48
2989 | 11.8 | 0.44
2990 | 12.8 | 0.47
2991 | 12.9 | 0.54
2992 | 12 | 0.55
2993 | 12 | 0.53
2994 | 11 | 0.49
2995 | 10.4 | 0.53
2996 | 8.5 | 0.64
2997 | 6 | 0.74
2998 | 4.3 | 0.82
2999 | 6 | 0.77
3000 | 5.7 | 0.78
3001 | 6.1 | 0.73
3002 | 5.7 | 0.75
3003 | 5.9 | 0.73
3004 | 6 | 0.73
3005 | 6.2 | 0.73
3006 | 6.6 | 0.69
3007 | 6.7 | 0.71
3008 | 7.8 | 0.71
3009 | 8.5 | 0.74
3010 | 9.1 | 0.71
3011 | 8.9 | 0.68
3012 | 10.2 | 0.67
3013 | 10.3 | 0.62
3014 | 11.4 | 0.61
3015 | 10.6 | 0.62
3016 | 10.5 | 0.64
3017 | 10 | 0.62
3018 | 9.8 | 0.67
3019 | 9.1 | 0.7
3020 | 8.4 | 0.71
3021 | 6.8 | 0.79
3022 | 6.6 | 0.81
3023 | 6.6 | 0.85
3024 | 6.6 | 0.9
3025 | 5.8 | 0.92
3026 | 5.8 | 0.92
3027 | 6.7 | 0.9
3028 | 7.6 | 0.91
3029 | 7.3 | 0.94
3030 | 6.8 | 0.96
3031 | 7 | 0.94
3032 | 7.8 | 0.96
3033 | 8.6 | 0.92
3034 | 9.7 | 0.86
3035 | 10.1 | 0.77
3036 | 11.3 | 0.66
3037 | 10.9 | 0.64
3038 | 10.2 | 0.71
3039 | 9.4 | 0.72
3040 | 10.1 | 0.61
3041 | 9.3 | 0.81
3042 | 8.5 | 0.88
3043 | 7.9 | 0.91
3044 | 7.7 | 0.96
3045 | 7.9 | 0.99
3046 | 7.9 | 0.97
3047 | 8.1 | 0.97
3048 | 7.9 | 0.99
3049 | 8.3 | 0.99
3050 | 8.1 | 0.99
3051 | 8.2 | 0.97
3052 | 7.9 | 0.97
3053 | 7.9 | 0.94
3054 | 7.6 | 0.99
3055 | 7.4 | 0.97
3056 | 7.3 | 0.97
3057 | 7.5 | 0.97
3058 | 7.7 | 0.94
3059 | 7.7 | 0.96
3060 | 7.9 | 0.91
3061 | 8.2 | 0.9
3062 | 8.4 | 0.89
3063 | 8.6 | 0.89
3064 | 8.8 | 0.85
3065 | 8.5 | 0.82
3066 | 8.3 | 0.82
3067 | 8 | 0.83
3068 | 8.2 | 0.82
3069 | 7.7 | 0.87
3070 | 7.7 | 0.87
3071 | 7.5 | 0.86
3072 | 6.9 | 0.87
3073 | 6.4 | 0.86
3074 | 6.2 | 0.89
3075 | 6.4 | 0.89
3076 | 5.7 | 0.91
3077 | 5.4 | 0.91
3078 | 4.9 | 0.89
3079 | 5.5 | 0.86
3080 | 6.5 | 0.81
3081 | 8 | 0.71
3082 | 8.7 | 0.67
3083 | 10.1 | 0.6
3084 | 10.8 | 0.56
3085 | 12 | 0.52
3086 | 11.9 | 0.5
3087 | 12.7 | 0.46
3088 | 13.1 | 0.43
3089 | 12.7 | 0.42
3090 | 12.5 | 0.39
3091 | 11.9 | 0.4
3092 | 11 | 0.45
3093 | 9.2 | 0.57
3094 | 7.8 | 0.64
3095 | 6.7 | 0.68
3096 | 5.9 | 0.71
3097 | 5.7 | 0.74
3098 | 5.4 | 0.77
3099 | 5.4 | 0.75
3100 | 5 | 0.75
3101 | 4.6 | 0.79
3102 | 4.8 | 0.78
3103 | 5.1 | 0.76
3104 | 7.6 | 0.66
3105 | 8.9 | 0.67
3106 | 9.4 | 0.57
3107 | 10.1 | 0.59
3108 | 10.8 | 0.53
3109 | 11.8 | 0.51
3110 | 11.9 | 0.62
3111 | 10.7 | 0.63
3112 | 12.1 | 0.6
3113 | 11.9 | 0.61
3114 | 12.2 | 0.63
3115 | 10 | 0.69
3116 | 9.2 | 0.79
3117 | 8.6 | 0.77
3118 | 8.1 | 0.82
3119 | 7.9 | 0.82
3120 | 7.4 | 0.81
3121 | 6.9 | 0.81
3122 | 5.8 | 0.86
3123 | 5.4 | 0.89
3124 | 5.1 | 0.92
3125 | 5 | 0.94
3126 | 5 | 0.94
3127 | 5.1 | 0.94
3128 | 5.6 | 0.92
3129 | 7.3 | 0.84
3130 | 9.7 | 0.74
3131 | 10.9 | 0.64
3132 | 11 | 0.58
3133 | 12.2 | 0.5
3134 | 13.5 | 0.43
3135 | 13 | 0.45
3136 | 13.4 | 0.45
3137 | 13.7 | 0.44
3138 | 13.7 | 0.64
3139 | 12.4 | 0.65
3140 | 10.9 | 0.66
3141 | 8.5 | 0.75
3142 | 7.3 | 0.74
3143 | 8.9 | 0.67
3144 | 8.6 | 0.66
3145 | 8.4 | 0.66
3146 | 8.5 | 0.7
3147 | 7.3 | 0.76
3148 | 5.4 | 0.83
3149 | 5.7 | 0.82
3150 | 6.1 | 0.86
3151 | 8.1 | 0.87
3152 | 9.3 | 0.89
3153 | 10.3 | 0.86
3154 | 11.8 | 0.73
3155 | 12.4 | 0.62
3156 | 12.8 | 0.65
3157 | 12.9 | 0.63
3158 | 12.9 | 0.67
3159 | 13.3 | 0.55
3160 | 13.3 | 0.53
3161 | 13.2 | 0.54
3162 | 12.4 | 0.48
3163 | 11.7 | 0.49
3164 | 9.8 | 0.65
3165 | 8.5 | 0.81
3166 | 7.8 | 0.89
3167 | 8.1 | 0.92
3168 | 8 | 0.93
3169 | 7.5 | 0.93
3170 | 7.6 | 0.93
3171 | 7.9 | 0.94
3172 | 8.1 | 0.96
3173 | 8.6 | 0.96
3174 | 8.6 | 0.96
3175 | 9.5 | 0.93
3176 | 10.6 | 0.86
3177 | 11.5 | 0.75
3178 | 12.6 | 0.7
3179 | 13.2 | 0.69
3180 | 13.6 | 0.66
3181 | 13.6 | 0.71
3182 | 13.6 | 0.71
3183 | 13.4 | 0.71
3184 | 13.2 | 0.72
3185 | 12.7 | 0.69
3186 | 12.3 | 0.7
3187 | 11.7 | 0.78
3188 | 10.5 | 0.8
3189 | 9.3 | 0.89
3190 | 8.5 | 0.92
3191 | 8.2 | 0.93
3192 | 8.2 | 0.9
3193 | 8.1 | 0.87
3194 | 8.1 | 0.85
3195 | 8.1 | 0.79
3196 | 8.5 | 0.86
3197 | 8.6 | 0.84
3198 | 8.9 | 0.88
3199 | 9.4 | 0.87
3200 | 10.2 | 0.85
3201 | 10.9 | 0.78
3202 | 12.1 | 0.74
3203 | 12.9 | 0.71
3204 | 13.6 | 0.68
3205 | 13.7 | 0.68
3206 | 13.9 | 0.7
3207 | 13.7 | 0.71
3208 | 13.6 | 0.72
3209 | 13.1 | 0.75
3210 | 12.7 | 0.72
3211 | 12.1 | 0.73
3212 | 11.5 | 0.72
3213 | 10.6 | 0.71
3214 | 10.4 | 0.69
3215 | 10.2 | 0.7
3216 | 9.8 | 0.74
3217 | 9.2 | 0.77
3218 | 9.1 | 0.89
3219 | 9.5 | 0.83
3220 | 9.6 | 0.82
3221 | 9.5 | 0.85
3222 | 10.4 | 0.8
3223 | 10.5 | 0.79
3224 | 10.7 | 0.77
3225 | 11.1 | 0.83
3226 | 11.5 | 0.78
3227 | 12.6 | 0.8
3228 | 13.2 | 0.8
3229 | 14.1 | 0.75
3230 | 14.6 | 0.76
3231 | 13.6 | 0.77
3232 | 13.1 | 0.78
3233 | 12.7 | 0.79
3234 | 12.3 | 0.82
3235 | 11.5 | 0.85
3236 | 11.1 | 0.89
3237 | 10.7 | 0.92
3238 | 10.4 | 0.94
3239 | 10.2 | 0.95
3240 | 10.1 | 0.93
3241 | 10 | 0.96
3242 | 10 | 0.95
3243 | 10.2 | 0.93
3244 | 10.1 | 0.88
3245 | 10 | 0.88
3246 | 9.8 | 0.93
3247 | 9.9 | 0.91
3248 | 10.2 | 0.91
3249 | 10.7 | 0.87
3250 | 11.3 | 0.85
3251 | 11.7 | 0.76
3252 | 12.3 | 0.68
3253 | 12.4 | 0.71
3254 | 13.3 | 0.7
3255 | 13.3 | 0.72
3256 | 12.3 | 0.73
3257 | 11.8 | 0.73
3258 | 11.6 | 0.73
3259 | 11.6 | 0.76
3260 | 11.1 | 0.77
3261 | 10.4 | 0.8
3262 | 9.8 | 0.84
3263 | 9.7 | 0.87
3264 | 9.9 | 0.91
3265 | 9.6 | 0.91
3266 | 9.4 | 0.93
3267 | 9.2 | 0.95
3268 | 9.2 | 0.96
3269 | 9.1 | 0.96
3270 | 8.9 | 0.96
3271 | 9 | 0.97
3272 | 9.7 | 0.93
3273 | 10.6 | 0.89
3274 | 11.6 | 0.81
3275 | 12.8 | 0.71
3276 | 14.5 | 0.64
3277 | 14.8 | 0.64
3278 | 15.3 | 0.62
3279 | 14.6 | 0.71
3280 | 12.8 | 0.73
3281 | 14.2 | 0.7
3282 | 13 | 0.64
3283 | 12 | 0.68
3284 | 11.4 | 0.72
3285 | 10.6 | 0.82
3286 | 10.6 | 0.9
3287 | 10.2 | 0.93
3288 | 9.7 | 0.96
3289 | 9.6 | 0.96
3290 | 9.4 | 0.95
3291 | 9.3 | 0.96
3292 | 9.4 | 0.96
3293 | 9.5 | 0.96
3294 | 9.4 | 0.95
3295 | 9.4 | 0.93
3296 | 9.3 | 0.92
3297 | 10 | 0.88
3298 | 11 | 0.83
3299 | 12.4 | 0.75
3300 | 13.7 | 0.7
3301 | 13.5 | 0.63
3302 | 13.5 | 0.63
3303 | 15.4 | 0.62
3304 | 15 | 0.58
3305 | 14.8 | 0.6
3306 | 14.1 | 0.64
3307 | 12.4 | 0.73
3308 | 11.5 | 0.82
3309 | 10.9 | 0.81
3310 | 10.6 | 0.82
3311 | 10.4 | 0.82
3312 | 10 | 0.83
3313 | 9.8 | 0.86
3314 | 9.6 | 0.85
3315 | 9 | 0.86
3316 | 8.6 | 0.89
3317 | 8.3 | 0.92
3318 | 8.2 | 0.92
3319 | 8.6 | 0.9
3320 | 10.2 | 0.81
3321 | 10.8 | 0.74
3322 | 11.6 | 0.68
3323 | 12.8 | 0.61
3324 | 14.7 | 0.56
3325 | 14.7 | 0.49
3326 | 14.1 | 0.51
3327 | 14.6 | 0.48
3328 | 15.1 | 0.49
3329 | 15.8 | 0.44
3330 | 15.5 | 0.46
3331 | 15.1 | 0.46
3332 | 13.9 | 0.54
3333 | 11.8 | 0.65
3334 | 10.3 | 0.69
3335 | 9 | 0.72
3336 | 8.3 | 0.79
3337 | 7.7 | 0.83
3338 | 7.7 | 0.84
3339 | 7.6 | 0.86
3340 | 7 | 0.88
3341 | 6.9 | 0.9
3342 | 6.6 | 0.9
3343 | 7.2 | 0.88
3344 | 8.4 | 0.85
3345 | 10.4 | 0.77
3346 | 12.6 | 0.67
3347 | 13.3 | 0.6
3348 | 14.2 | 0.52
3349 | 14.4 | 0.47
3350 | 14.4 | 0.62
3351 | 15.7 | 0.59
3352 | 15.4 | 0.56
3353 | 13.6 | 0.66
3354 | 13.7 | 0.63
3355 | 13.3 | 0.7
3356 | 12.6 | 0.73
3357 | 11.7 | 0.75
3358 | 11.3 | 0.76
3359 | 10.7 | 0.77
3360 | 10.5 | 0.77
3361 | 10.3 | 0.75
3362 | 10 | 0.73
3363 | 9.4 | 0.72
3364 | 8.6 | 0.73
3365 | 8.5 | 0.71
3366 | 8.5 | 0.7
3367 | 9.6 | 0.7
3368 | 9.6 | 0.73
3369 | 10.9 | 0.7
3370 | 13.3 | 0.63
3371 | 14.8 | 0.55
3372 | 15.5 | 0.51
3373 | 16.2 | 0.48
3374 | 16.1 | 0.47
3375 | 16.5 | 0.56
3376 | 15.1 | 0.6
3377 | 15.6 | 0.59
3378 | 15 | 0.61
3379 | 13.9 | 0.58
3380 | 12.8 | 0.54
3381 | 10.5 | 0.71
3382 | 8.4 | 0.88
3383 | 7.5 | 0.91
3384 | 8.6 | 0.89
3385 | 9.4 | 0.87
3386 | 9.3 | 0.87
3387 | 9.6 | 0.87
3388 | 9.8 | 0.84
3389 | 9.8 | 0.86
3390 | 9.3 | 0.87
3391 | 10.1 | 0.87
3392 | 11.1 | 0.84
3393 | 11.4 | 0.77
3394 | 12.1 | 0.71
3395 | 12.5 | 0.74
3396 | 14.4 | 0.69
3397 | 13.1 | 0.75
3398 | 12.7 | 0.74
3399 | 14.3 | 0.67
3400 | 15.2 | 0.66
3401 | 14.1 | 0.68
3402 | 13.8 | 0.7
3403 | 12.6 | 0.76
3404 | 12.1 | 0.81
3405 | 11 | 0.85
3406 | 9.5 | 0.91
3407 | 9.7 | 0.92
3408 | 10.1 | 0.92
3409 | 9.9 | 0.95
3410 | 10.3 | 0.94
3411 | 10.3 | 0.95
3412 | 10.3 | 0.95
3413 | 10.6 | 0.95
3414 | 10.5 | 0.96
3415 | 11.3 | 0.94
3416 | 11.7 | 0.93
3417 | 12.4 | 0.87
3418 | 12.3 | 0.88
3419 | 12.6 | 0.87
3420 | 11.9 | 0.93
3421 | 12.7 | 0.86
3422 | 14.7 | 0.74
3423 | 14.9 | 0.73
3424 | 14.9 | 0.71
3425 | 15.1 | 0.72
3426 | 15.3 | 0.74
3427 | 15.4 | 0.75
3428 | 13.5 | 0.85
3429 | 13.5 | 0.85
3430 | 12.7 | 0.87
3431 | 11.9 | 0.9
3432 | 11 | 0.9
3433 | 10.2 | 0.92
3434 | 10.1 | 0.93
3435 | 10.4 | 0.95
3436 | 10.6 | 0.96
3437 | 10.3 | 0.97
3438 | 10.5 | 0.96
3439 | 11.5 | 0.93
3440 | 12.3 | 0.92
3441 | 13.2 | 0.88
3442 | 13.4 | 0.87
3443 | 13.8 | 0.86
3444 | 14.2 | 0.84
3445 | 15.4 | 0.78
3446 | 15.5 | 0.72
3447 | 15.5 | 0.72
3448 | 16 | 0.67
3449 | 16.6 | 0.61
3450 | 16.5 | 0.62
3451 | 16.8 | 0.63
3452 | 15.7 | 0.65
3453 | 15.1 | 0.68
3454 | 14.6 | 0.72
3455 | 14.4 | 0.74
3456 | 13.4 | 0.85
3457 | 13 | 0.86
3458 | 12.8 | 0.85
3459 | 12.7 | 0.86
3460 | 12.4 | 0.89
3461 | 12.7 | 0.89
3462 | 12.6 | 0.92
3463 | 12.6 | 0.95
3464 | 13.2 | 0.93
3465 | 14.2 | 0.88
3466 | 16.2 | 0.76
3467 | 17.3 | 0.66
3468 | 17.7 | 0.67
3469 | 17.5 | 0.7
3470 | 17.1 | 0.74
3471 | 19 | 0.69
3472 | 19.5 | 0.7
3473 | 19.2 | 0.7
3474 | 20 | 0.67
3475 | 18.6 | 0.71
3476 | 17.3 | 0.73
3477 | 16.4 | 0.75
3478 | 15.1 | 0.84
3479 | 13.5 | 0.93
3480 | 13.5 | 0.94
3481 | 13.1 | 0.98
3482 | 13 | 0.98
3483 | 12.9 | 0.99
3484 | 13 | 0.98
3485 | 13.1 | 0.98
3486 | 13 | 0.98
3487 | 13.2 | 0.98
3488 | 14 | 0.94
3489 | 13.9 | 0.84
3490 | 12.8 | 0.77
3491 | 13.7 | 0.66
3492 | 14.7 | 0.61
3493 | 15.7 | 0.58
3494 | 15.8 | 0.56
3495 | 16.7 | 0.55
3496 | 16.8 | 0.51
3497 | 16.5 | 0.54
3498 | 15.8 | 0.54
3499 | 14.7 | 0.58
3500 | 14 | 0.63
3501 | 13.3 | 0.66
3502 | 12.5 | 0.72
3503 | 11.4 | 0.77
3504 | 10.3 | 0.82
3505 | 10.5 | 0.83
3506 | 10.7 | 0.89
3507 | 11 | 0.83
3508 | 10.7 | 0.8
3509 | 9.4 | 0.87
3510 | 9.5 | 0.84
3511 | 10.9 | 0.78
3512 | 11.4 | 0.77
3513 | 11.9 | 0.74
3514 | 13.3 | 0.67
3515 | 13.2 | 0.58
3516 | 14.6 | 0.58
3517 | 14.1 | 0.65
3518 | 15.5 | 0.59
3519 | 13.2 | 0.67
3520 | 12 | 0.76
3521 | 13.9 | 0.63
3522 | 12.8 | 0.62
3523 | 12.9 | 0.59
3524 | 11.8 | 0.65
3525 | 10.9 | 0.7
3526 | 10.2 | 0.76
3527 | 9.6 | 0.79
3528 | 9.3 | 0.83
3529 | 8.9 | 0.88
3530 | 8.8 | 0.86
3531 | 8.7 | 0.85
3532 | 9.2 | 0.84
3533 | 8.7 | 0.88
3534 | 8.4 | 0.86
3535 | 8.7 | 0.84
3536 | 10.1 | 0.77
3537 | 10.6 | 0.75
3538 | 11.8 | 0.66
3539 | 12.9 | 0.56
3540 | 13.4 | 0.55
3541 | 13.6 | 0.54
3542 | 14.3 | 0.5
3543 | 13.9 | 0.53
3544 | 14.8 | 0.51
3545 | 12.6 | 0.69
3546 | 13.1 | 0.69
3547 | 13.3 | 0.73
3548 | 12.6 | 0.74
3549 | 10.8 | 0.87
3550 | 9 | 0.92
3551 | 8.6 | 0.96
3552 | 8.9 | 0.97
3553 | 9.1 | 0.99
3554 | 9.8 | 0.99
3555 | 11.3 | 0.99
3556 | 11.4 | 0.99
3557 | 11.1 | 0.99
3558 | 11.6 | 0.99
3559 | 12.6 | 0.98
3560 | 13.1 | 0.96
3561 | 13.6 | 0.94
3562 | 14.6 | 0.91
3563 | 15.3 | 0.86
3564 | 15.4 | 0.93
3565 | 16.1 | 0.85
3566 | 15.8 | 0.87
3567 | 15.3 | 0.88
3568 | 16 | 0.84
3569 | 15.7 | 0.84
3570 | 15.5 | 0.87
3571 | 15.6 | 0.88
3572 | 14.8 | 0.88
3573 | 14.1 | 0.9
3574 | 13.3 | 0.91
3575 | 13 | 0.93
3576 | 13.3 | 0.93
3577 | 13.5 | 0.93
3578 | 13.3 | 0.94
3579 | 13.4 | 0.94
3580 | 13.3 | 0.93
3581 | 13.1 | 0.94
3582 | 12.9 | 0.94
3583 | 13.6 | 0.92
3584 | 15 | 0.86
3585 | 14.7 | 0.89
3586 | 15.4 | 0.86
3587 | 14.8 | 0.89
3588 | 15.6 | 0.86
3589 | 15.5 | 0.86
3590 | 17.2 | 0.8
3591 | 17.3 | 0.83
3592 | 17.4 | 0.76
3593 | 16.7 | 0.77
3594 | 16.1 | 0.82
3595 | 14.9 | 0.92
3596 | 14.4 | 0.94
3597 | 13.7 | 0.98
3598 | 13.4 | 1
3599 | 13.1 | 1
3600 | 13.1 | 0.99
3601 | 12.9 | 1
3602 | 12.8 | 0.99
3603 | 12.8 | 1
3604 | 12.7 | 1
3605 | 12.7 | 1
3606 | 12.7 | 1
3607 | 12.8 | 0.99
3608 | 12.5 | 1
3609 | 12.4 | 0.99
3610 | 12.3 | 0.95
3611 | 12.6 | 0.96
3612 | 13.5 | 0.9
3613 | 13 | 0.95
3614 | 13.2 | 0.93
3615 | 13.2 | 0.95
3616 | 13 | 0.98
3617 | 13.7 | 0.97
3618 | 14.8 | 0.9
3619 | 15 | 0.87
3620 | 14.8 | 0.86
3621 | 13.4 | 0.91
3622 | 11.5 | 0.93
3623 | 10.2 | 0.96
3624 | 9.4 | 0.99
3625 | 9.1 | 1
3626 | 10.1 | 0.99
3627 | 10.4 | 1
3628 | 10.6 | 1
3629 | 10.6 | 1
3630 | 10.9 | 0.99
3631 | 11 | 0.99
3632 | 11.4 | 1
3633 | 11.9 | 1
3634 | 12.6 | 1
3635 | 12.7 | 0.99
3636 | 14 | 0.92
3637 | 14.6 | 0.9
3638 | 14.3 | 0.93
3639 | 14 | 0.99
3640 | 14.1 | 0.98
3641 | 14 | 0.99
3642 | 13.9 | 0.99
3643 | 13.5 | 0.99
3644 | 13.3 | 0.99
3645 | 12.7 | 1
3646 | 12.6 | 1
3647 | 12.5 | 0.99
3648 | 12.9 | 0.99
3649 | 12.9 | 0.99
3650 | 13.1 | 1
3651 | 13.3 | 0.99
3652 | 13.6 | 0.99
3653 | 12.9 | 0.99
3654 | 12.2 | 0.95
3655 | 11.8 | 0.96
3656 | 12.1 | 0.95
3657 | 12.4 | 0.8
3658 | 13.4 | 0.72
3659 | 14.3 | 0.68
3660 | 13.9 | 0.65
3661 | 15 | 0.61
3662 | 13 | 0.73
3663 | 13.2 | 0.75
3664 | 13.1 | 0.85
3665 | 14.3 | 0.72
3666 | 14 | 0.67
3667 | 13.4 | 0.68
3668 | 13 | 0.69
3669 | 11.4 | 0.76
3670 | 10 | 0.76
3671 | 9.2 | 0.84
3672 | 8.2 | 0.92
3673 | 8.3 | 0.94
3674 | 8.2 | 0.96
3675 | 7.7 | 0.96
3676 | 6.9 | 0.97
3677 | 6.7 | 0.96
3678 | 7.2 | 0.94
3679 | 8.5 | 0.93
3680 | 10.2 | 0.88
3681 | 11.8 | 0.75
3682 | 11.8 | 0.7
3683 | 12.8 | 0.7
3684 | 12 | 0.75
3685 | 14.1 | 0.68
3686 | 10.7 | 0.85
3687 | 12.6 | 0.68
3688 | 12.6 | 0.77
3689 | 12.9 | 0.7
3690 | 12.6 | 0.77
3691 | 12.8 | 0.71
3692 | 11.3 | 0.79
3693 | 10.8 | 0.85
3694 | 10.1 | 0.92
3695 | 9.6 | 0.93
3696 | 9.9 | 0.95
3697 | 10.1 | 0.99
3698 | 9.9 | 0.99
3699 | 9.8 | 0.97
3700 | 9.6 | 0.97
3701 | 9.8 | 0.99
3702 | 9.5 | 0.99
3703 | 9.5 | 0.99
3704 | 9.6 | 0.97
3705 | 9.6 | 0.96
3706 | 9.6 | 0.95
3707 | 9.6 | 0.95
3708 | 10.4 | 0.92
3709 | 11.5 | 0.83
3710 | 11.5 | 0.73
3711 | 12 | 0.72
3712 | 12.6 | 0.68
3713 | 12.4 | 0.67
3714 | 11.9 | 0.71
3715 | 11.2 | 0.74
3716 | 11.1 | 0.73
3717 | 9 | 0.89
3718 | 9 | 0.88
3719 | 8.4 | 0.89
3720 | 8.4 | 0.9
3721 | 8.4 | 0.82
3722 | 8.2 | 0.9
3723 | 8.1 | 0.92
3724 | 8.2 | 0.92
3725 | 7.8 | 0.93
3726 | 7.7 | 0.9
3727 | 8.1 | 0.86
3728 | 9.7 | 0.82
3729 | 10.5 | 0.76
3730 | 11.5 | 0.68
3731 | 11.4 | 0.67
3732 | 13.6 | 0.59
3733 | 13.2 | 0.57
3734 | 13.1 | 0.58
3735 | 11.9 | 0.66
3736 | 10.5 | 0.79
3737 | 10.2 | 0.8
3738 | 8.9 | 0.89
3739 | 9.4 | 0.87
3740 | 9.3 | 0.91
3741 | 8.3 | 0.93
3742 | 8.1 | 0.96
3743 | 8.6 | 0.86
3744 | 8.3 | 0.82
3745 | 8 | 0.83
3746 | 7.3 | 0.88
3747 | 6.7 | 0.9
3748 | 6.3 | 0.91
3749 | 5.9 | 0.92
3750 | 5.9 | 0.92
3751 | 6.9 | 0.88
3752 | 8.3 | 0.86
3753 | 9.4 | 0.8
3754 | 10.9 | 0.73
3755 | 12.2 | 0.62
3756 | 11.5 | 0.53
3757 | 11.4 | 0.59
3758 | 11.2 | 0.71
3759 | 12.8 | 0.66
3760 | 13.4 | 0.62
3761 | 13.3 | 0.62
3762 | 12.8 | 0.67
3763 | 11.4 | 0.71
3764 | 11.2 | 0.72
3765 | 10.4 | 0.73
3766 | 9.3 | 0.79
3767 | 8.5 | 0.82
3768 | 8.3 | 0.82
3769 | 7.9 | 0.86
3770 | 7.7 | 0.87
3771 | 6.6 | 0.93
3772 | 6.4 | 0.95
3773 | 6.3 | 0.92
3774 | 6.8 | 0.9
3775 | 7.9 | 0.84
3776 | 8.9 | 0.82
3777 | 10.1 | 0.74
3778 | 11.8 | 0.69
3779 | 13.4 | 0.63
3780 | 13.5 | 0.64
3781 | 14.6 | 0.61
3782 | 15.3 | 0.6
3783 | 14.6 | 0.65
3784 | 12.7 | 0.8
3785 | 13.9 | 0.7
3786 | 13.3 | 0.72
3787 | 13.6 | 0.67
3788 | 13.1 | 0.68
3789 | 12.1 | 0.71
3790 | 10.4 | 0.75
3791 | 9.4 | 0.81
3792 | 8.8 | 0.84
3793 | 8.3 | 0.87
3794 | 8.2 | 0.87
3795 | 8 | 0.87
3796 | 7.8 | 0.89
3797 | 7.9 | 0.89
3798 | 7.9 | 0.9
3799 | 8.9 | 0.85
3800 | 9.9 | 0.81
3801 | 10.8 | 0.75
3802 | 11.2 | 0.73
3803 | 12.8 | 0.65
3804 | 13.6 | 0.63
3805 | 12.3 | 0.74
3806 | 14.2 | 0.6
3807 | 14.5 | 0.5
3808 | 14.7 | 0.57
3809 | 14.5 | 0.57
3810 | 14.6 | 0.57
3811 | 13.8 | 0.6
3812 | 12.9 | 0.67
3813 | 11.9 | 0.66
3814 | 10.8 | 0.73
3815 | 9.5 | 0.76
3816 | 8.1 | 0.86
3817 | 8.7 | 0.89
3818 | 8.2 | 0.89
3819 | 7.1 | 0.91
3820 | 7.6 | 0.91
3821 | 6 | 0.92
3822 | 6.8 | 0.94
3823 | 8.5 | 0.94
3824 | 10.1 | 0.86
3825 | 11.5 | 0.82
3826 | 11.8 | 0.71
3827 | 12.5 | 0.79
3828 | 11.1 | 0.86
3829 | 8.7 | 0.92
3830 | 13.1 | 0.8
3831 | 10 | 0.81
3832 | 10.5 | 0.9
3833 | 10.3 | 0.83
3834 | 12.2 | 0.77
3835 | 11 | 0.8
3836 | 11 | 0.79
3837 | 9.9 | 0.87
3838 | 8.7 | 0.93
3839 | 8.3 | 0.9
3840 | 8.2 | 0.93
3841 | 8.7 | 0.9
3842 | 8 | 0.94
3843 | 7.7 | 0.96
3844 | 7.2 | 0.97
3845 | 6.7 | 0.94
3846 | 6.3 | 0.97
3847 | 7.5 | 0.9
3848 | 8.4 | 0.89
3849 | 10 | 0.83
3850 | 11.6 | 0.7
3851 | 12.8 | 0.66
3852 | 13.3 | 0.63
3853 | 13.7 | 0.57
3854 | 14.6 | 0.58
3855 | 15.1 | 0.54
3856 | 15.6 | 0.52
3857 | 12.5 | 0.65
3858 | 13.8 | 0.72
3859 | 13.5 | 0.69
3860 | 13.1 | 0.69
3861 | 12.8 | 0.71
3862 | 11.3 | 0.82
3863 | 11.1 | 0.77
3864 | 10.1 | 0.83
3865 | 9.7 | 0.83
3866 | 9.2 | 0.85
3867 | 8.9 | 0.86
3868 | 8.1 | 0.9
3869 | 7.4 | 0.9
3870 | 7.7 | 0.87
3871 | 8.6 | 0.85
3872 | 9.1 | 0.8
3873 | 9.9 | 0.75
3874 | 10.7 | 0.74
3875 | 12.4 | 0.65
3876 | 13.5 | 0.61
3877 | 14.7 | 0.56
3878 | 15 | 0.55
3879 | 15.2 | 0.54
3880 | 15.6 | 0.5
3881 | 15.9 | 0.5
3882 | 15.6 | 0.5
3883 | 14.9 | 0.53
3884 | 14 | 0.57
3885 | 13.1 | 0.69
3886 | 10.9 | 0.89
3887 | 10.6 | 0.89
3888 | 10.6 | 0.86
3889 | 10.5 | 0.86
3890 | 10.4 | 0.85
3891 | 9.1 | 0.89
3892 | 8.8 | 0.88
3893 | 8 | 0.9
3894 | 8.6 | 0.88
3895 | 9 | 0.88
3896 | 9.1 | 0.89
3897 | 10.3 | 0.83
3898 | 10.5 | 0.83
3899 | 11.1 | 0.79
3900 | 11.9 | 0.71
3901 | 11.2 | 0.77
3902 | 10.9 | 0.79
3903 | 11.4 | 0.76
3904 | 11.3 | 0.74
3905 | 11.6 | 0.75
3906 | 11.9 | 0.75
3907 | 11.8 | 0.76
3908 | 11.5 | 0.77
3909 | 10.8 | 0.85
3910 | 10.5 | 0.85
3911 | 10.4 | 0.85
3912 | 10 | 0.95
3913 | 9.8 | 0.95
3914 | 9.6 | 0.92
3915 | 9.3 | 0.93
3916 | 9.2 | 0.93
3917 | 9.2 | 0.96
3918 | 9.3 | 0.96
3919 | 9.6 | 0.96
3920 | 9.9 | 0.95
3921 | 10.2 | 0.92
3922 | 10.4 | 0.91
3923 | 11.5 | 0.86
3924 | 11.4 | 0.89
3925 | 10.5 | 0.92
3926 | 11.8 | 0.81
3927 | 11.4 | 0.78
3928 | 10.7 | 0.81
3929 | 12 | 0.74
3930 | 12 | 0.66
3931 | 11.4 | 0.64
3932 | 11.1 | 0.67
3933 | 10.8 | 0.69
3934 | 10.2 | 0.75
3935 | 9.9 | 0.78
3936 | 8.8 | 0.84
3937 | 8.9 | 0.84
3938 | 7.2 | 0.91
3939 | 7.8 | 0.93
3940 | 8.7 | 0.85
3941 | 8.3 | 0.92
3942 | 7.5 | 0.96
3943 | 9 | 0.95
3944 | 10.2 | 0.92
3945 | 10.6 | 0.94
3946 | 11.1 | 0.96
3947 | 12.3 | 0.81
3948 | 12.2 | 0.74
3949 | 12.7 | 0.68
3950 | 12.4 | 0.64
3951 | 12.5 | 0.64
3952 | 10.4 | 0.86
3953 | 10.2 | 0.96
3954 | 10 | 0.95
3955 | 9.8 | 0.91
3956 | 9.8 | 0.86
3957 | 9.7 | 0.87
3958 | 9.8 | 0.87
3959 | 9.4 | 0.91
3960 | 8.7 | 0.96
3961 | 8.4 | 0.88
3962 | 7.7 | 0.87
3963 | 7.6 | 0.86
3964 | 7.2 | 0.84
3965 | 7.6 | 0.86
3966 | 7.5 | 0.86
3967 | 7.9 | 0.83
3968 | 9.5 | 0.78
3969 | 11 | 0.73
3970 | 11.8 | 0.66
3971 | 13.3 | 0.58
3972 | 13.1 | 0.68
3973 | 12.9 | 0.67
3974 | 11.9 | 0.68
3975 | 12.7 | 0.62
3976 | 13.4 | 0.63
3977 | 12.4 | 0.7
3978 | 12.3 | 0.66
3979 | 12.7 | 0.7
3980 | 11.2 | 0.72
3981 | 10.3 | 0.83
3982 | 7.9 | 0.89
3983 | 7.8 | 0.93
3984 | 7.6 | 0.96
3985 | 7.2 | 0.97
3986 | 7.9 | 0.96
3987 | 8.2 | 0.96
3988 | 8.6 | 0.93
3989 | 9 | 0.95
3990 | 9.2 | 0.96
3991 | 9.6 | 0.96
3992 | 11.2 | 0.92
3993 | 11.9 | 0.85
3994 | 11.9 | 0.85
3995 | 13.5 | 0.76
3996 | 13.9 | 0.83
3997 | 12.5 | 0.94
3998 | 12.2 | 0.99
3999 | 12.9 | 0.98
4000 | 14.2 | 0.89
4001 | 15.1 | 0.82
4002 | 15.2 | 0.75
4003 | 13.1 | 0.84
4004 | 12.7 | 0.79
4005 | 12 | 0.82
4006 | 10.5 | 0.92
4007 | 10.5 | 0.96
4008 | 10.2 | 0.95
4009 | 9.9 | 0.97
4010 | 9.7 | 0.96
4011 | 9.9 | 0.97
4012 | 9.7 | 0.96
4013 | 9.7 | 0.97
4014 | 10 | 0.97
4015 | 10.8 | 0.96
4016 | 12 | 0.91
4017 | 12.9 | 0.84
4018 | 13.2 | 0.79
4019 | 12.4 | 0.85
4020 | 13.7 | 0.83
4021 | 14 | 0.75
4022 | 14.6 | 0.73
4023 | 14.4 | 0.77
4024 | 14.3 | 0.78
4025 | 15.6 | 0.7
4026 | 15.4 | 0.69
4027 | 14.3 | 0.77
4028 | 13.7 | 0.78
4029 | 12.8 | 0.82
4030 | 10.5 | 0.88
4031 | 9.1 | 0.95
4032 | 9 | 0.96
4033 | 9.2 | 0.97
4034 | 9.5 | 0.96
4035 | 8.2 | 0.96
4036 | 9.1 | 0.96
4037 | 8.8 | 0.97
4038 | 8.6 | 0.97
4039 | 9.2 | 0.96
4040 | 9.9 | 0.93
4041 | 11.1 | 0.89
4042 | 12.5 | 0.86
4043 | 14.6 | 0.71
4044 | 15.6 | 0.61
4045 | 16.4 | 0.66
4046 | 14.8 | 0.71
4047 | 14.5 | 0.67
4048 | 15.4 | 0.71
4049 | 16 | 0.65
4050 | 15.4 | 0.75
4051 | 15 | 0.73
4052 | 14.1 | 0.78
4053 | 12.9 | 0.85
4054 | 13.1 | 0.79
4055 | 12.4 | 0.74
4056 | 11.5 | 0.76
4057 | 10.9 | 0.81
4058 | 10.3 | 0.86
4059 | 9.8 | 0.87
4060 | 9.1 | 0.91
4061 | 9.1 | 0.91
4062 | 8.9 | 0.92
4063 | 9.9 | 0.88
4064 | 10.9 | 0.84
4065 | 12.3 | 0.8
4066 | 13.9 | 0.72
4067 | 16.1 | 0.62
4068 | 15.9 | 0.58
4069 | 15.4 | 0.64
4070 | 15.9 | 0.58
4071 | 16 | 0.62
4072 | 14.7 | 0.71
4073 | 14.4 | 0.8
4074 | 14.9 | 0.67
4075 | 15.2 | 0.65
4076 | 13.1 | 0.68
4077 | 12.6 | 0.74
4078 | 10.9 | 0.81
4079 | 10.4 | 0.81
4080 | 9.7 | 0.87
4081 | 9.5 | 0.87
4082 | 9 | 0.9
4083 | 9.3 | 0.91
4084 | 8.6 | 0.9
4085 | 8.9 | 0.89
4086 | 8.9 | 0.88
4087 | 9.1 | 0.89
4088 | 11 | 0.81
4089 | 12 | 0.75
4090 | 12.7 | 0.65
4091 | 12.5 | 0.69
4092 | 14.3 | 0.61
4093 | 12.1 | 0.82
4094 | 14.6 | 0.59
4095 | 15 | 0.67
4096 | 14.9 | 0.58
4097 | 14.8 | 0.54
4098 | 15.6 | 0.56
4099 | 15.1 | 0.56
4100 | 14 | 0.6
4101 | 13.2 | 0.63
4102 | 11.6 | 0.7
4103 | 10.6 | 0.74
4104 | 9.9 | 0.75
4105 | 8.8 | 0.8
4106 | 8.9 | 0.78
4107 | 8 | 0.83
4108 | 8 | 0.86
4109 | 7.6 | 0.86
4110 | 8.2 | 0.83
4111 | 9.1 | 0.8
4112 | 10.5 | 0.76
4113 | 12.2 | 0.69
4114 | 13 | 0.63
4115 | 14.2 | 0.64
4116 | 14.4 | 0.63
4117 | 15 | 0.62
4118 | 14.3 | 0.68
4119 | 14.9 | 0.7
4120 | 14.8 | 0.71
4121 | 14.3 | 0.76
4122 | 13.7 | 0.83
4123 | 13.6 | 0.85
4124 | 14 | 0.8
4125 | 12.5 | 0.86
4126 | 11.2 | 0.92
4127 | 10.4 | 0.96
4128 | 10.3 | 0.95
4129 | 10.3 | 0.96
4130 | 10.1 | 0.96
4131 | 10.6 | 0.99
4132 | 10.8 | 0.99
4133 | 10.9 | 0.99
4134 | 11.5 | 0.99
4135 | 12 | 0.99
4136 | 12.6 | 0.94
4137 | 13.8 | 0.86
4138 | 13.8 | 0.84
4139 | 14.4 | 0.82
4140 | 15.7 | 0.73
4141 | 15.4 | 0.77
4142 | 14.4 | 0.78
4143 | 14.9 | 0.75
4144 | 15.1 | 0.77
4145 | 14.2 | 0.79
4146 | 13.8 | 0.8
4147 | 13.7 | 0.81
4148 | 13.6 | 0.84
4149 | 13.4 | 0.86
4150 | 12.9 | 0.91
4151 | 12.7 | 0.92
4152 | 12.6 | 0.94
4153 | 13.3 | 0.92
4154 | 13.5 | 0.88
4155 | 13.6 | 0.86
4156 | 13.3 | 0.88
4157 | 13.1 | 0.91
4158 | 13 | 0.92
4159 | 12.7 | 0.94
4160 | 12.7 | 0.95
4161 | 12.9 | 0.96
4162 | 13 | 0.99
4163 | 13 | 0.98
4164 | 13.1 | 0.98
4165 | 13.1 | 0.99
4166 | 13.2 | 0.98
4167 | 13.3 | 1
4168 | 13.5 | 0.99
4169 | 13.6 | 0.99
4170 | 13.5 | 0.99
4171 | 13.5 | 1
4172 | 13.5 | 0.99
4173 | 13.6 | 1
4174 | 13.6 | 0.99
4175 | 13.8 | 0.99
4176 | 13.8 | 0.99
4177 | 13.8 | 1
4178 | 13.9 | 0.99
4179 | 13.9 | 0.99
4180 | 13.8 | 0.99
4181 | 13.7 | 1
4182 | 13.7 | 0.99
4183 | 13.9 | 0.99
4184 | 14.3 | 0.98
4185 | 14.4 | 0.97
4186 | 17.1 | 0.81
4187 | 15.8 | 0.87
4188 | 16.8 | 0.78
4189 | 17 | 0.79
4190 | 17.8 | 0.75
4191 | 18.2 | 0.76
4192 | 18.4 | 0.72
4193 | 19.1 | 0.71
4194 | 19.6 | 0.68
4195 | 19.4 | 0.71
4196 | 17.9 | 0.82
4197 | 16.1 | 0.87
4198 | 14.1 | 0.94
4199 | 16.1 | 0.85
4200 | 15.3 | 0.85
4201 | 14.6 | 0.9
4202 | 14.4 | 0.9
4203 | 14.4 | 0.9
4204 | 13.9 | 0.93
4205 | 14.1 | 0.95
4206 | 14 | 0.97
4207 | 14.3 | 0.97
4208 | 14.8 | 0.94
4209 | 15.8 | 0.9
4210 | 16.4 | 0.88
4211 | 16.3 | 0.86
4212 | 16.8 | 0.87
4213 | 17.5 | 0.84
4214 | 18.8 | 0.84
4215 | 18.8 | 0.79
4216 | 18.5 | 0.83
4217 | 19.3 | 0.81
4218 | 19.3 | 0.78
4219 | 18.2 | 0.83
4220 | 18.1 | 0.82
4221 | 17 | 0.88
4222 | 16.5 | 0.86
4223 | 16.5 | 0.88
4224 | 15.9 | 0.9
4225 | 15.3 | 0.93
4226 | 14.9 | 0.92
4227 | 14.6 | 0.94
4228 | 14.7 | 0.96
4229 | 14.3 | 0.93
4230 | 14.3 | 0.93
4231 | 14.6 | 0.89
4232 | 15.6 | 0.83
4233 | 17.3 | 0.76
4234 | 17.7 | 0.76
4235 | 18 | 0.77
4236 | 18.8 | 0.75
4237 | 18.7 | 0.75
4238 | 18.5 | 0.73
4239 | 19.3 | 0.74
4240 | 19.1 | 0.72
4241 | 17.6 | 0.84
4242 | 18.4 | 0.82
4243 | 18.9 | 0.8
4244 | 18.9 | 0.74
4245 | 17.8 | 0.76
4246 | 16.9 | 0.78
4247 | 16.1 | 0.74
4248 | 15.5 | 0.74
4249 | 15.2 | 0.81
4250 | 15.4 | 0.84
4251 | 15 | 0.88
4252 | 14.8 | 0.89
4253 | 14.5 | 0.9
4254 | 14.9 | 0.87
4255 | 15.1 | 0.84
4256 | 16.1 | 0.78
4257 | 16.5 | 0.75
4258 | 17.3 | 0.71
4259 | 18.6 | 0.69
4260 | 19.3 | 0.68
4261 | 20.6 | 0.62
4262 | 21 | 0.59
4263 | 21.6 | 0.57
4264 | 22.2 | 0.55
4265 | 23.3 | 0.54
4266 | 22.1 | 0.55
4267 | 21.2 | 0.53
4268 | 20.5 | 0.56
4269 | 18.7 | 0.63
4270 | 17.2 | 0.7
4271 | 17.6 | 0.7
4272 | 17.6 | 0.72
4273 | 17.6 | 0.73
4274 | 17 | 0.76
4275 | 16.9 | 0.76
4276 | 16.2 | 0.79
4277 | 15.8 | 0.81
4278 | 15.4 | 0.83
4279 | 15.3 | 0.83
4280 | 15.3 | 0.84
4281 | 15 | 0.86
4282 | 14.7 | 0.89
4283 | 14.1 | 0.97
4284 | 14.3 | 0.98
4285 | 14.3 | 0.99
4286 | 14.7 | 0.99
4287 | 14.9 | 0.99
4288 | 15.1 | 0.99
4289 | 15.4 | 0.99
4290 | 15.6 | 0.99
4291 | 15.5 | 0.98
4292 | 15.6 | 0.98
4293 | 15 | 0.97
4294 | 14 | 0.97
4295 | 13.4 | 0.95
4296 | 13.4 | 0.96
4297 | 13.1 | 0.98
4298 | 13.3 | 0.98
4299 | 13.4 | 0.99
4300 | 13.6 | 1
4301 | 13.6 | 1
4302 | 13.8 | 0.99
4303 | 14.1 | 0.99
4304 | 14.2 | 0.98
4305 | 14.6 | 0.98
4306 | 15.8 | 0.81
4307 | 17.7 | 0.75
4308 | 17 | 0.79
4309 | 17.9 | 0.75
4310 | 17.9 | 0.71
4311 | 17.8 | 0.77
4312 | 17 | 0.79
4313 | 16.5 | 0.83
4314 | 17.2 | 0.79
4315 | 16.4 | 0.85
4316 | 15.7 | 0.89
4317 | 15.1 | 0.91
4318 | 14.6 | 0.92
4319 | 14.2 | 0.94
4320 | 13.3 | 0.93
4321 | 12.4 | 0.95
4322 | 12.7 | 0.96
4323 | 13.1 | 0.94
4324 | 12.7 | 0.95
4325 | 13.3 | 0.94
4326 | 13.4 | 0.93
4327 | 13.5 | 0.91
4328 | 13.9 | 0.88
4329 | 14.6 | 0.86
4330 | 15.4 | 0.81
4331 | 15.9 | 0.81
4332 | 15.8 | 0.78
4333 | 16.5 | 0.76
4334 | 14.7 | 0.92
4335 | 17.8 | 0.78
4336 | 17.1 | 0.76
4337 | 17.8 | 0.66
4338 | 16.4 | 0.7
4339 | 17 | 0.62
4340 | 15.2 | 0.62
4341 | 14.3 | 0.65
4342 | 13.2 | 0.69
4343 | 12.7 | 0.77
4344 | 12 | 0.81
4345 | 11.4 | 0.83
4346 | 12 | 0.81
4347 | 12.1 | 0.8
4348 | 11.8 | 0.82
4349 | 12.1 | 0.82
4350 | 12 | 0.83
4351 | 12.2 | 0.83
4352 | 12.6 | 0.81
4353 | 13.4 | 0.79
4354 | 13.7 | 0.74
4355 | 16.1 | 0.62
4356 | 16.5 | 0.59
4357 | 17.3 | 0.59
4358 | 17.5 | 0.6
4359 | 18.3 | 0.55
4360 | 18.5 | 0.55
4361 | 18.1 | 0.56
4362 | 18 | 0.55
4363 | 17.3 | 0.58
4364 | 16.1 | 0.62
4365 | 14.6 | 0.67
4366 | 13 | 0.74
4367 | 11.9 | 0.78
4368 | 11.4 | 0.8
4369 | 11 | 0.84
4370 | 10.7 | 0.84
4371 | 10.4 | 0.86
4372 | 10.4 | 0.88
4373 | 10.2 | 0.91
4374 | 9.9 | 0.92
4375 | 10.7 | 0.91
4376 | 11.8 | 0.87
4377 | 13.5 | 0.78
4378 | 15.1 | 0.66
4379 | 15.3 | 0.63
4380 | 16.4 | 0.58
4381 | 16.4 | 0.56
4382 | 16.9 | 0.55
4383 | 16 | 0.73
4384 | 15 | 0.78
4385 | 15 | 0.74
4386 | 15.4 | 0.74
4387 | 15.3 | 0.73
4388 | 14.9 | 0.77
4389 | 14.2 | 0.8
4390 | 13.8 | 0.81
4391 | 14.6 | 0.7
4392 | 14.2 | 0.66
4393 | 13.9 | 0.68
4394 | 13.4 | 0.73
4395 | 12.8 | 0.77
4396 | 12.8 | 0.78
4397 | 12.3 | 0.83
4398 | 12.6 | 0.78
4399 | 12.8 | 0.78
4400 | 13.2 | 0.78
4401 | 13.9 | 0.72
4402 | 15.2 | 0.67
4403 | 15.6 | 0.65
4404 | 16.7 | 0.65
4405 | 16 | 0.7
4406 | 17.2 | 0.68
4407 | 17.5 | 0.7
4408 | 17.7 | 0.7
4409 | 17.3 | 0.7
4410 | 16.5 | 0.71
4411 | 16 | 0.73
4412 | 15.1 | 0.72
4413 | 13.7 | 0.79
4414 | 11.6 | 0.83
4415 | 11.1 | 0.85
4416 | 11.1 | 0.84
4417 | 11.3 | 0.83
4418 | 11.8 | 0.82
4419 | 11.7 | 0.83
4420 | 11.1 | 0.89
4421 | 10.2 | 0.92
4422 | 10.4 | 0.92
4423 | 11.1 | 0.87
4424 | 12.5 | 0.82
4425 | 14.3 | 0.75
4426 | 16.1 | 0.65
4427 | 17.8 | 0.62
4428 | 19.2 | 0.58
4429 | 19.8 | 0.58
4430 | 20.6 | 0.55
4431 | 20 | 0.69
4432 | 20.3 | 0.68
4433 | 20.7 | 0.67
4434 | 19.8 | 0.7
4435 | 18.7 | 0.71
4436 | 19.9 | 0.59
4437 | 18.1 | 0.58
4438 | 15.8 | 0.6
4439 | 14.3 | 0.73
4440 | 13.5 | 0.76
4441 | 12.8 | 0.84
4442 | 12.5 | 0.86
4443 | 12.3 | 0.88
4444 | 12.1 | 0.88
4445 | 11.9 | 0.89
4446 | 11.6 | 0.89
4447 | 12 | 0.88
4448 | 13.1 | 0.83
4449 | 14.8 | 0.74
4450 | 15.2 | 0.72
4451 | 17.6 | 0.61
4452 | 18.6 | 0.6
4453 | 19.8 | 0.57
4454 | 20.4 | 0.55
4455 | 21.5 | 0.57
4456 | 22.3 | 0.53
4457 | 22.6 | 0.54
4458 | 22 | 0.56
4459 | 21.7 | 0.56
4460 | 20 | 0.65
4461 | 18.6 | 0.7
4462 | 16.4 | 0.77
4463 | 15.3 | 0.82
4464 | 14.7 | 0.84
4465 | 14.3 | 0.86
4466 | 13.8 | 0.9
4467 | 13.5 | 0.87
4468 | 13.2 | 0.86
4469 | 12.8 | 0.87
4470 | 12.3 | 0.89
4471 | 13 | 0.86
4472 | 13.9 | 0.83
4473 | 14.5 | 0.82
4474 | 14.9 | 0.8
4475 | 16.4 | 0.76
4476 | 16.9 | 0.78
4477 | 18.3 | 0.73
4478 | 18.7 | 0.71
4479 | 18.9 | 0.74
4480 | 18.7 | 0.73
4481 | 18 | 0.84
4482 | 18.7 | 0.77
4483 | 17.6 | 0.89
4484 | 17.5 | 0.86
4485 | 17 | 0.88
4486 | 16.3 | 0.85
4487 | 16 | 0.87
4488 | 15.6 | 0.88
4489 | 15.2 | 0.88
4490 | 15 | 0.9
4491 | 14.8 | 0.85
4492 | 14.6 | 0.91
4493 | 14.4 | 0.91
4494 | 14.4 | 0.92
4495 | 14.6 | 0.91
4496 | 15.1 | 0.9
4497 | 15.1 | 0.89
4498 | 15.6 | 0.86
4499 | 16.3 | 0.84
4500 | 16.8 | 0.82
4501 | 16.5 | 0.86
4502 | 16.3 | 0.91
4503 | 15.5 | 0.97
4504 | 14.9 | 0.98
4505 | 15.1 | 0.98
4506 | 15 | 0.98
4507 | 14.9 | 0.98
4508 | 14.9 | 0.98
4509 | 14.7 | 0.99
4510 | 14.6 | 0.99
4511 | 14.5 | 0.99
4512 | 14.5 | 0.99
4513 | 14.5 | 0.99
4514 | 14.5 | 0.99
4515 | 14.5 | 0.99
4516 | 14.7 | 0.99
4517 | 14.8 | 0.99
4518 | 14.9 | 1
4519 | 14.9 | 0.99
4520 | 15.3 | 0.99
4521 | 15.6 | 0.98
4522 | 16.8 | 0.92
4523 | 17.5 | 0.89
4524 | 17.7 | 0.88
4525 | 17.7 | 0.87
4526 | 17.9 | 0.88
4527 | 18.8 | 0.74
4528 | 19.2 | 0.76
4529 | 20.1 | 0.72
4530 | 19.3 | 0.73
4531 | 18.9 | 0.74
4532 | 17.2 | 0.8
4533 | 16.7 | 0.84
4534 | 15.5 | 0.9
4535 | 14 | 0.94
4536 | 15.2 | 0.92
4537 | 15.7 | 0.86
4538 | 15.1 | 0.87
4539 | 14.6 | 0.87
4540 | 14.6 | 0.87
4541 | 14 | 0.88
4542 | 15 | 0.85
4543 | 15.2 | 0.85
4544 | 16.2 | 0.8
4545 | 17.5 | 0.77
4546 | 18.4 | 0.77
4547 | 18.9 | 0.72
4548 | 19.5 | 0.71
4549 | 19.9 | 0.71
4550 | 20 | 0.68
4551 | 20 | 0.69
4552 | 21.6 | 0.63
4553 | 19.7 | 0.7
4554 | 18 | 0.73
4555 | 17.8 | 0.74
4556 | 16.8 | 0.76
4557 | 16 | 0.76
4558 | 13.7 | 0.91
4559 | 13.1 | 0.94
4560 | 12.9 | 0.92
4561 | 12.3 | 0.92
4562 | 12.7 | 0.94
4563 | 13.6 | 0.95
4564 | 14.2 | 0.95
4565 | 14.2 | 0.95
4566 | 14.4 | 0.95
4567 | 14.9 | 0.92
4568 | 15.3 | 0.97
4569 | 15.6 | 0.99
4570 | 15.5 | 0.98
4571 | 15.6 | 0.99
4572 | 16.8 | 0.99
4573 | 18.6 | 0.89
4574 | 18.1 | 0.91
4575 | 17.7 | 0.94
4576 | 16.8 | 0.91
4577 | 16.6 | 0.9
4578 | 16.2 | 0.89
4579 | 15.9 | 0.9
4580 | 15.9 | 0.89
4581 | 15.4 | 0.95
4582 | 15.4 | 0.96
4583 | 15.3 | 0.98
4584 | 15.3 | 0.98
4585 | 15.3 | 0.98
4586 | 15.3 | 0.98
4587 | 15.3 | 0.98
4588 | 15.3 | 0.99
4589 | 15.3 | 0.99
4590 | 15.3 | 0.99
4591 | 15.4 | 0.99
4592 | 15.7 | 0.98
4593 | 16.5 | 0.98
4594 | 17.3 | 0.96
4595 | 17.6 | 0.97
4596 | 18.3 | 0.96
4597 | 18.7 | 0.94
4598 | 19.1 | 0.9
4599 | 20.8 | 0.73
4600 | 21 | 0.68
4601 | 21.2 | 0.61
4602 | 20.3 | 0.61
4603 | 19.6 | 0.62
4604 | 18.3 | 0.68
4605 | 17.5 | 0.71
4606 | 16.1 | 0.8
4607 | 15.9 | 0.83
4608 | 15.5 | 0.87
4609 | 15.1 | 0.88
4610 | 14.9 | 0.86
4611 | 14.5 | 0.83
4612 | 13.8 | 0.83
4613 | 13.9 | 0.88
4614 | 13.2 | 0.88
4615 | 13.6 | 0.87
4616 | 14.4 | 0.83
4617 | 14.9 | 0.82
4618 | 15.7 | 0.78
4619 | 16.3 | 0.77
4620 | 17.9 | 0.68
4621 | 18.2 | 0.69
4622 | 18.7 | 0.7
4623 | 20.2 | 0.65
4624 | 19.6 | 0.65
4625 | 19.5 | 0.64
4626 | 18.3 | 0.64
4627 | 17.4 | 0.7
4628 | 16.2 | 0.71
4629 | 15.2 | 0.74
4630 | 14.4 | 0.76
4631 | 14.1 | 0.78
4632 | 13.2 | 0.83
4633 | 12.5 | 0.87
4634 | 12.1 | 0.87
4635 | 12 | 0.86
4636 | 11.9 | 0.87
4637 | 12.1 | 0.88
4638 | 12.4 | 0.88
4639 | 12.6 | 0.88
4640 | 13.5 | 0.86
4641 | 14.4 | 0.73
4642 | 15.4 | 0.67
4643 | 15.6 | 0.67
4644 | 17.1 | 0.64
4645 | 18.1 | 0.6
4646 | 19.2 | 0.56
4647 | 20 | 0.57
4648 | 20.2 | 0.57
4649 | 19.8 | 0.69
4650 | 18.5 | 0.71
4651 | 18.4 | 0.71
4652 | 17.6 | 0.75
4653 | 16.2 | 0.81
4654 | 14.5 | 0.89
4655 | 15.7 | 0.8
4656 | 15.1 | 0.82
4657 | 14.5 | 0.83
4658 | 13.6 | 0.87
4659 | 12.9 | 0.91
4660 | 12.6 | 0.9
4661 | 12.4 | 0.89
4662 | 12.1 | 0.9
4663 | 13.1 | 0.85
4664 | 14.2 | 0.81
4665 | 15.9 | 0.76
4666 | 16.9 | 0.72
4667 | 18.4 | 0.7
4668 | 18.8 | 0.67
4669 | 19.9 | 0.7
4670 | 20 | 0.7
4671 | 20 | 0.7
4672 | 20 | 0.71
4673 | 19.5 | 0.72
4674 | 19.2 | 0.73
4675 | 17.7 | 0.77
4676 | 16.6 | 0.8
4677 | 15.1 | 0.86
4678 | 13.6 | 0.92
4679 | 13.5 | 0.94
4680 | 14.1 | 0.92
4681 | 13.8 | 0.91
4682 | 13.8 | 0.95
4683 | 12.9 | 0.96
4684 | 12.3 | 0.96
4685 | 12.2 | 0.98
4686 | 11.6 | 0.98
4687 | 13.5 | 0.94
4688 | 14.9 | 0.87
4689 | 16.1 | 0.81
4690 | 17.2 | 0.82
4691 | 18.4 | 0.78
4692 | 19 | 0.76
4693 | 19.5 | 0.75
4694 | 18.7 | 0.76
4695 | 17.9 | 0.79
4696 | 17.5 | 0.82
4697 | 17.7 | 0.82
4698 | 17.5 | 0.82
4699 | 17.4 | 0.85
4700 | 17 | 0.89
4701 | 16.6 | 0.9
4702 | 16 | 0.94
4703 | 16 | 0.94
4704 | 15.7 | 0.96
4705 | 15.7 | 0.97
4706 | 15.6 | 0.97
4707 | 15.6 | 0.97
4708 | 15.7 | 0.99
4709 | 15.7 | 0.98
4710 | 15.1 | 0.99
4711 | 15.5 | 0.98
4712 | 16 | 0.96
4713 | 17.5 | 0.83
4714 | 18.1 | 0.76
4715 | 18.4 | 0.71
4716 | 20.3 | 0.7
4717 | 20.1 | 0.67
4718 | 19.1 | 0.71
4719 | 20.7 | 0.66
4720 | 21.3 | 0.63
4721 | 20.1 | 0.7
4722 | 21.2 | 0.63
4723 | 20 | 0.62
4724 | 18.3 | 0.64
4725 | 16.9 | 0.71
4726 | 15.1 | 0.82
4727 | 15 | 0.81
4728 | 14.4 | 0.88
4729 | 14.1 | 0.91
4730 | 13.6 | 0.94
4731 | 13.6 | 0.94
4732 | 13.4 | 0.96
4733 | 14.1 | 0.95
4734 | 14.4 | 0.95
4735 | 14.6 | 0.96
4736 | 15 | 0.96
4737 | 14.9 | 0.92
4738 | 14.2 | 0.93
4739 | 15.7 | 0.86
4740 | 15.2 | 0.97
4741 | 15.3 | 0.98
4742 | 16.4 | 0.98
4743 | 17.5 | 0.98
4744 | 19.3 | 0.83
4745 | 19.1 | 0.76
4746 | 18.6 | 0.8
4747 | 16.3 | 0.94
4748 | 16.2 | 0.86
4749 | 15.2 | 0.83
4750 | 14.4 | 0.77
4751 | 13.5 | 0.78
4752 | 12.8 | 0.85
4753 | 12.6 | 0.87
4754 | 12.2 | 0.88
4755 | 12.3 | 0.87
4756 | 12.5 | 0.89
4757 | 12.4 | 0.89
4758 | 12.6 | 0.87
4759 | 13.1 | 0.86
4760 | 14 | 0.85
4761 | 15.9 | 0.75
4762 | 16.9 | 0.61
4763 | 17.2 | 0.6
4764 | 18.4 | 0.62
4765 | 19.1 | 0.61
4766 | 19.7 | 0.55
4767 | 18.8 | 0.63
4768 | 17.9 | 0.71
4769 | 16.9 | 0.75
4770 | 16.7 | 0.77
4771 | 16.8 | 0.74
4772 | 15.9 | 0.81
4773 | 14.9 | 0.9
4774 | 14.4 | 0.9
4775 | 14.4 | 0.91
4776 | 14.2 | 0.94
4777 | 13.8 | 0.98
4778 | 13.8 | 0.99
4779 | 13.8 | 0.99
4780 | 13.9 | 0.98
4781 | 14.2 | 0.99
4782 | 14.6 | 1
4783 | 15.4 | 0.99
4784 | 16.9 | 0.99
4785 | 17 | 0.98
4786 | 17.8 | 0.92
4787 | 18.4 | 0.89
4788 | 17.2 | 0.95
4789 | 18.7 | 0.85
4790 | 17.6 | 0.92
4791 | 17.6 | 0.9
4792 | 17.8 | 0.89
4793 | 17.2 | 0.95
4794 | 17.9 | 0.88
4795 | 16.4 | 0.87
4796 | 15.9 | 0.87
4797 | 14.9 | 0.88
4798 | 14.4 | 0.89
4799 | 14.2 | 0.9
4800 | 14.7 | 0.86
4801 | 14.8 | 0.86
4802 | 14.5 | 0.88
4803 | 14.1 | 0.88
4804 | 13.7 | 0.85
4805 | 13.1 | 0.85
4806 | 13.2 | 0.86
4807 | 13.7 | 0.86
4808 | 14.4 | 0.82
4809 | 14.6 | 0.81
4810 | 15.7 | 0.73
4811 | 15.9 | 0.7
4812 | 17 | 0.61
4813 | 18 | 0.61
4814 | 17.7 | 0.62
4815 | 17.6 | 0.66
4816 | 17.9 | 0.71
4817 | 18.1 | 0.66
4818 | 17.8 | 0.65
4819 | 18 | 0.69
4820 | 17 | 0.72
4821 | 15.6 | 0.77
4822 | 14.4 | 0.86
4823 | 14.6 | 0.86
4824 | 14.2 | 0.92
4825 | 14.6 | 0.9
4826 | 13.5 | 0.93
4827 | 13.7 | 0.93
4828 | 13.7 | 0.95
4829 | 14 | 0.97
4830 | 14.8 | 0.96
4831 | 15.3 | 0.96
4832 | 16.1 | 0.98
4833 | 16.8 | 0.94
4834 | 16.7 | 0.94
4835 | 16.8 | 0.93
4836 | 17.6 | 0.86
4837 | 17.7 | 0.88
4838 | 16.3 | 0.97
4839 | 16.6 | 0.98
4840 | 17 | 0.99
4841 | 17.3 | 0.99
4842 | 17.6 | 0.99
4843 | 17.8 | 1
4844 | 17.6 | 0.99
4845 | 17.5 | 0.99
4846 | 17.4 | 0.99
4847 | 17.3 | 0.99
4848 | 17.4 | 0.98
4849 | 17.3 | 0.98
4850 | 17.3 | 0.95
4851 | 17 | 0.99
4852 | 17.1 | 0.95
4853 | 16.7 | 0.98
4854 | 16.6 | 0.99
4855 | 16.7 | 0.99
4856 | 17 | 0.98
4857 | 17.1 | 0.98
4858 | 18 | 0.96
4859 | 18.4 | 0.93
4860 | 19.2 | 0.91
4861 | 19.4 | 0.89
4862 | 19.9 | 0.86
4863 | 18.5 | 0.92
4864 | 18.2 | 0.93
4865 | 18 | 0.92
4866 | 17.7 | 0.94
4867 | 17.3 | 0.95
4868 | 17.4 | 0.95
4869 | 17 | 0.98
4870 | 16.7 | 0.98
4871 | 16.6 | 0.98
4872 | 16.5 | 0.96
4873 | 16.4 | 0.97
4874 | 16.4 | 0.97
4875 | 16.1 | 0.97
4876 | 16 | 0.97
4877 | 15.8 | 0.97
4878 | 15.8 | 0.94
4879 | 16.1 | 0.94
4880 | 16 | 0.94
4881 | 16 | 0.96
4882 | 16.2 | 0.98
4883 | 17 | 0.94
4884 | 17.6 | 0.91
4885 | 17.3 | 0.92
4886 | 17 | 0.92
4887 | 17.7 | 0.83
4888 | 18 | 0.83
4889 | 17.6 | 0.83
4890 | 17.1 | 0.86
4891 | 17.2 | 0.83
4892 | 16.7 | 0.88
4893 | 16.2 | 0.93
4894 | 15.7 | 0.94
4895 | 15.8 | 0.98
4896 | 16.2 | 0.99
4897 | 16.5 | 0.99
4898 | 15.2 | 0.98
4899 | 14.4 | 0.98
4900 | 14.5 | 0.98
4901 | 14.6 | 0.96
4902 | 14.2 | 0.98
4903 | 15.1 | 0.99
4904 | 16 | 0.98
4905 | 16.3 | 0.98
4906 | 16.7 | 0.96
4907 | 17.7 | 0.92
4908 | 18.1 | 0.87
4909 | 17.8 | 0.87
4910 | 17.7 | 0.87
4911 | 18.3 | 0.82
4912 | 17.4 | 0.89
4913 | 17.4 | 0.92
4914 | 17.1 | 0.95
4915 | 17.5 | 0.94
4916 | 17.1 | 0.95
4917 | 16.8 | 0.96
4918 | 16.7 | 0.96
4919 | 17 | 0.98
4920 | 17.3 | 0.98
4921 | 17.3 | 0.99
4922 | 17.4 | 1
4923 | 17.4 | 0.99
4924 | 17.1 | 0.99
4925 | 17.1 | 0.97
4926 | 16.9 | 0.98
4927 | 16.8 | 0.99
4928 | 16.9 | 0.99
4929 | 17.1 | 0.99
4930 | 17.6 | 0.99
4931 | 17.6 | 0.97
4932 | 17.9 | 0.95
4933 | 18 | 0.95
4934 | 18.3 | 0.94
4935 | 18.7 | 0.9
4936 | 18.4 | 0.92
4937 | 18.5 | 0.89
4938 | 18 | 0.92
4939 | 16.9 | 0.97
4940 | 16.8 | 0.96
4941 | 16.5 | 0.98
4942 | 16.5 | 0.98
4943 | 16.1 | 0.98
4944 | 15.6 | 0.97
4945 | 15.5 | 0.97
4946 | 15.7 | 0.99
4947 | 15.5 | 0.98
4948 | 14.8 | 0.98
4949 | 14.3 | 0.97
4950 | 14.2 | 0.98
4951 | 14.4 | 0.98
4952 | 14.7 | 0.98
4953 | 15.4 | 0.89
4954 | 16.9 | 0.85
4955 | 17.1 | 0.84
4956 | 18.5 | 0.75
4957 | 18.8 | 0.72
4958 | 18.7 | 0.7
4959 | 18.4 | 0.65
4960 | 19.3 | 0.62
4961 | 19.5 | 0.6
4962 | 17.7 | 0.63
4963 | 16.8 | 0.66
4964 | 16.3 | 0.68
4965 | 14.6 | 0.7
4966 | 13.2 | 0.77
4967 | 12.9 | 0.85
4968 | 12.1 | 0.89
4969 | 12.4 | 0.88
4970 | 12.2 | 0.88
4971 | 11.6 | 0.89
4972 | 11.1 | 0.91
4973 | 11 | 0.91
4974 | 10.9 | 0.94
4975 | 11.2 | 0.92
4976 | 12.5 | 0.88
4977 | 13.6 | 0.83
4978 | 15.2 | 0.73
4979 | 17.1 | 0.69
4980 | 17.8 | 0.6
4981 | 18.5 | 0.54
4982 | 17.7 | 0.63
4983 | 19.2 | 0.56
4984 | 18.5 | 0.59
4985 | 19 | 0.55
4986 | 18.5 | 0.59
4987 | 17.8 | 0.6
4988 | 17.6 | 0.6
4989 | 16.1 | 0.65
4990 | 14.7 | 0.73
4991 | 13.4 | 0.78
4992 | 12.9 | 0.83
4993 | 12.4 | 0.86
4994 | 12.1 | 0.89
4995 | 11.7 | 0.9
4996 | 11.5 | 0.89
4997 | 11.2 | 0.89
4998 | 11.1 | 0.9
4999 | 11.5 | 0.9
5000 | 12.7 | 0.87
5001 | 14 | 0.83
5002 | 15.7 | 0.76
5003 | 15.6 | 0.7
5004 | 16.4 | 0.7
5005 | 16.8 | 0.68
5006 | 16.1 | 0.67
5007 | 14.8 | 0.77
5008 | 15.7 | 0.73
5009 | 16.2 | 0.67
5010 | 15.1 | 0.81
5011 | 14.2 | 0.88
5012 | 13.7 | 0.91
5013 | 13.3 | 0.92
5014 | 13.1 | 0.93
5015 | 13 | 0.93
5016 | 12.7 | 0.94
5017 | 12.7 | 0.94
5018 | 12.4 | 0.95
5019 | 12 | 0.95
5020 | 11.9 | 0.95
5021 | 11.8 | 0.95
5022 | 11.1 | 0.96
5023 | 11.9 | 0.95
5024 | 12.9 | 0.89
5025 | 14.6 | 0.83
5026 | 17 | 0.76
5027 | 16.9 | 0.72
5028 | 17.8 | 0.66
5029 | 18 | 0.65
5030 | 17.4 | 0.67
5031 | 14.2 | 0.9
5032 | 14.5 | 0.93
5033 | 14.1 | 0.97
5034 | 13.8 | 0.98
5035 | 13.5 | 0.97
5036 | 13.5 | 0.97
5037 | 13.2 | 0.96
5038 | 13.2 | 0.98
5039 | 13.7 | 0.97
5040 | 13.9 | 0.95
5041 | 13.9 | 0.95
5042 | 14 | 0.94
5043 | 14 | 0.95
5044 | 13.7 | 0.94
5045 | 13.5 | 0.94
5046 | 13.2 | 0.93
5047 | 13.4 | 0.93
5048 | 13.9 | 0.9
5049 | 14.3 | 0.88
5050 | 15.4 | 0.81
5051 | 17.1 | 0.71
5052 | 16.8 | 0.72
5053 | 17.9 | 0.66
5054 | 17.4 | 0.68
5055 | 18.1 | 0.64
5056 | 17.5 | 0.65
5057 | 16.4 | 0.71
5058 | 16.4 | 0.7
5059 | 16.4 | 0.66
5060 | 15.8 | 0.69
5061 | 14.8 | 0.71
5062 | 13.4 | 0.75
5063 | 12.5 | 0.78
5064 | 12.1 | 0.81
5065 | 12.2 | 0.82
5066 | 12.2 | 0.86
5067 | 12.9 | 0.8
5068 | 12.9 | 0.8
5069 | 12.1 | 0.92
5070 | 12.4 | 0.92
5071 | 12.7 | 0.92
5072 | 13 | 0.93
5073 | 14.2 | 0.84
5074 | 14.7 | 0.85
5075 | 14.3 | 0.91
5076 | 15.9 | 0.86
5077 | 15.5 | 0.92
5078 | 15.9 | 0.88
5079 | 16.3 | 0.78
5080 | 18 | 0.67
5081 | 18.9 | 0.6
5082 | 18.9 | 0.61
5083 | 18.2 | 0.61
5084 | 17 | 0.63
5085 | 15.4 | 0.68
5086 | 14.1 | 0.74
5087 | 13.1 | 0.79
5088 | 12.8 | 0.8
5089 | 12.4 | 0.82
5090 | 12.1 | 0.84
5091 | 11.8 | 0.81
5092 | 11.6 | 0.85
5093 | 11.8 | 0.87
5094 | 11.7 | 0.89
5095 | 12.1 | 0.88
5096 | 13.3 | 0.86
5097 | 14.3 | 0.81
5098 | 16.5 | 0.72
5099 | 17.6 | 0.68
5100 | 19 | 0.6
5101 | 19.7 | 0.63
5102 | 19.5 | 0.62
5103 | 19.6 | 0.61
5104 | 19.6 | 0.65
5105 | 19.6 | 0.6
5106 | 19.1 | 0.64
5107 | 18.4 | 0.65
5108 | 17.4 | 0.72
5109 | 15.2 | 0.85
5110 | 13.1 | 0.92
5111 | 13.3 | 0.95
5112 | 13.3 | 0.95
5113 | 13.9 | 0.92
5114 | 12.8 | 0.95
5115 | 12.8 | 0.95
5116 | 11.9 | 0.98
5117 | 11.6 | 0.96
5118 | 11.5 | 1
5119 | 12.3 | 0.99
5120 | 12.4 | 1
5121 | 14.1 | 0.99
5122 | 14.7 | 0.98
5123 | 17.3 | 0.77
5124 | 19.1 | 0.67
5125 | 19.4 | 0.67
5126 | 19.6 | 0.68
5127 | 19.9 | 0.64
5128 | 18.9 | 0.74
5129 | 19.1 | 0.71
5130 | 18.1 | 0.76
5131 | 17.4 | 0.81
5132 | 16.7 | 0.88
5133 | 16.3 | 0.92
5134 | 15.8 | 0.94
5135 | 15.4 | 0.95
5136 | 15.4 | 0.96
5137 | 15.6 | 0.95
5138 | 15.9 | 0.95
5139 | 16 | 0.95
5140 | 16 | 0.96
5141 | 15.7 | 0.98
5142 | 14.9 | 0.98
5143 | 14.7 | 0.99
5144 | 15.1 | 0.99
5145 | 15.6 | 0.98
5146 | 16.1 | 0.93
5147 | 15.4 | 0.97
5148 | 15.9 | 0.97
5149 | 15.7 | 0.96
5150 | 15.7 | 0.94
5151 | 15.9 | 0.98
5152 | 16.6 | 0.99
5153 | 17.2 | 0.95
5154 | 17.1 | 0.92
5155 | 16.6 | 0.92
5156 | 16.4 | 0.91
5157 | 15.1 | 0.94
5158 | 14.2 | 0.97
5159 | 13.3 | 0.98
5160 | 13.5 | 0.98
5161 | 13.2 | 0.99
5162 | 13.1 | 0.99
5163 | 13.1 | 1
5164 | 13 | 1
5165 | 13.8 | 1
5166 | 14.2 | 0.99
5167 | 14.4 | 0.99
5168 | 15.3 | 0.97
5169 | 16.2 | 0.94
5170 | 16.7 | 0.9
5171 | 17.5 | 0.87
5172 | 16.7 | 0.92
5173 | 17.3 | 0.84
5174 | 17.5 | 0.83
5175 | 16.8 | 0.86
5176 | 15.2 | 0.97
5177 | 15.4 | 0.98
5178 | 15.9 | 0.99
5179 | 17.1 | 0.9
5180 | 16 | 0.82
5181 | 13.9 | 0.88
5182 | 12.7 | 0.94
5183 | 12.5 | 0.95
5184 | 12.3 | 0.95
5185 | 11.9 | 0.96
5186 | 11.4 | 0.97
5187 | 11.6 | 0.98
5188 | 12 | 0.96
5189 | 12.1 | 0.96
5190 | 11.8 | 0.98
5191 | 12.1 | 0.96
5192 | 13.7 | 0.94
5193 | 14.8 | 0.92
5194 | 15.1 | 0.91
5195 | 16.7 | 0.88
5196 | 17.4 | 0.84
5197 | 17.3 | 0.81
5198 | 18.5 | 0.73
5199 | 18.2 | 0.76
5200 | 17.9 | 0.73
5201 | 18.2 | 0.74
5202 | 16.7 | 0.79
5203 | 16 | 0.8
5204 | 15.6 | 0.82
5205 | 14.6 | 0.85
5206 | 14.1 | 0.91
5207 | 13.9 | 0.9
5208 | 13.5 | 0.91
5209 | 14.2 | 0.89
5210 | 14.3 | 0.93
5211 | 14.3 | 0.94
5212 | 14.1 | 0.95
5213 | 14.1 | 0.98
5214 | 13.8 | 0.98
5215 | 13.3 | 0.95
5216 | 13.6 | 0.95
5217 | 14.8 | 0.94
5218 | 16.5 | 0.81
5219 | 17.2 | 0.74
5220 | 17 | 0.76
5221 | 17.2 | 0.74
5222 | 18.6 | 0.7
5223 | 18.5 | 0.7
5224 | 17.9 | 0.74
5225 | 18 | 0.73
5226 | 18.7 | 0.71
5227 | 17.5 | 0.72
5228 | 16.4 | 0.75
5229 | 15.1 | 0.83
5230 | 14.6 | 0.86
5231 | 14.5 | 0.86
5232 | 14 | 0.89
5233 | 13.8 | 0.9
5234 | 13.5 | 0.93
5235 | 13.5 | 0.93
5236 | 12.7 | 0.94
5237 | 12.4 | 0.94
5238 | 12.5 | 0.92
5239 | 12.4 | 0.93
5240 | 13.9 | 0.89
5241 | 14.4 | 0.82
5242 | 15.7 | 0.79
5243 | 16 | 0.77
5244 | 17.3 | 0.74
5245 | 18.5 | 0.65
5246 | 19.1 | 0.63
5247 | 19.1 | 0.65
5248 | 19.9 | 0.61
5249 | 19.3 | 0.6
5250 | 19.1 | 0.63
5251 | 18.9 | 0.65
5252 | 17.7 | 0.7
5253 | 16.8 | 0.7
5254 | 16.1 | 0.78
5255 | 15.3 | 0.82
5256 | 14.7 | 0.86
5257 | 14.6 | 0.86
5258 | 13.8 | 0.86
5259 | 13 | 0.91
5260 | 12.9 | 0.89
5261 | 13.1 | 0.92
5262 | 12.7 | 0.94
5263 | 12.3 | 0.95
5264 | 14.2 | 0.87
5265 | 16 | 0.84
5266 | 17 | 0.77
5267 | 17.5 | 0.77
5268 | 17.2 | 0.81
5269 | 18.3 | 0.72
5270 | 17.8 | 0.76
5271 | 17.7 | 0.74
5272 | 16.7 | 0.81
5273 | 16.2 | 0.81
5274 | 15.3 | 0.93
5275 | 14.8 | 0.94
5276 | 14.4 | 0.97
5277 | 14.5 | 0.98
5278 | 15.1 | 0.98
5279 | 15.8 | 0.99
5280 | 17.2 | 0.99
5281 | 17.5 | 0.99
5282 | 16.5 | 0.99
5283 | 15.7 | 0.97
5284 | 15.6 | 0.96
5285 | 15.7 | 0.98
5286 | 16.1 | 0.98
5287 | 16 | 0.98
5288 | 16.1 | 0.98
5289 | 16.1 | 0.98
5290 | 16.8 | 0.96
5291 | 16.7 | 0.95
5292 | 16.3 | 0.98
5293 | 16.1 | 0.98
5294 | 16.6 | 0.98
5295 | 16.5 | 0.98
5296 | 16.3 | 0.97
5297 | 16 | 0.98
5298 | 15.9 | 0.99
5299 | 15.9 | 0.98
5300 | 16.2 | 0.98
5301 | 15.8 | 0.96
5302 | 15.4 | 0.96
5303 | 15.3 | 0.97
5304 | 15.3 | 0.97
5305 | 15.5 | 0.97
5306 | 15.1 | 0.98
5307 | 14.8 | 0.98
5308 | 14.9 | 0.99
5309 | 15.3 | 0.97
5310 | 14.9 | 0.91
5311 | 14.7 | 0.91
5312 | 15.4 | 0.9
5313 | 16.1 | 0.84
5314 | 16.1 | 0.8
5315 | 15.9 | 0.78
5316 | 16.6 | 0.73
5317 | 16.8 | 0.7
5318 | 17.7 | 0.64
5319 | 17.2 | 0.67
5320 | 16.5 | 0.7
5321 | 15.9 | 0.73
5322 | 15.6 | 0.78
5323 | 15.4 | 0.81
5324 | 14.4 | 0.9
5325 | 14.1 | 0.94
5326 | 14 | 0.94
5327 | 13.9 | 0.97
5328 | 14 | 0.95
5329 | 13.8 | 0.95
5330 | 13.6 | 0.95
5331 | 13.4 | 0.94
5332 | 13.1 | 0.94
5333 | 12.9 | 0.94
5334 | 12.7 | 0.94
5335 | 12.6 | 0.93
5336 | 13 | 0.92
5337 | 13.5 | 0.88
5338 | 13.2 | 0.9
5339 | 13.7 | 0.84
5340 | 14.4 | 0.78
5341 | 14.5 | 0.77
5342 | 15.2 | 0.73
5343 | 14.6 | 0.71
5344 | 15 | 0.68
5345 | 15.9 | 0.63
5346 | 15.2 | 0.62
5347 | 14.9 | 0.65
5348 | 14.2 | 0.65
5349 | 12.9 | 0.7
5350 | 11.9 | 0.76
5351 | 11.3 | 0.8
5352 | 10.8 | 0.82
5353 | 10.4 | 0.85
5354 | 9.7 | 0.87
5355 | 9.3 | 0.89
5356 | 9.4 | 0.88
5357 | 9.9 | 0.84
5358 | 9.7 | 0.83
5359 | 10.2 | 0.82
5360 | 10.6 | 0.84
5361 | 12 | 0.82
5362 | 13.6 | 0.82
5363 | 14.7 | 0.76
5364 | 16.9 | 0.61
5365 | 17.5 | 0.59
5366 | 17.1 | 0.64
5367 | 12.9 | 0.86
5368 | 16.3 | 0.7
5369 | 17.4 | 0.6
5370 | 17.1 | 0.53
5371 | 15.9 | 0.59
5372 | 14.8 | 0.65
5373 | 13.9 | 0.7
5374 | 13.4 | 0.72
5375 | 12.5 | 0.78
5376 | 12.4 | 0.79
5377 | 12.5 | 0.79
5378 | 12 | 0.81
5379 | 11.9 | 0.82
5380 | 11.5 | 0.88
5381 | 11.7 | 0.89
5382 | 11.3 | 0.93
5383 | 11.2 | 0.94
5384 | 12.3 | 0.95
5385 | 12.7 | 0.96
5386 | 13.4 | 0.9
5387 | 14 | 0.89
5388 | 14.2 | 0.91
5389 | 15.6 | 0.85
5390 | 15.9 | 0.83
5391 | 15.5 | 0.9
5392 | 15.8 | 0.83
5393 | 15 | 0.92
5394 | 14.4 | 0.93
5395 | 14.2 | 0.99
5396 | 14.2 | 0.98
5397 | 14.3 | 0.98
5398 | 14.1 | 0.99
5399 | 14.4 | 0.99
5400 | 14.6 | 0.99
5401 | 14.8 | 0.99
5402 | 15.1 | 1
5403 | 15.6 | 0.99
5404 | 15.6 | 1
5405 | 15.6 | 0.99
5406 | 15.4 | 0.99
5407 | 15.4 | 0.99
5408 | 15.7 | 0.98
5409 | 16.5 | 0.98
5410 | 17.3 | 0.92
5411 | 18.5 | 0.85
5412 | 18.8 | 0.84
5413 | 19.9 | 0.78
5414 | 21.2 | 0.68
5415 | 18.8 | 0.75
5416 | 17.2 | 0.73
5417 | 17.8 | 0.69
5418 | 17.5 | 0.72
5419 | 16.7 | 0.77
5420 | 16.3 | 0.81
5421 | 15.5 | 0.87
5422 | 14.8 | 0.92
5423 | 14.6 | 0.88
5424 | 13.5 | 0.92
5425 | 15.3 | 0.81
5426 | 15 | 0.83
5427 | 14.8 | 0.86
5428 | 14.2 | 0.81
5429 | 13.7 | 0.89
5430 | 13.8 | 0.87
5431 | 13.9 | 0.88
5432 | 14.2 | 0.9
5433 | 15 | 0.88
5434 | 16.5 | 0.81
5435 | 17.6 | 0.78
5436 | 17.5 | 0.75
5437 | 18.1 | 0.75
5438 | 19.3 | 0.68
5439 | 20 | 0.62
5440 | 19.5 | 0.69
5441 | 18.4 | 0.68
5442 | 17.5 | 0.72
5443 | 16.5 | 0.73
5444 | 15.4 | 0.89
5445 | 15 | 0.93
5446 | 14.9 | 0.93
5447 | 15 | 0.94
5448 | 14.5 | 0.98
5449 | 15.1 | 0.94
5450 | 15 | 0.97
5451 | 14.8 | 0.96
5452 | 14.5 | 0.97
5453 | 14.3 | 0.99
5454 | 14.8 | 0.99
5455 | 15.4 | 0.99
5456 | 16.1 | 0.99
5457 | 16.3 | 0.99
5458 | 16.3 | 0.99
5459 | 16.4 | 0.99
5460 | 16.4 | 0.99
5461 | 17.5 | 0.97
5462 | 19.4 | 0.77
5463 | 19.8 | 0.72
5464 | 18.8 | 0.65
5465 | 18.9 | 0.66
5466 | 17.4 | 0.72
5467 | 16.3 | 0.79
5468 | 15.7 | 0.8
5469 | 15.1 | 0.84
5470 | 14.3 | 0.89
5471 | 14 | 0.92
5472 | 14.1 | 0.94
5473 | 13.4 | 0.94
5474 | 12.5 | 0.92
5475 | 12 | 0.89
5476 | 11.1 | 0.91
5477 | 10.4 | 0.95
5478 | 10.3 | 0.95
5479 | 11.3 | 0.94
5480 | 12.4 | 0.9
5481 | 13.5 | 0.86
5482 | 14 | 0.82
5483 | 16.2 | 0.69
5484 | 16.7 | 0.72
5485 | 16.5 | 0.72
5486 | 16.8 | 0.63
5487 | 16.6 | 0.66
5488 | 16.5 | 0.67
5489 | 16.7 | 0.64
5490 | 16.3 | 0.71
5491 | 14.9 | 0.71
5492 | 13.9 | 0.81
5493 | 12.4 | 0.89
5494 | 11.9 | 0.9
5495 | 11.4 | 0.93
5496 | 10.9 | 0.94
5497 | 11.1 | 0.95
5498 | 10.8 | 0.96
5499 | 10.4 | 0.97
5500 | 10.2 | 0.96
5501 | 10.5 | 0.96
5502 | 10.2 | 0.96
5503 | 10.6 | 0.94
5504 | 11.7 | 0.9
5505 | 13.1 | 0.86
5506 | 14.4 | 0.72
5507 | 16.1 | 0.66
5508 | 16.3 | 0.64
5509 | 16.5 | 0.66
5510 | 18.2 | 0.57
5511 | 17.6 | 0.61
5512 | 17.7 | 0.61
5513 | 16 | 0.69
5514 | 16.2 | 0.68
5515 | 15.4 | 0.75
5516 | 14.6 | 0.78
5517 | 13.4 | 0.85
5518 | 13.1 | 0.87
5519 | 12.7 | 0.93
5520 | 12.3 | 0.9
5521 | 11.9 | 0.91
5522 | 11.3 | 0.93
5523 | 11.1 | 0.91
5524 | 10.5 | 0.91
5525 | 10.6 | 0.9
5526 | 10.1 | 0.9
5527 | 10.1 | 0.9
5528 | 11.3 | 0.86
5529 | 12.4 | 0.85
5530 | 14.3 | 0.73
5531 | 16.2 | 0.62
5532 | 15.5 | 0.69
5533 | 14 | 0.82
5534 | 16.4 | 0.63
5535 | 15.2 | 0.67
5536 | 17.5 | 0.59
5537 | 16.5 | 0.58
5538 | 16 | 0.59
5539 | 15.5 | 0.57
5540 | 14.5 | 0.62
5541 | 13.1 | 0.69
5542 | 12 | 0.76
5543 | 10.9 | 0.82
5544 | 9.5 | 0.87
5545 | 8.3 | 0.92
5546 | 9.9 | 0.87
5547 | 9.3 | 0.88
5548 | 9.7 | 0.88
5549 | 10.1 | 0.91
5550 | 10.9 | 0.91
5551 | 11.1 | 0.92
5552 | 11.7 | 0.95
5553 | 12.8 | 0.96
5554 | 13.7 | 0.97
5555 | 15 | 0.92
5556 | 16.7 | 0.78
5557 | 16.9 | 0.82
5558 | 17.1 | 0.71
5559 | 17.1 | 0.74
5560 | 17.4 | 0.65
5561 | 17 | 0.65
5562 | 15.8 | 0.74
5563 | 16.1 | 0.76
5564 | 14.7 | 0.82
5565 | 13.3 | 0.87
5566 | 12.7 | 0.92
5567 | 12.6 | 0.95
5568 | 12.5 | 0.96
5569 | 13.1 | 0.98
5570 | 12.4 | 0.98
5571 | 12.7 | 0.98
5572 | 13.3 | 0.99
5573 | 13.4 | 0.98
5574 | 13.4 | 0.98
5575 | 13.5 | 0.97
5576 | 13.9 | 0.95
5577 | 14.3 | 0.92
5578 | 15 | 0.88
5579 | 15.2 | 0.86
5580 | 15.6 | 0.85
5581 | 15.5 | 0.86
5582 | 15.5 | 0.85
5583 | 15.5 | 0.87
5584 | 15.4 | 0.85
5585 | 14.5 | 0.93
5586 | 14.3 | 0.98
5587 | 14.4 | 0.98
5588 | 14.5 | 0.98
5589 | 14.6 | 0.98
5590 | 14.6 | 0.98
5591 | 14.8 | 0.97
5592 | 14.8 | 0.97
5593 | 14.8 | 0.96
5594 | 14.9 | 0.97
5595 | 14.9 | 0.98
5596 | 14.7 | 0.98
5597 | 14.8 | 0.99
5598 | 15.1 | 0.99
5599 | 15.3 | 0.98
5600 | 15.3 | 0.98
5601 | 15.4 | 0.95
5602 | 16 | 0.93
5603 | 16.3 | 0.89
5604 | 17.1 | 0.89
5605 | 16.9 | 0.94
5606 | 17.6 | 0.91
5607 | 18.1 | 0.89
5608 | 19.4 | 0.84
5609 | 18.2 | 0.9
5610 | 17.6 | 0.93
5611 | 17.6 | 0.89
5612 | 16.4 | 0.94
5613 | 15.9 | 0.97
5614 | 15.4 | 0.98
5615 | 15.1 | 0.98
5616 | 14.9 | 0.99
5617 | 14.7 | 0.99
5618 | 14.5 | 0.99
5619 | 14.1 | 0.98
5620 | 13.6 | 0.97
5621 | 13.6 | 0.97
5622 | 13.2 | 0.98
5623 | 13.6 | 0.98
5624 | 14.2 | 0.98
5625 | 15.3 | 0.92
5626 | 16.2 | 0.89
5627 | 15.6 | 0.88
5628 | 16.1 | 0.84
5629 | 15.6 | 0.91
5630 | 18 | 0.75
5631 | 17.3 | 0.79
5632 | 17.2 | 0.75
5633 | 16.9 | 0.75
5634 | 16.5 | 0.83
5635 | 15.6 | 0.89
5636 | 15.3 | 0.93
5637 | 14.3 | 0.95
5638 | 13.7 | 0.99
5639 | 13.9 | 0.99
5640 | 14.1 | 0.98
5641 | 14 | 0.99
5642 | 14.9 | 0.99
5643 | 15.1 | 0.99
5644 | 14.6 | 1
5645 | 14.4 | 0.99
5646 | 14.5 | 0.99
5647 | 15 | 0.99
5648 | 15.5 | 0.99
5649 | 16.3 | 0.98
5650 | 17 | 0.95
5651 | 18 | 0.9
5652 | 18.7 | 0.84
5653 | 18 | 0.9
5654 | 17.8 | 0.91
5655 | 18.3 | 0.86
5656 | 18.8 | 0.83
5657 | 18.8 | 0.8
5658 | 19.3 | 0.8
5659 | 19.4 | 0.75
5660 | 17.2 | 0.93
5661 | 17.2 | 0.87
5662 | 16.5 | 0.89
5663 | 15.6 | 0.92
5664 | 15.1 | 0.93
5665 | 15.1 | 0.91
5666 | 14.8 | 0.91
5667 | 14.4 | 0.89
5668 | 14.2 | 0.87
5669 | 13.7 | 0.86
5670 | 13.2 | 0.87
5671 | 13 | 0.87
5672 | 13.4 | 0.85
5673 | 14.4 | 0.8
5674 | 16 | 0.73
5675 | 16.4 | 0.71
5676 | 17.5 | 0.68
5677 | 18.5 | 0.63
5678 | 18.7 | 0.6
5679 | 19.8 | 0.57
5680 | 19.5 | 0.58
5681 | 20 | 0.58
5682 | 18.3 | 0.61
5683 | 17.7 | 0.67
5684 | 17.1 | 0.71
5685 | 15.9 | 0.77
5686 | 14.5 | 0.82
5687 | 13.7 | 0.85
5688 | 13 | 0.87
5689 | 12.4 | 0.9
5690 | 12.1 | 0.92
5691 | 11.8 | 0.9
5692 | 11.2 | 0.94
5693 | 11 | 0.94
5694 | 11.5 | 0.93
5695 | 10.7 | 0.92
5696 | 11.7 | 0.9
5697 | 12.8 | 0.89
5698 | 14.7 | 0.79
5699 | 15.6 | 0.74
5700 | 16.7 | 0.71
5701 | 17.1 | 0.66
5702 | 18.4 | 0.68
5703 | 18.2 | 0.72
5704 | 18.1 | 0.72
5705 | 16.4 | 0.82
5706 | 15.8 | 0.83
5707 | 15.4 | 0.86
5708 | 14.8 | 0.9
5709 | 14.4 | 0.93
5710 | 13.1 | 0.95
5711 | 13 | 0.98
5712 | 13.1 | 0.98
5713 | 13.2 | 0.98
5714 | 13.2 | 0.99
5715 | 13.4 | 0.99
5716 | 13.8 | 0.99
5717 | 14 | 0.99
5718 | 14.2 | 0.99
5719 | 14 | 0.98
5720 | 14 | 0.98
5721 | 14 | 0.98
5722 | 14.3 | 0.98
5723 | 15.2 | 0.96
5724 | 14.8 | 0.98
5725 | 14.7 | 0.97
5726 | 15.3 | 0.93
5727 | 15.2 | 0.91
5728 | 16.1 | 0.86
5729 | 15.4 | 0.9
5730 | 15.5 | 0.9
5731 | 15 | 0.97
5732 | 14.4 | 0.98
5733 | 15 | 0.99
5734 | 13.9 | 0.98
5735 | 13.1 | 0.96
5736 | 13.1 | 0.95
5737 | 12.4 | 0.94
5738 | 11.8 | 0.96
5739 | 11.5 | 0.93
5740 | 10.3 | 0.92
5741 | 9.7 | 0.95
5742 | 9.5 | 0.93
5743 | 9.9 | 0.91
5744 | 10.7 | 0.89
5745 | 12.2 | 0.83
5746 | 14.3 | 0.76
5747 | 14.7 | 0.71
5748 | 16 | 0.68
5749 | 16.7 | 0.65
5750 | 16.2 | 0.7
5751 | 17 | 0.63
5752 | 16.4 | 0.68
5753 | 16.5 | 0.72
5754 | 15.6 | 0.75
5755 | 14.8 | 0.8
5756 | 14.4 | 0.84
5757 | 12.6 | 0.92
5758 | 11.7 | 0.94
5759 | 11.4 | 0.95
5760 | 10.9 | 0.97
5761 | 10.8 | 0.96
5762 | 10.5 | 0.96
5763 | 10.4 | 0.96
5764 | 10.4 | 0.96
5765 | 11.8 | 0.95
5766 | 12.3 | 0.94
5767 | 13.1 | 0.94
5768 | 13.4 | 0.93
5769 | 14.2 | 0.92
5770 | 14.9 | 0.9
5771 | 16.1 | 0.82
5772 | 16.3 | 0.81
5773 | 16.5 | 0.85
5774 | 15.7 | 0.9
5775 | 16.6 | 0.86
5776 | 17.1 | 0.82
5777 | 16.4 | 0.85
5778 | 16.6 | 0.82
5779 | 16 | 0.87
5780 | 15.2 | 0.86
5781 | 14.8 | 0.88
5782 | 14.6 | 0.93
5783 | 14.7 | 0.93
5784 | 15.1 | 0.91
5785 | 15.3 | 0.91
5786 | 15.3 | 0.93
5787 | 15.3 | 0.91
5788 | 15.3 | 0.92
5789 | 15.3 | 0.93
5790 | 15.3 | 0.92
5791 | 15.4 | 0.91
5792 | 15.3 | 0.93
5793 | 15.4 | 0.92
5794 | 15.6 | 0.92
5795 | 16.7 | 0.87
5796 | 16.3 | 0.88
5797 | 16.2 | 0.88
5798 | 16.8 | 0.87
5799 | 17.4 | 0.87
5800 | 17.3 | 0.86
5801 | 17.1 | 0.86
5802 | 16.3 | 0.89
5803 | 16 | 0.9
5804 | 15.5 | 0.93
5805 | 15.4 | 0.93
5806 | 15.3 | 0.93
5807 | 15.4 | 0.93
5808 | 15.5 | 0.92
5809 | 15.4 | 0.93
5810 | 15.1 | 0.98
5811 | 14.9 | 0.99
5812 | 14.8 | 0.98
5813 | 12.3 | 0.93
5814 | 11.6 | 0.89
5815 | 11.2 | 0.88
5816 | 11.5 | 0.86
5817 | 12.6 | 0.81
5818 | 13.7 | 0.73
5819 | 14.8 | 0.66
5820 | 15.2 | 0.63
5821 | 16.1 | 0.63
5822 | 15.3 | 0.64
5823 | 15.4 | 0.59
5824 | 16.3 | 0.57
5825 | 16 | 0.6
5826 | 14.9 | 0.56
5827 | 14.3 | 0.63
5828 | 13.1 | 0.73
5829 | 11.9 | 0.77
5830 | 11.1 | 0.85
5831 | 11.1 | 0.83
5832 | 10.9 | 0.84
5833 | 10.8 | 0.84
5834 | 10.6 | 0.84
5835 | 10.2 | 0.85
5836 | 9.8 | 0.84
5837 | 9.5 | 0.87
5838 | 9 | 0.88
5839 | 8.9 | 0.89
5840 | 10.2 | 0.82
5841 | 11.7 | 0.78
5842 | 12.9 | 0.7
5843 | 14.1 | 0.65
5844 | 14.9 | 0.66
5845 | 16.7 | 0.57
5846 | 15.4 | 0.57
5847 | 16.2 | 0.66
5848 | 16 | 0.69
5849 | 16 | 0.66
5850 | 15.6 | 0.63
5851 | 14.8 | 0.74
5852 | 14.1 | 0.8
5853 | 13 | 0.84
5854 | 12.2 | 0.89
5855 | 11.9 | 0.93
5856 | 11.6 | 0.91
5857 | 11.1 | 0.9
5858 | 11.3 | 0.9
5859 | 11.6 | 0.93
5860 | 11.8 | 0.89
5861 | 10.7 | 0.94
5862 | 11.6 | 0.91
5863 | 10.7 | 0.95
5864 | 12 | 0.95
5865 | 13.1 | 0.93
5866 | 14.6 | 0.88
5867 | 15.3 | 0.82
5868 | 16 | 0.75
5869 | 17.9 | 0.69
5870 | 17.6 | 0.67
5871 | 17.3 | 0.71
5872 | 16.8 | 0.7
5873 | 15.7 | 0.73
5874 | 15.2 | 0.75
5875 | 15.1 | 0.73
5876 | 13.2 | 0.88
5877 | 13.4 | 0.87
5878 | 12.6 | 0.92
5879 | 12.3 | 0.94
5880 | 13.1 | 0.95
5881 | 13.7 | 0.92
5882 | 13.1 | 0.93
5883 | 13.5 | 0.9
5884 | 13.5 | 0.91
5885 | 13.3 | 0.96
5886 | 13.5 | 0.98
5887 | 13.8 | 0.99
5888 | 14.2 | 0.99
5889 | 14.6 | 0.99
5890 | 15.2 | 0.98
5891 | 15.3 | 0.98
5892 | 15.6 | 0.99
5893 | 16.6 | 0.95
5894 | 16.8 | 0.96
5895 | 17.9 | 0.89
5896 | 17 | 0.94
5897 | 16.1 | 0.98
5898 | 16.6 | 0.98
5899 | 16.4 | 0.95
5900 | 16 | 0.97
5901 | 15.4 | 0.95
5902 | 14.6 | 0.98
5903 | 14.7 | 0.97
5904 | 13.8 | 0.85
5905 | 12.1 | 0.89
5906 | 11.5 | 0.86
5907 | 10.8 | 0.81
5908 | 10.1 | 0.84
5909 | 10.3 | 0.86
5910 | 9.5 | 0.89
5911 | 9.4 | 0.88
5912 | 10.2 | 0.88
5913 | 12.3 | 0.83
5914 | 13.2 | 0.82
5915 | 13.5 | 0.87
5916 | 16.1 | 0.7
5917 | 15.7 | 0.64
5918 | 14.6 | 0.65
5919 | 15.7 | 0.59
5920 | 15.9 | 0.58
5921 | 15.4 | 0.58
5922 | 14.8 | 0.58
5923 | 14 | 0.65
5924 | 12.2 | 0.72
5925 | 11.7 | 0.72
5926 | 10.9 | 0.76
5927 | 10.5 | 0.74
5928 | 9.6 | 0.74
5929 | 8 | 0.8
5930 | 8.4 | 0.78
5931 | 8.4 | 0.79
5932 | 8.1 | 0.83
5933 | 8.8 | 0.86
5934 | 9.6 | 0.83
5935 | 9.7 | 0.83
5936 | 10.9 | 0.8
5937 | 11.7 | 0.78
5938 | 12.9 | 0.76
5939 | 13.9 | 0.66
5940 | 14.8 | 0.66
5941 | 15.3 | 0.65
5942 | 16.6 | 0.59
5943 | 17 | 0.59
5944 | 17.4 | 0.59
5945 | 18 | 0.59
5946 | 17.2 | 0.57
5947 | 16 | 0.64
5948 | 14 | 0.73
5949 | 12.3 | 0.78
5950 | 10.2 | 0.87
5951 | 10.4 | 0.88
5952 | 10.1 | 0.91
5953 | 12 | 0.81
5954 | 11.8 | 0.84
5955 | 12 | 0.84
5956 | 12.3 | 0.84
5957 | 12.6 | 0.86
5958 | 12.5 | 0.9
5959 | 12.6 | 0.92
5960 | 13.1 | 0.92
5961 | 14.3 | 0.9
5962 | 14.7 | 0.91
5963 | 16.2 | 0.83
5964 | 16.8 | 0.79
5965 | 17.2 | 0.61
5966 | 16.4 | 0.65
5967 | 16.6 | 0.61
5968 | 16.7 | 0.58
5969 | 16.9 | 0.53
5970 | 16.4 | 0.52
5971 | 15.2 | 0.61
5972 | 13.6 | 0.67
5973 | 12.5 | 0.77
5974 | 12 | 0.8
5975 | 11.4 | 0.83
5976 | 11.3 | 0.84
5977 | 10.9 | 0.85
5978 | 11.1 | 0.85
5979 | 11.6 | 0.79
5980 | 11.4 | 0.79
5981 | 11.4 | 0.78
5982 | 11.3 | 0.8
5983 | 11.6 | 0.81
5984 | 11.4 | 0.85
5985 | 11.7 | 0.85
5986 | 12.4 | 0.82
5987 | 13.5 | 0.75
5988 | 13.8 | 0.69
5989 | 15.3 | 0.59
5990 | 15.6 | 0.58
5991 | 15.4 | 0.6
5992 | 15.6 | 0.57
5993 | 15.8 | 0.57
5994 | 15.7 | 0.57
5995 | 15.1 | 0.6
5996 | 15 | 0.61
5997 | 14 | 0.67
5998 | 13.1 | 0.7
5999 | 12.2 | 0.76
6000 | 11.3 | 0.82
6001 | 10.7 | 0.85
6002 | 10.4 | 0.86
6003 | 10.1 | 0.88
6004 | 10 | 0.87
6005 | 9.8 | 0.88
6006 | 9.1 | 0.91
6007 | 9 | 0.93
6008 | 9.4 | 0.92
6009 | 11.4 | 0.89
6010 | 12.8 | 0.88
6011 | 14.6 | 0.79
6012 | 15.4 | 0.75
6013 | 15.5 | 0.77
6014 | 15.6 | 0.81
6015 | 15.1 | 0.86
6016 | 14.3 | 0.86
6017 | 14.4 | 0.87
6018 | 13.1 | 0.99
6019 | 13.3 | 1
6020 | 13 | 0.98
6021 | 12.7 | 0.98
6022 | 12.6 | 0.99
6023 | 12.6 | 1
6024 | 12.6 | 0.99
6025 | 12.6 | 0.98
6026 | 12.7 | 0.82
6027 | 11.8 | 0.94
6028 | 11.3 | 0.89
6029 | 10.5 | 0.9
6030 | 10.6 | 0.89
6031 | 10.7 | 0.87
6032 | 10.8 | 0.85
6033 | 11.9 | 0.83
6034 | 12.8 | 0.79
6035 | 13.8 | 0.7
6036 | 14.1 | 0.68
6037 | 15.6 | 0.57
6038 | 15.3 | 0.59
6039 | 15.8 | 0.6
6040 | 14.7 | 0.58
6041 | 13 | 0.76
6042 | 14.2 | 0.7
6043 | 14.2 | 0.66
6044 | 12.5 | 0.7
6045 | 11.4 | 0.76
6046 | 10.6 | 0.81
6047 | 10 | 0.83
6048 | 9.3 | 0.87
6049 | 9.4 | 0.85
6050 | 8.7 | 0.88
6051 | 8.5 | 0.9
6052 | 8.5 | 0.9
6053 | 8.2 | 0.92
6054 | 8.5 | 0.9
6055 | 8.6 | 0.9
6056 | 10.1 | 0.86
6057 | 11.1 | 0.81
6058 | 13.2 | 0.74
6059 | 14 | 0.66
6060 | 14.9 | 0.65
6061 | 14.4 | 0.7
6062 | 14.6 | 0.71
6063 | 15.1 | 0.73
6064 | 14.9 | 0.75
6065 | 14.7 | 0.81
6066 | 14.3 | 0.89
6067 | 13.6 | 0.95
6068 | 13.9 | 0.98
6069 | 14.2 | 0.99
6070 | 14.5 | 0.98
6071 | 14.8 | 0.98
6072 | 15 | 0.98
6073 | 15.1 | 0.98
6074 | 15.7 | 0.97
6075 | 15.7 | 0.97
6076 | 15.7 | 0.94
6077 | 15.9 | 0.94
6078 | 15.7 | 0.95
6079 | 15.7 | 0.97
6080 | 16 | 0.95
6081 | 15.6 | 0.9
6082 | 15.7 | 0.87
6083 | 16 | 0.79
6084 | 17.7 | 0.71
6085 | 18.2 | 0.65
6086 | 17.7 | 0.66
6087 | 18.9 | 0.56
6088 | 18.5 | 0.6
6089 | 18.6 | 0.58
6090 | 18.4 | 0.62
6091 | 17.2 | 0.67
6092 | 15.1 | 0.8
6093 | 14.6 | 0.83
6094 | 13.8 | 0.9
6095 | 13.8 | 0.86
6096 | 13.3 | 0.94
6097 | 13.5 | 0.99
6098 | 14.1 | 1
6099 | 14.9 | 0.99
6100 | 15.1 | 0.99
6101 | 15.1 | 0.99
6102 | 15.1 | 0.99
6103 | 14.7 | 0.98
6104 | 14.9 | 0.97
6105 | 15.1 | 0.99
6106 | 15.4 | 0.98
6107 | 15.8 | 0.99
6108 | 16.6 | 0.99
6109 | 17.6 | 0.93
6110 | 18.2 | 0.93
6111 | 17.5 | 0.83
6112 | 16.5 | 0.8
6113 | 16.2 | 0.74
6114 | 15.3 | 0.73
6115 | 14.5 | 0.69
6116 | 12.9 | 0.75
6117 | 11.9 | 0.75
6118 | 11.2 | 0.79
6119 | 10.5 | 0.83
6120 | 10.2 | 0.86
6121 | 9.7 | 0.87
6122 | 9.4 | 0.88
6123 | 8.2 | 0.92
6124 | 8.1 | 0.93
6125 | 8.5 | 0.9
6126 | 8.4 | 0.92
6127 | 8.6 | 0.9
6128 | 8.7 | 0.9
6129 | 10.5 | 0.87
6130 | 12.5 | 0.78
6131 | 14.3 | 0.73
6132 | 15.3 | 0.64
6133 | 16.1 | 0.54
6134 | 16.7 | 0.5
6135 | 17.2 | 0.53
6136 | 17.7 | 0.5
6137 | 16.1 | 0.65
6138 | 15.2 | 0.66
6139 | 13.7 | 0.73
6140 | 11.3 | 0.82
6141 | 11.4 | 0.82
6142 | 11.6 | 0.82
6143 | 11.3 | 0.84
6144 | 10.6 | 0.87
6145 | 10 | 0.88
6146 | 9.9 | 0.91
6147 | 9.1 | 0.92
6148 | 9.5 | 0.92
6149 | 9.1 | 0.93
6150 | 8.4 | 0.96
6151 | 8.3 | 0.96
6152 | 9.2 | 0.93
6153 | 11.7 | 0.93
6154 | 13.6 | 0.87
6155 | 14.4 | 0.82
6156 | 15.6 | 0.75
6157 | 17.1 | 0.68
6158 | 17.5 | 0.6
6159 | 17.9 | 0.66
6160 | 18.2 | 0.61
6161 | 18.2 | 0.63
6162 | 17.3 | 0.63
6163 | 16.3 | 0.71
6164 | 13.7 | 0.85
6165 | 13.1 | 0.88
6166 | 12.9 | 0.89
6167 | 12.1 | 0.9
6168 | 10.7 | 0.96
6169 | 10.7 | 0.95
6170 | 11.2 | 0.96
6171 | 11.1 | 0.97
6172 | 12.5 | 0.96
6173 | 12.7 | 0.98
6174 | 12.6 | 0.99
6175 | 13 | 0.99
6176 | 13.5 | 0.98
6177 | 13.7 | 0.99
6178 | 14.3 | 0.98
6179 | 15.3 | 0.97
6180 | 16.6 | 0.89
6181 | 16.9 | 0.88
6182 | 18.9 | 0.8
6183 | 19.3 | 0.78
6184 | 18.5 | 0.81
6185 | 18.4 | 0.79
6186 | 17.5 | 0.83
6187 | 16.8 | 0.86
6188 | 15.8 | 0.9
6189 | 15.2 | 0.92
6190 | 14.8 | 0.94
6191 | 14.7 | 0.94
6192 | 14.5 | 0.97
6193 | 14.6 | 0.97
6194 | 14.8 | 0.96
6195 | 14.9 | 0.97
6196 | 15 | 0.98
6197 | 15.1 | 0.97
6198 | 15.1 | 0.97
6199 | 15.1 | 0.97
6200 | 15.4 | 0.96
6201 | 15.9 | 0.94
6202 | 16.9 | 0.9
6203 | 17.3 | 0.87
6204 | 18.1 | 0.82
6205 | 18.7 | 0.8
6206 | 18.7 | 0.79
6207 | 17.3 | 0.9
6208 | 17.9 | 0.84
6209 | 18.3 | 0.78
6210 | 17.4 | 0.81
6211 | 14.8 | 0.96
6212 | 14.4 | 0.98
6213 | 13.9 | 0.98
6214 | 13.6 | 0.98
6215 | 13.2 | 0.98
6216 | 13.1 | 0.98
6217 | 12.8 | 0.98
6218 | 12.7 | 0.99
6219 | 12.6 | 0.96
6220 | 12.6 | 0.98
6221 | 12.2 | 0.96
6222 | 10.2 | 0.95
6223 | 9.2 | 0.96
6224 | 9.4 | 0.96
6225 | 10.7 | 0.89
6226 | 12.2 | 0.81
6227 | 13.8 | 0.75
6228 | 14.4 | 0.73
6229 | 15.5 | 0.67
6230 | 16.3 | 0.67
6231 | 16.7 | 0.65
6232 | 16.2 | 0.68
6233 | 15.3 | 0.67
6234 | 15 | 0.67
6235 | 13.6 | 0.77
6236 | 11.4 | 0.84
6237 | 11.1 | 0.85
6238 | 11.5 | 0.85
6239 | 11 | 0.87
6240 | 10.6 | 0.9
6241 | 10.4 | 0.91
6242 | 10.1 | 0.92
6243 | 9.7 | 0.93
6244 | 8.9 | 0.95
6245 | 8.7 | 0.96
6246 | 8.3 | 0.96
6247 | 8.3 | 0.93
6248 | 9 | 0.89
6249 | 10.7 | 0.86
6250 | 12.5 | 0.87
6251 | 13.7 | 0.86
6252 | 14.8 | 0.84
6253 | 16.3 | 0.75
6254 | 16.7 | 0.72
6255 | 17.3 | 0.68
6256 | 17.9 | 0.66
6257 | 17.8 | 0.64
6258 | 16.6 | 0.74
6259 | 14.9 | 0.82
6260 | 12.4 | 0.92
6261 | 11.7 | 0.96
6262 | 11.7 | 0.96
6263 | 12.1 | 0.98
6264 | 12.1 | 0.98
6265 | 11.8 | 0.98
6266 | 11 | 1
6267 | 10.4 | 1
6268 | 10.1 | 1
6269 | 9.8 | 1
6270 | 10.1 | 1
6271 | 10.2 | 1
6272 | 10.8 | 1
6273 | 11.8 | 1
6274 | 13.5 | 0.99
6275 | 14.7 | 0.9
6276 | 16.3 | 0.76
6277 | 17.7 | 0.64
6278 | 17.5 | 0.73
6279 | 17.6 | 0.7
6280 | 17.6 | 0.67
6281 | 17.1 | 0.73
6282 | 16.4 | 0.75
6283 | 15.2 | 0.8
6284 | 13.6 | 0.95
6285 | 13.1 | 0.94
6286 | 13.1 | 0.96
6287 | 12.9 | 1
6288 | 12.7 | 1
6289 | 12.5 | 0.96
6290 | 12.6 | 0.96
6291 | 12.5 | 0.96
6292 | 12.6 | 0.96
6293 | 12.6 | 0.98
6294 | 13.6 | 0.98
6295 | 13.4 | 0.94
6296 | 13.6 | 0.94
6297 | 14.4 | 0.9
6298 | 14.8 | 0.9
6299 | 15 | 0.86
6300 | 16 | 0.8
6301 | 16.1 | 0.79
6302 | 16.1 | 0.76
6303 | 16.2 | 0.76
6304 | 15.6 | 0.81
6305 | 15.8 | 0.77
6306 | 15.5 | 0.79
6307 | 14.9 | 0.83
6308 | 14.1 | 0.8
6309 | 14 | 0.79
6310 | 13.7 | 0.83
6311 | 13.9 | 0.84
6312 | 14.1 | 0.87
6313 | 14.7 | 0.85
6314 | 14.9 | 0.85
6315 | 15.2 | 0.84
6316 | 15.3 | 0.84
6317 | 15 | 0.85
6318 | 14.9 | 0.86
6319 | 15.3 | 0.86
6320 | 15.5 | 0.86
6321 | 15.4 | 0.89
6322 | 15.1 | 0.93
6323 | 15 | 0.98
6324 | 15.4 | 0.98
6325 | 15.7 | 0.98
6326 | 15.9 | 0.97
6327 | 15.9 | 0.98
6328 | 15.9 | 0.98
6329 | 15.7 | 0.99
6330 | 15.7 | 0.99
6331 | 15.6 | 0.99
6332 | 15.6 | 0.99
6333 | 15.6 | 0.99
6334 | 15.6 | 0.98
6335 | 14.3 | 0.98
6336 | 14.5 | 0.99
6337 | 14.7 | 0.99
6338 | 14.7 | 1
6339 | 14.8 | 0.99
6340 | 14.3 | 1
6341 | 14.1 | 1
6342 | 14 | 0.99
6343 | 13.6 | 0.99
6344 | 13 | 0.98
6345 | 13.2 | 0.99
6346 | 14 | 0.97
6347 | 14.7 | 0.89
6348 | 15.9 | 0.78
6349 | 15.9 | 0.77
6350 | 14.4 | 0.84
6351 | 16.2 | 0.69
6352 | 16.4 | 0.65
6353 | 16.1 | 0.66
6354 | 15.2 | 0.7
6355 | 14.5 | 0.75
6356 | 12.9 | 0.84
6357 | 11.6 | 0.85
6358 | 10.7 | 0.9
6359 | 9.9 | 0.92
6360 | 8.8 | 0.97
6361 | 8.4 | 0.97
6362 | 8.9 | 0.99
6363 | 10.2 | 0.97
6364 | 10.6 | 0.99
6365 | 12 | 0.98
6366 | 13.1 | 0.96
6367 | 13.8 | 0.98
6368 | 14.2 | 0.97
6369 | 13.6 | 0.97
6370 | 13.8 | 0.97
6371 | 14.1 | 0.99
6372 | 14.5 | 0.99
6373 | 15.9 | 0.98
6374 | 17.2 | 0.95
6375 | 16.9 | 0.96
6376 | 17.2 | 0.93
6377 | 16.3 | 0.98
6378 | 16.1 | 0.98
6379 | 16 | 0.97
6380 | 15.7 | 0.98
6381 | 15.6 | 0.99
6382 | 15.7 | 0.99
6383 | 15.5 | 0.98
6384 | 15.2 | 0.98
6385 | 14.6 | 0.97
6386 | 14.4 | 0.98
6387 | 14.3 | 0.99
6388 | 14.5 | 0.98
6389 | 14.2 | 0.98
6390 | 14 | 0.97
6391 | 13.3 | 0.96
6392 | 13.6 | 0.94
6393 | 14.3 | 0.92
6394 | 14.1 | 0.95
6395 | 14.3 | 0.99
6396 | 14.9 | 0.97
6397 | 15.2 | 0.95
6398 | 15 | 0.94
6399 | 14.1 | 0.95
6400 | 14 | 0.98
6401 | 14.1 | 0.99
6402 | 14.8 | 0.99
6403 | 14.9 | 0.98
6404 | 14.9 | 0.97
6405 | 14.4 | 0.97
6406 | 14.3 | 0.97
6407 | 14.4 | 0.93
6408 | 14.2 | 0.92
6409 | 14.4 | 0.92
6410 | 14.1 | 0.91
6411 | 13.8 | 0.92
6412 | 13.4 | 0.91
6413 | 13.6 | 0.97
6414 | 13.4 | 0.95
6415 | 13.1 | 0.92
6416 | 12.1 | 0.98
6417 | 12.8 | 0.91
6418 | 13 | 0.92
6419 | 13.7 | 0.94
6420 | 14.6 | 0.97
6421 | 16 | 0.95
6422 | 16.1 | 0.94
6423 | 16.3 | 0.94
6424 | 16.5 | 0.9
6425 | 15.6 | 0.96
6426 | 15.1 | 0.97
6427 | 14.9 | 0.98
6428 | 15.3 | 0.99
6429 | 15.3 | 0.98
6430 | 14.6 | 0.96
6431 | 14 | 0.93
6432 | 12.8 | 0.93
6433 | 12.1 | 0.95
6434 | 12.6 | 0.95
6435 | 12.2 | 0.89
6436 | 11.8 | 0.95
6437 | 11.9 | 0.9
6438 | 11.8 | 0.91
6439 | 11 | 0.91
6440 | 11.1 | 0.92
6441 | 12 | 0.89
6442 | 12.8 | 0.87
6443 | 13.9 | 0.83
6444 | 14.3 | 0.81
6445 | 13.8 | 0.87
6446 | 14.5 | 0.81
6447 | 14.8 | 0.83
6448 | 13.5 | 0.93
6449 | 14.3 | 0.82
6450 | 14 | 0.82
6451 | 12.9 | 0.85
6452 | 12.1 | 0.88
6453 | 12.1 | 0.94
6454 | 11.8 | 0.91
6455 | 11.4 | 0.93
6456 | 11.5 | 0.94
6457 | 11.8 | 0.94
6458 | 12.1 | 0.93
6459 | 12.3 | 0.94
6460 | 12.2 | 0.92
6461 | 12.3 | 0.93
6462 | 12.3 | 0.94
6463 | 12.3 | 0.94
6464 | 12.2 | 0.94
6465 | 11.5 | 0.9
6466 | 12.3 | 0.93
6467 | 13.7 | 0.82
6468 | 14.8 | 0.7
6469 | 15.2 | 0.64
6470 | 14.4 | 0.65
6471 | 15.1 | 0.64
6472 | 16.1 | 0.63
6473 | 15.8 | 0.61
6474 | 14.5 | 0.72
6475 | 13.1 | 0.78
6476 | 11.1 | 0.89
6477 | 11.6 | 0.9
6478 | 11.9 | 0.95
6479 | 12.5 | 0.95
6480 | 12.9 | 0.93
6481 | 12.7 | 0.96
6482 | 12.5 | 0.95
6483 | 12.7 | 0.92
6484 | 12.4 | 0.95
6485 | 12.1 | 0.93
6486 | 11.8 | 0.94
6487 | 11.4 | 0.94
6488 | 11.4 | 0.94
6489 | 11.9 | 0.93
6490 | 12.8 | 0.88
6491 | 12.8 | 0.84
6492 | 13.3 | 0.78
6493 | 13.3 | 0.78
6494 | 13.5 | 0.85
6495 | 13.3 | 0.9
6496 | 12.6 | 0.95
6497 | 12.1 | 0.98
6498 | 12.4 | 0.98
6499 | 13 | 0.99
6500 | 13.7 | 0.99
6501 | 15.4 | 0.99
6502 | 15.3 | 0.99
6503 | 14.9 | 0.99
6504 | 14.9 | 0.98
6505 | 14.9 | 0.99
6506 | 14.8 | 0.99
6507 | 11.2 | 0.96
6508 | 10.7 | 0.99
6509 | 10.9 | 0.96
6510 | 10.9 | 0.96
6511 | 11.2 | 0.91
6512 | 11.3 | 0.91
6513 | 12 | 0.88
6514 | 13.6 | 0.84
6515 | 14.2 | 0.83
6516 | 14.8 | 0.81
6517 | 15.6 | 0.74
6518 | 16.3 | 0.65
6519 | 15.7 | 0.72
6520 | 16.4 | 0.7
6521 | 15.7 | 0.72
6522 | 15.4 | 0.74
6523 | 13.5 | 0.78
6524 | 11.9 | 0.82
6525 | 11.3 | 0.86
6526 | 10.9 | 0.87
6527 | 10.4 | 0.91
6528 | 10.2 | 0.91
6529 | 9.6 | 0.95
6530 | 10.2 | 0.93
6531 | 9.6 | 0.95
6532 | 9.3 | 0.96
6533 | 9.5 | 0.96
6534 | 10.5 | 0.92
6535 | 10.4 | 0.97
6536 | 11 | 0.97
6537 | 11.5 | 0.99
6538 | 11.2 | 0.97
6539 | 11.6 | 0.98
6540 | 12.9 | 1
6541 | 13.6 | 0.99
6542 | 15.8 | 0.99
6543 | 15.8 | 0.99
6544 | 16 | 0.94
6545 | 15.9 | 0.84
6546 | 14.9 | 0.87
6547 | 14.1 | 0.93
6548 | 14 | 0.94
6549 | 14.1 | 0.98
6550 | 14.2 | 0.98
6551 | 13.3 | 0.96
6552 | 13.6 | 0.99
6553 | 14 | 0.98
6554 | 13.7 | 0.98
6555 | 13.8 | 0.98
6556 | 13.5 | 0.99
6557 | 13.4 | 0.98
6558 | 13.5 | 0.99
6559 | 13.3 | 0.98
6560 | 12.9 | 0.98
6561 | 12.7 | 0.96
6562 | 12.6 | 0.94
6563 | 12.5 | 0.9
6564 | 12.1 | 0.88
6565 | 12.6 | 0.79
6566 | 11.8 | 0.81
6567 | 12.1 | 0.75
6568 | 11.9 | 0.76
6569 | 12.3 | 0.72
6570 | 12 | 0.69
6571 | 11.5 | 0.72
6572 | 10.5 | 0.71
6573 | 9.4 | 0.75
6574 | 8.5 | 0.81
6575 | 8 | 0.8
6576 | 7.6 | 0.8
6577 | 6.8 | 0.82
6578 | 6.6 | 0.87
6579 | 5.7 | 0.85
6580 | 5.2 | 0.92
6581 | 4.8 | 0.92
6582 | 4.7 | 0.89
6583 | 4.7 | 0.89
6584 | 4.5 | 0.89
6585 | 5.2 | 0.86
6586 | 6.5 | 0.84
6587 | 8.9 | 0.76
6588 | 10.5 | 0.7
6589 | 11.4 | 0.58
6590 | 11.6 | 0.56
6591 | 12.3 | 0.6
6592 | 12 | 0.63
6593 | 11.2 | 0.67
6594 | 10.2 | 0.73
6595 | 9.1 | 0.81
6596 | 8.4 | 0.82
6597 | 8.5 | 0.79
6598 | 8.2 | 0.82
6599 | 9.2 | 0.83
6600 | 9.3 | 0.84
6601 | 9.5 | 0.84
6602 | 9.5 | 0.85
6603 | 10.4 | 0.8
6604 | 10.9 | 0.81
6605 | 11.2 | 0.81
6606 | 11.7 | 0.83
6607 | 12.4 | 0.83
6608 | 12.7 | 0.88
6609 | 13.3 | 0.82
6610 | 12.6 | 0.96
6611 | 12.6 | 0.99
6612 | 13.3 | 0.99
6613 | 14.4 | 0.99
6614 | 15.2 | 0.98
6615 | 14.8 | 0.98
6616 | 14.7 | 0.94
6617 | 14.2 | 0.91
6618 | 14 | 0.83
6619 | 12.7 | 0.77
6620 | 12.3 | 0.76
6621 | 11.5 | 0.84
6622 | 12.2 | 0.76
6623 | 12.2 | 0.8
6624 | 12.2 | 0.74
6625 | 12.1 | 0.76
6626 | 11.9 | 0.78
6627 | 11.9 | 0.77
6628 | 11.9 | 0.76
6629 | 12.3 | 0.73
6630 | 11.2 | 0.79
6631 | 11.5 | 0.78
6632 | 12.2 | 0.74
6633 | 12.7 | 0.71
6634 | 13.9 | 0.68
6635 | 14 | 0.68
6636 | 14.7 | 0.66
6637 | 14.8 | 0.68
6638 | 15.5 | 0.65
6639 | 16.1 | 0.63
6640 | 15.4 | 0.62
6641 | 15.1 | 0.63
6642 | 14.1 | 0.68
6643 | 13.4 | 0.72
6644 | 12.8 | 0.72
6645 | 12.6 | 0.82
6646 | 11.5 | 0.85
6647 | 11.4 | 0.93
6648 | 12 | 0.95
6649 | 12.4 | 0.99
6650 | 13.1 | 1
6651 | 13.5 | 0.99
6652 | 13.8 | 0.99
6653 | 13.6 | 0.99
6654 | 13.6 | 0.99
6655 | 13.8 | 0.99
6656 | 13.9 | 0.99
6657 | 14 | 0.99
6658 | 14.1 | 0.99
6659 | 14.1 | 0.99
6660 | 14.4 | 0.99
6661 | 14.6 | 0.99
6662 | 14.8 | 0.99
6663 | 15 | 0.99
6664 | 15.8 | 0.99
6665 | 16.5 | 0.83
6666 | 15.6 | 0.84
6667 | 14 | 0.88
6668 | 13 | 0.86
6669 | 12.2 | 0.86
6670 | 11.3 | 0.88
6671 | 10.5 | 0.87
6672 | 10.1 | 0.88
6673 | 10 | 0.9
6674 | 9.3 | 0.92
6675 | 9.6 | 0.91
6676 | 9.9 | 0.87
6677 | 9.9 | 0.87
6678 | 9.8 | 0.87
6679 | 9.9 | 0.86
6680 | 10 | 0.86
6681 | 10.4 | 0.85
6682 | 11.8 | 0.81
6683 | 12.6 | 0.77
6684 | 13.1 | 0.73
6685 | 13.6 | 0.67
6686 | 14.1 | 0.71
6687 | 13.8 | 0.69
6688 | 13.4 | 0.73
6689 | 12.7 | 0.77
6690 | 11.9 | 0.85
6691 | 11.8 | 0.88
6692 | 11.5 | 0.93
6693 | 11.2 | 0.94
6694 | 10.4 | 0.97
6695 | 10.8 | 0.97
6696 | 10.9 | 0.97
6697 | 11.7 | 0.98
6698 | 12.2 | 1
6699 | 13.1 | 0.99
6700 | 13.7 | 0.99
6701 | 14.3 | 0.99
6702 | 13.8 | 0.99
6703 | 13.3 | 0.98
6704 | 12.7 | 0.98
6705 | 12.8 | 0.98
6706 | 13.5 | 0.93
6707 | 14.5 | 0.88
6708 | 15.1 | 0.75
6709 | 15.4 | 0.79
6710 | 14 | 0.86
6711 | 14.9 | 0.83
6712 | 14.9 | 0.8
6713 | 15 | 0.72
6714 | 13.8 | 0.74
6715 | 12.5 | 0.86
6716 | 11.8 | 0.88
6717 | 11.2 | 0.91
6718 | 10.8 | 0.94
6719 | 10.9 | 0.92
6720 | 10.6 | 0.91
6721 | 11.1 | 0.9
6722 | 10.8 | 0.91
6723 | 10.9 | 0.91
6724 | 10.9 | 0.94
6725 | 10.1 | 0.92
6726 | 9.7 | 0.93
6727 | 9.5 | 0.95
6728 | 9.3 | 0.96
6729 | 9.9 | 0.86
6730 | 10.6 | 0.81
6731 | 11.1 | 0.81
6732 | 11.4 | 0.82
6733 | 12.5 | 0.71
6734 | 12.9 | 0.72
6735 | 11.7 | 0.82
6736 | 12.4 | 0.78
6737 | 12.4 | 0.73
6738 | 11.6 | 0.76
6739 | 10.2 | 0.83
6740 | 9.9 | 0.83
6741 | 9.7 | 0.88
6742 | 9.1 | 0.92
6743 | 9.5 | 0.88
6744 | 9.4 | 0.91
6745 | 8.9 | 0.93
6746 | 8.8 | 0.89
6747 | 8.2 | 0.86
6748 | 7.3 | 0.84
6749 | 7.8 | 0.84
6750 | 7.7 | 0.89
6751 | 7.8 | 0.89
6752 | 7.9 | 0.89
6753 | 8.4 | 0.88
6754 | 10.2 | 0.82
6755 | 11 | 0.8
6756 | 12.6 | 0.76
6757 | 10.6 | 0.86
6758 | 11.9 | 0.77
6759 | 12.9 | 0.74
6760 | 12.9 | 0.63
6761 | 12 | 0.74
6762 | 11.9 | 0.68
6763 | 9.9 | 0.79
6764 | 8.8 | 0.84
6765 | 8.8 | 0.82
6766 | 7.3 | 0.88
6767 | 8.6 | 0.86
6768 | 9.1 | 0.87
6769 | 8.2 | 0.89
6770 | 9.1 | 0.87
6771 | 8.3 | 0.9
6772 | 9 | 0.92
6773 | 9.5 | 0.91
6774 | 10.2 | 0.91
6775 | 10.7 | 0.9
6776 | 10.4 | 0.96
6777 | 11.5 | 1
6778 | 12.7 | 0.96
6779 | 13.5 | 0.92
6780 | 13.4 | 0.91
6781 | 14.3 | 0.91
6782 | 14.8 | 0.86
6783 | 13.7 | 0.98
6784 | 13.9 | 0.95
6785 | 13.4 | 0.86
6786 | 13.1 | 0.85
6787 | 13 | 0.89
6788 | 12.8 | 0.95
6789 | 12.6 | 0.94
6790 | 11.6 | 0.94
6791 | 12.5 | 0.94
6792 | 12.6 | 0.94
6793 | 12.3 | 0.96
6794 | 12.3 | 0.98
6795 | 12.1 | 0.98
6796 | 11.6 | 0.98
6797 | 11.3 | 0.99
6798 | 10.5 | 0.97
6799 | 10.1 | 0.96
6800 | 9.5 | 0.97
6801 | 8.8 | 0.99
6802 | 10.7 | 0.96
6803 | 12.3 | 0.87
6804 | 13.3 | 0.76
6805 | 14 | 0.7
6806 | 12.9 | 0.72
6807 | 12.7 | 0.77
6808 | 12.3 | 0.76
6809 | 11.7 | 0.76
6810 | 11 | 0.86
6811 | 10.4 | 0.91
6812 | 10.1 | 0.91
6813 | 9.4 | 0.92
6814 | 9.1 | 0.92
6815 | 8.3 | 0.94
6816 | 8.3 | 0.94
6817 | 7.9 | 0.96
6818 | 7.3 | 0.97
6819 | 7.2 | 0.97
6820 | 6.9 | 0.97
6821 | 6.7 | 0.98
6822 | 6.4 | 0.98
6823 | 6.1 | 0.98
6824 | 5.8 | 0.98
6825 | 8 | 0.99
6826 | 10.4 | 0.94
6827 | 12.6 | 0.87
6828 | 13.1 | 0.8
6829 | 13.4 | 0.76
6830 | 14.1 | 0.7
6831 | 13.9 | 0.68
6832 | 12.9 | 0.74
6833 | 12.3 | 0.8
6834 | 11.3 | 0.89
6835 | 10.2 | 0.92
6836 | 9.5 | 0.93
6837 | 8.4 | 0.94
6838 | 8.9 | 0.95
6839 | 8.8 | 0.97
6840 | 9.2 | 0.96
6841 | 9.4 | 0.96
6842 | 9.3 | 0.97
6843 | 9.2 | 0.97
6844 | 9 | 0.97
6845 | 8.4 | 0.97
6846 | 8.4 | 0.97
6847 | 8.3 | 0.99
6848 | 8.2 | 0.99
6849 | 8.5 | 0.97
6850 | 9.5 | 0.96
6851 | 10 | 0.96
6852 | 11.6 | 0.89
6853 | 12.3 | 0.81
6854 | 12.1 | 0.74
6855 | 13.4 | 0.7
6856 | 11.4 | 0.78
6857 | 12.3 | 0.75
6858 | 11 | 0.78
6859 | 8.1 | 0.86
6860 | 7.8 | 0.9
6861 | 7.6 | 0.9
6862 | 8.4 | 0.9
6863 | 9 | 0.9
6864 | 9.6 | 0.92
6865 | 10.5 | 0.92
6866 | 10.8 | 0.92
6867 | 11.4 | 0.94
6868 | 12 | 0.94
6869 | 12.2 | 0.95
6870 | 12.3 | 0.95
6871 | 12.6 | 0.94
6872 | 12.5 | 0.93
6873 | 12.6 | 0.92
6874 | 13 | 0.95
6875 | 12.9 | 0.98
6876 | 12.8 | 0.96
6877 | 11.8 | 0.96
6878 | 12 | 0.98
6879 | 11.9 | 0.96
6880 | 12.3 | 0.98
6881 | 12.1 | 0.96
6882 | 12.1 | 0.98
6883 | 11.6 | 0.98
6884 | 11.6 | 0.96
6885 | 11.6 | 0.96
6886 | 10.2 | 0.97
6887 | 10 | 0.96
6888 | 9.9 | 0.97
6889 | 9.8 | 0.97
6890 | 9.8 | 0.97
6891 | 9.6 | 0.97
6892 | 8.9 | 0.96
6893 | 8.3 | 0.94
6894 | 8.7 | 0.94
6895 | 8.7 | 0.94
6896 | 7.2 | 0.9
6897 | 7.5 | 0.94
6898 | 9.8 | 0.86
6899 | 10.9 | 0.86
6900 | 11.7 | 0.85
6901 | 11.8 | 0.87
6902 | 12.4 | 0.88
6903 | 12.6 | 0.89
6904 | 12.1 | 0.92
6905 | 11.7 | 0.96
6906 | 11.8 | 0.98
6907 | 12.5 | 0.98
6908 | 12.8 | 0.98
6909 | 13.2 | 0.98
6910 | 10.8 | 0.97
6911 | 9.8 | 0.91
6912 | 8.6 | 0.89
6913 | 7.4 | 0.9
6914 | 7.4 | 0.88
6915 | 7.1 | 0.88
6916 | 6.6 | 0.9
6917 | 6.1 | 0.91
6918 | 6 | 0.92
6919 | 6.6 | 0.9
6920 | 6.1 | 0.92
6921 | 7.3 | 0.88
6922 | 9.2 | 0.85
6923 | 10.7 | 0.81
6924 | 11.9 | 0.76
6925 | 12.5 | 0.68
6926 | 12.2 | 0.72
6927 | 11.5 | 0.75
6928 | 11.9 | 0.7
6929 | 11 | 0.74
6930 | 10.2 | 0.78
6931 | 9 | 0.84
6932 | 9.6 | 0.82
6933 | 9.9 | 0.87
6934 | 8.8 | 0.88
6935 | 8.6 | 0.89
6936 | 8.3 | 0.92
6937 | 8.6 | 0.9
6938 | 9.4 | 0.89
6939 | 8.9 | 0.9
6940 | 9.1 | 0.89
6941 | 9.6 | 0.88
6942 | 9.3 | 0.91
6943 | 9.8 | 0.87
6944 | 9.5 | 0.93
6945 | 9 | 0.92
6946 | 9.3 | 0.93
6947 | 10.4 | 0.88
6948 | 11.2 | 0.85
6949 | 11.4 | 0.8
6950 | 8.6 | 0.93
6951 | 10.2 | 0.78
6952 | 10.2 | 0.83
6953 | 9.3 | 0.83
6954 | 7.5 | 0.88
6955 | 7.1 | 0.93
6956 | 6.8 | 0.96
6957 | 7.4 | 0.9
6958 | 7.9 | 0.91
6959 | 8 | 0.9
6960 | 8.1 | 0.89
6961 | 8.1 | 0.93
6962 | 9.4 | 0.88
6963 | 8.8 | 0.89
6964 | 8.1 | 0.92
6965 | 7.6 | 0.93
6966 | 8 | 0.93
6967 | 8.4 | 0.92
6968 | 8.9 | 0.93
6969 | 8.2 | 0.92
6970 | 9.5 | 0.91
6971 | 10.4 | 0.87
6972 | 10.4 | 0.86
6973 | 11 | 0.8
6974 | 11.3 | 0.79
6975 | 11.5 | 0.75
6976 | 11.6 | 0.73
6977 | 10.8 | 0.78
6978 | 10.5 | 0.8
6979 | 9.5 | 0.85
6980 | 8.5 | 0.9
6981 | 8.1 | 0.9
6982 | 8 | 0.92
6983 | 7.8 | 0.91
6984 | 7.8 | 0.9
6985 | 7.6 | 0.91
6986 | 7.5 | 0.91
6987 | 7.3 | 0.93
6988 | 7.3 | 0.93
6989 | 7.4 | 0.93
6990 | 7.3 | 0.93
6991 | 6.6 | 0.94
6992 | 6.5 | 0.94
6993 | 6.8 | 0.94
6994 | 7.9 | 0.89
6995 | 9.9 | 0.83
6996 | 11.2 | 0.81
6997 | 11 | 0.78
6998 | 10.6 | 0.82
6999 | 12.1 | 0.74
7000 | 11 | 0.84
7001 | 11.2 | 0.8
7002 | 10.8 | 0.82
7003 | 10 | 0.87
7004 | 9.6 | 0.89
7005 | 9 | 0.89
7006 | 8.3 | 0.87
7007 | 7.4 | 0.9
7008 | 7 | 0.91
7009 | 6.9 | 0.93
7010 | 7 | 0.94
7011 | 7.7 | 0.93
7012 | 7.6 | 0.93
7013 | 7.6 | 0.91
7014 | 7.3 | 0.88
7015 | 6.9 | 0.91
7016 | 6.9 | 0.91
7017 | 7.6 | 0.91
7018 | 8.9 | 0.88
7019 | 10.2 | 0.8
7020 | 10.7 | 0.74
7021 | 11.2 | 0.7
7022 | 11.5 | 0.6
7023 | 10.5 | 0.6
7024 | 10.3 | 0.54
7025 | 9.7 | 0.58
7026 | 9.3 | 0.61
7027 | 8.4 | 0.69
7028 | 7.8 | 0.72
7029 | 7.2 | 0.76
7030 | 6.4 | 0.81
7031 | 6.9 | 0.8
7032 | 6 | 0.83
7033 | 5.1 | 0.87
7034 | 4.8 | 0.89
7035 | 5.1 | 0.87
7036 | 4.7 | 0.87
7037 | 4 | 0.9
7038 | 3.7 | 0.9
7039 | 3.6 | 0.9
7040 | 3.6 | 0.9
7041 | 3.6 | 0.88
7042 | 4.9 | 0.86
7043 | 7 | 0.78
7044 | 9.1 | 0.73
7045 | 10.3 | 0.69
7046 | 11 | 0.67
7047 | 11.6 | 0.59
7048 | 11.9 | 0.58
7049 | 11.4 | 0.55
7050 | 10.8 | 0.6
7051 | 9.1 | 0.65
7052 | 8.7 | 0.65
7053 | 7.2 | 0.74
7054 | 7 | 0.75
7055 | 6.8 | 0.77
7056 | 6.6 | 0.69
7057 | 4.7 | 0.79
7058 | 5.6 | 0.8
7059 | 5.3 | 0.83
7060 | 6.1 | 0.79
7061 | 6.4 | 0.84
7062 | 6.3 | 0.83
7063 | 6.6 | 0.82
7064 | 6.8 | 0.85
7065 | 7.2 | 0.84
7066 | 8 | 0.85
7067 | 8.6 | 0.82
7068 | 9 | 0.84
7069 | 9.8 | 0.8
7070 | 10.4 | 0.8
7071 | 10.6 | 0.77
7072 | 10.4 | 0.8
7073 | 10.1 | 0.83
7074 | 10.1 | 0.84
7075 | 9.8 | 0.87
7076 | 9.9 | 0.87
7077 | 9.9 | 0.9
7078 | 10.1 | 0.91
7079 | 10.8 | 0.9
7080 | 10.3 | 0.92
7081 | 10.7 | 0.9
7082 | 10.6 | 0.89
7083 | 10.6 | 0.89
7084 | 10.5 | 0.9
7085 | 10.8 | 0.87
7086 | 10.7 | 0.89
7087 | 10.9 | 0.86
7088 | 10.8 | 0.86
7089 | 11.1 | 0.86
7090 | 11.3 | 0.85
7091 | 12 | 0.84
7092 | 12 | 0.83
7093 | 11.8 | 0.85
7094 | 11.4 | 0.93
7095 | 11.1 | 0.97
7096 | 11.3 | 0.97
7097 | 11.4 | 0.97
7098 | 11.7 | 0.98
7099 | 11.7 | 0.98
7100 | 11.9 | 0.99
7101 | 10.8 | 0.99
7102 | 9.2 | 0.99
7103 | 8.8 | 0.99
7104 | 8.9 | 0.99
7105 | 9.5 | 0.99
7106 | 8.7 | 0.99
7107 | 6.9 | 1
7108 | 7.4 | 1
7109 | 7.5 | 0.99
7110 | 7.1 | 0.99
7111 | 5.6 | 0.98
7112 | 5.9 | 0.97
7113 | 6.3 | 0.98
7114 | 8.9 | 0.97
7115 | 10.4 | 0.87
7116 | 11.4 | 0.84
7117 | 11.6 | 0.76
7118 | 12.6 | 0.72
7119 | 11.3 | 0.7
7120 | 11.7 | 0.72
7121 | 9.5 | 0.87
7122 | 9.4 | 0.84
7123 | 8.9 | 0.86
7124 | 8.3 | 0.86
7125 | 8.2 | 0.85
7126 | 8.2 | 0.83
7127 | 7.7 | 0.87
7128 | 7.9 | 0.86
7129 | 7.7 | 0.83
7130 | 7.4 | 0.84
7131 | 7 | 0.91
7132 | 7.3 | 0.86
7133 | 7.6 | 0.9
7134 | 7.3 | 0.96
7135 | 7.5 | 0.97
7136 | 7.6 | 0.99
7137 | 7.5 | 0.97
7138 | 7.2 | 0.99
7139 | 7 | 0.97
7140 | 7 | 0.99
7141 | 6.6 | 0.95
7142 | 6.9 | 0.96
7143 | 6.8 | 0.96
7144 | 6.5 | 0.94
7145 | 6.4 | 0.94
7146 | 6.4 | 0.92
7147 | 6.2 | 0.94
7148 | 6.1 | 0.95
7149 | 5.9 | 0.95
7150 | 5.9 | 0.95
7151 | 5.8 | 0.95
7152 | 5.7 | 0.95
7153 | 5.5 | 0.97
7154 | 5.4 | 0.97
7155 | 5.3 | 0.95
7156 | 5.1 | 0.97
7157 | 5 | 0.98
7158 | 4.8 | 0.98
7159 | 4.7 | 0.97
7160 | 4.5 | 0.95
7161 | 4.6 | 0.93
7162 | 4.5 | 0.93
7163 | 5.2 | 0.92
7164 | 6.9 | 0.87
7165 | 7.8 | 0.75
7166 | 8.4 | 0.65
7167 | 8.6 | 0.6
7168 | 8.3 | 0.62
7169 | 8.1 | 0.64
7170 | 7.2 | 0.64
7171 | 5.9 | 0.7
7172 | 5.3 | 0.72
7173 | 4.8 | 0.73
7174 | 4.4 | 0.74
7175 | 3.8 | 0.78
7176 | 4.1 | 0.79
7177 | 4.1 | 0.79
7178 | 3.6 | 0.81
7179 | 2.4 | 0.87
7180 | 3.3 | 0.83
7181 | 3.3 | 0.83
7182 | 2.3 | 0.87
7183 | 3.4 | 0.83
7184 | 2.4 | 0.89
7185 | 3.6 | 0.86
7186 | 4.4 | 0.84
7187 | 6.9 | 0.75
7188 | 7.7 | 0.76
7189 | 8.7 | 0.7
7190 | 9.3 | 0.61
7191 | 9.7 | 0.57
7192 | 9.7 | 0.57
7193 | 9.4 | 0.56
7194 | 7.9 | 0.64
7195 | 6.4 | 0.72
7196 | 5.6 | 0.77
7197 | 5.6 | 0.75
7198 | 4.8 | 0.79
7199 | 4.3 | 0.82
7200 | 4.3 | 0.8
7201 | 4.2 | 0.82
7202 | 3.4 | 0.86
7203 | 3.8 | 0.85
7204 | 4.1 | 0.85
7205 | 4 | 0.85
7206 | 4.1 | 0.85
7207 | 4.5 | 0.82
7208 | 4.6 | 0.81
7209 | 5.2 | 0.8
7210 | 6.1 | 0.79
7211 | 7.8 | 0.72
7212 | 8.5 | 0.66
7213 | 8.4 | 0.71
7214 | 8.7 | 0.77
7215 | 8.2 | 0.78
7216 | 8.5 | 0.77
7217 | 8.4 | 0.73
7218 | 7.8 | 0.75
7219 | 7.4 | 0.72
7220 | 6.7 | 0.74
7221 | 5.8 | 0.79
7222 | 5.8 | 0.76
7223 | 6 | 0.74
7224 | 6.4 | 0.75
7225 | 6.5 | 0.75
7226 | 6.7 | 0.75
7227 | 6.7 | 0.76
7228 | 6.6 | 0.78
7229 | 6.7 | 0.79
7230 | 6.8 | 0.79
7231 | 6.9 | 0.8
7232 | 7 | 0.82
7233 | 7.1 | 0.84
7234 | 7.4 | 0.84
7235 | 7.7 | 0.82
7236 | 8.5 | 0.79
7237 | 9.4 | 0.75
7238 | 10 | 0.73
7239 | 9.3 | 0.76
7240 | 8.9 | 0.77
7241 | 8.8 | 0.78
7242 | 8.9 | 0.77
7243 | 9.1 | 0.79
7244 | 9.3 | 0.8
7245 | 9.5 | 0.82
7246 | 9.6 | 0.82
7247 | 9.8 | 0.8
7248 | 9.7 | 0.82
7249 | 9.6 | 0.82
7250 | 9.6 | 0.83
7251 | 9.5 | 0.87
7252 | 9.5 | 0.87
7253 | 9.4 | 0.88
7254 | 9.4 | 0.91
7255 | 10.1 | 0.87
7256 | 9.7 | 0.93
7257 | 9.5 | 0.96
7258 | 9.6 | 0.97
7259 | 9.7 | 0.96
7260 | 9.8 | 0.95
7261 | 9.8 | 0.96
7262 | 9.8 | 0.97
7263 | 9.8 | 0.97
7264 | 10 | 0.97
7265 | 10.1 | 0.97
7266 | 10.2 | 0.97
7267 | 10.3 | 0.97
7268 | 10.3 | 0.99
7269 | 10.2 | 0.97
7270 | 10.1 | 0.99
7271 | 10.1 | 0.99
7272 | 10 | 0.99
7273 | 10.1 | 0.97
7274 | 10 | 0.97
7275 | 10.2 | 0.99
7276 | 10.2 | 0.97
7277 | 10.2 | 0.99
7278 | 10.4 | 0.99
7279 | 10.5 | 1
7280 | 10.7 | 1
7281 | 10.8 | 0.99
7282 | 11.1 | 1
7283 | 11.6 | 0.99
7284 | 11.9 | 0.99
7285 | 12.2 | 0.98
7286 | 12.3 | 0.99
7287 | 12.3 | 0.98
7288 | 12 | 0.98
7289 | 11.8 | 0.98
7290 | 11.9 | 0.99
7291 | 12.1 | 0.99
7292 | 12.2 | 0.99
7293 | 12.5 | 1
7294 | 12.5 | 1
7295 | 12.6 | 0.99
7296 | 13 | 1
7297 | 13 | 1
7298 | 12.6 | 0.99
7299 | 12.4 | 0.99
7300 | 12.4 | 0.98
7301 | 12.4 | 0.96
7302 | 12.5 | 0.96
7303 | 12.2 | 0.96
7304 | 12.1 | 0.96
7305 | 12.2 | 0.95
7306 | 12.5 | 0.98
7307 | 12.9 | 0.98
7308 | 12.6 | 0.98
7309 | 12.8 | 0.99
7310 | 12.9 | 0.98
7311 | 13.2 | 1
7312 | 13.1 | 0.98
7313 | 12.6 | 0.96
7314 | 12.4 | 0.98
7315 | 12.2 | 0.96
7316 | 11.1 | 0.91
7317 | 10.6 | 0.94
7318 | 9.3 | 0.92
7319 | 8.5 | 0.93
7320 | 8.2 | 0.96
7321 | 8.2 | 0.96
7322 | 8 | 0.93
7323 | 8.7 | 0.96
7324 | 8.9 | 0.97
7325 | 8.4 | 0.97
7326 | 8 | 0.96
7327 | 8.6 | 0.96
7328 | 9.9 | 0.95
7329 | 10.3 | 0.85
7330 | 10.3 | 0.88
7331 | 10.6 | 0.91
7332 | 10.3 | 0.9
7333 | 10 | 0.83
7334 | 9.6 | 0.82
7335 | 9.5 | 0.84
7336 | 9.5 | 0.82
7337 | 9.2 | 0.85
7338 | 8.9 | 0.81
7339 | 8.2 | 0.83
7340 | 7.1 | 0.87
7341 | 7.7 | 0.87
7342 | 7.8 | 0.9
7343 | 8.1 | 0.92
7344 | 8.6 | 0.9
7345 | 9.2 | 0.88
7346 | 8.8 | 0.92
7347 | 9.2 | 0.92
7348 | 9.4 | 0.96
7349 | 10 | 0.96
7350 | 10.4 | 0.94
7351 | 10.3 | 0.94
7352 | 10.2 | 0.95
7353 | 10.2 | 0.97
7354 | 10.5 | 0.92
7355 | 10.4 | 0.92
7356 | 10.7 | 0.9
7357 | 10.7 | 0.84
7358 | 11 | 0.74
7359 | 10.6 | 0.69
7360 | 10 | 0.72
7361 | 9.6 | 0.78
7362 | 8.8 | 0.86
7363 | 8.5 | 0.99
7364 | 7.8 | 0.93
7365 | 6.9 | 0.91
7366 | 6.2 | 0.95
7367 | 6.2 | 0.95
7368 | 6.2 | 0.95
7369 | 5.3 | 0.95
7370 | 5.5 | 0.95
7371 | 6.3 | 0.95
7372 | 6.2 | 0.95
7373 | 5.6 | 0.97
7374 | 5.8 | 0.97
7375 | 5.6 | 1
7376 | 5.5 | 0.98
7377 | 5.9 | 0.98
7378 | 5.9 | 0.95
7379 | 5.9 | 0.94
7380 | 7.3 | 0.88
7381 | 7.7 | 0.87
7382 | 8.2 | 0.83
7383 | 7.8 | 0.89
7384 | 7.8 | 0.93
7385 | 8.7 | 0.89
7386 | 9 | 0.89
7387 | 8.9 | 0.88
7388 | 8.9 | 0.85
7389 | 8.6 | 0.88
7390 | 8.2 | 0.89
7391 | 8.4 | 0.85
7392 | 8.1 | 0.87
7393 | 8.4 | 0.86
7394 | 8.5 | 0.86
7395 | 8.8 | 0.82
7396 | 8.9 | 0.84
7397 | 8.7 | 0.84
7398 | 8.6 | 0.82
7399 | 8.2 | 0.83
7400 | 7.8 | 0.83
7401 | 7.3 | 0.88
7402 | 8.1 | 0.87
7403 | 9.3 | 0.83
7404 | 9.8 | 0.8
7405 | 9.9 | 0.81
7406 | 11 | 0.73
7407 | 10.7 | 0.71
7408 | 10.5 | 0.68
7409 | 10.1 | 0.7
7410 | 9 | 0.75
7411 | 8.1 | 0.76
7412 | 7.2 | 0.77
7413 | 6.4 | 0.81
7414 | 6.5 | 0.87
7415 | 6.8 | 0.88
7416 | 6.6 | 0.9
7417 | 6.9 | 0.85
7418 | 6.6 | 0.84
7419 | 6.7 | 0.82
7420 | 6.3 | 0.88
7421 | 6.3 | 0.86
7422 | 6 | 0.89
7423 | 5.8 | 0.92
7424 | 5.8 | 0.95
7425 | 5.7 | 0.95
7426 | 6 | 0.95
7427 | 6.7 | 0.97
7428 | 7.5 | 0.96
7429 | 8.2 | 0.97
7430 | 8.5 | 0.99
7431 | 8.2 | 0.97
7432 | 8.4 | 0.79
7433 | 7.6 | 0.82
7434 | 6.6 | 0.87
7435 | 6 | 0.83
7436 | 5.5 | 0.81
7437 | 4.9 | 0.84
7438 | 4.7 | 0.84
7439 | 4.7 | 0.85
7440 | 2.7 | 0.91
7441 | 3.6 | 0.86
7442 | 2.6 | 0.89
7443 | 2.8 | 0.89
7444 | 3.7 | 0.88
7445 | 3.8 | 0.9
7446 | 3.6 | 0.91
7447 | 3.9 | 0.93
7448 | 4.3 | 0.93
7449 | 4.4 | 0.95
7450 | 4.3 | 0.95
7451 | 5.2 | 0.89
7452 | 5.5 | 0.87
7453 | 5 | 0.92
7454 | 5.9 | 0.88
7455 | 6.4 | 0.84
7456 | 6.4 | 0.79
7457 | 6.6 | 0.76
7458 | 6.5 | 0.78
7459 | 6.2 | 0.8
7460 | 6.4 | 0.81
7461 | 6.4 | 0.84
7462 | 6.3 | 0.85
7463 | 6.4 | 0.85
7464 | 6.3 | 0.86
7465 | 6 | 0.88
7466 | 5.3 | 0.91
7467 | 4.6 | 0.93
7468 | 4.2 | 0.93
7469 | 3.8 | 0.95
7470 | 3.5 | 0.97
7471 | 3.3 | 0.95
7472 | 3.2 | 0.95
7473 | 2.7 | 0.96
7474 | 3.6 | 0.93
7475 | 4.5 | 0.92
7476 | 5.9 | 0.83
7477 | 7.1 | 0.78
7478 | 8.9 | 0.69
7479 | 9.5 | 0.63
7480 | 9.8 | 0.64
7481 | 8 | 0.75
7482 | 5.6 | 0.86
7483 | 5 | 0.9
7484 | 5.1 | 0.9
7485 | 6 | 0.92
7486 | 5.8 | 0.94
7487 | 6.4 | 0.92
7488 | 6.8 | 0.93
7489 | 7.3 | 0.93
7490 | 7.7 | 0.94
7491 | 8.1 | 0.99
7492 | 8.1 | 0.92
7493 | 7.6 | 0.93
7494 | 6.6 | 0.81
7495 | 5.8 | 0.79
7496 | 5.1 | 0.9
7497 | 4.9 | 0.92
7498 | 4.4 | 0.9
7499 | 5.7 | 0.88
7500 | 7.6 | 0.77
7501 | 7.7 | 0.75
7502 | 8.1 | 0.72
7503 | 8.9 | 0.68
7504 | 8.2 | 0.7
7505 | 7.6 | 0.73
7506 | 7.2 | 0.77
7507 | 6.5 | 0.81
7508 | 5.9 | 0.88
7509 | 5.8 | 0.88
7510 | 5.8 | 0.85
7511 | 5.7 | 0.85
7512 | 5.5 | 0.83
7513 | 5.8 | 0.85
7514 | 5.2 | 0.87
7515 | 5.3 | 0.86
7516 | 4.8 | 0.87
7517 | 4.5 | 0.89
7518 | 3.7 | 0.9
7519 | 3.2 | 0.91
7520 | 3.1 | 0.93
7521 | 2.5 | 0.95
7522 | 3.4 | 0.91
7523 | 4.8 | 0.84
7524 | 6.4 | 0.78
7525 | 6.1 | 0.85
7526 | 6.3 | 0.91
7527 | 6.4 | 0.88
7528 | 6.8 | 0.82
7529 | 7.1 | 0.83
7530 | 7.1 | 0.88
7531 | 7.4 | 0.88
7532 | 7.1 | 0.94
7533 | 7.8 | 0.97
7534 | 8.3 | 1
7535 | 7.5 | 0.81
7536 | 6.9 | 0.77
7537 | 6.4 | 0.7
7538 | 5.8 | 0.71
7539 | 4.8 | 0.78
7540 | 4.6 | 0.82
7541 | 4.1 | 0.83
7542 | 4.7 | 0.79
7543 | 4.1 | 0.85
7544 | 4.5 | 0.82
7545 | 4.7 | 0.81
7546 | 4.9 | 0.84
7547 | 6.4 | 0.75
7548 | 5.5 | 0.83
7549 | 5.6 | 0.84
7550 | 6.5 | 0.84
7551 | 6.6 | 0.81
7552 | 6 | 0.86
7553 | 5.4 | 0.8
7554 | 5.1 | 0.83
7555 | 4.8 | 0.84
7556 | 4.6 | 0.82
7557 | 4.2 | 0.85
7558 | 4.9 | 0.81
7559 | 3.3 | 0.9
7560 | 3.9 | 0.85
7561 | 3.8 | 0.85
7562 | 3.8 | 0.83
7563 | 3.5 | 0.88
7564 | 3.6 | 0.85
7565 | 3.4 | 0.86
7566 | 3.6 | 0.83
7567 | 3.8 | 0.82
7568 | 3.5 | 0.83
7569 | 3.6 | 0.85
7570 | 4.3 | 0.8
7571 | 5.4 | 0.78
7572 | 6.6 | 0.75
7573 | 7.2 | 0.7
7574 | 7.7 | 0.64
7575 | 8.2 | 0.67
7576 | 7.7 | 0.71
7577 | 6.2 | 0.76
7578 | 5.4 | 0.8
7579 | 5.2 | 0.8
7580 | 4.9 | 0.81
7581 | 4.4 | 0.82
7582 | 5 | 0.79
7583 | 4.4 | 0.84
7584 | 4.2 | 0.84
7585 | 3.6 | 0.85
7586 | 4 | 0.85
7587 | 4.4 | 0.82
7588 | 4.1 | 0.83
7589 | 4.1 | 0.87
7590 | 3.7 | 0.9
7591 | 4.1 | 0.9
7592 | 3.7 | 0.92
7593 | 4.5 | 0.93
7594 | 5.3 | 0.94
7595 | 5.6 | 0.92
7596 | 3.1 | 0.95
7597 | 3.2 | 0.93
7598 | 5.3 | 0.81
7599 | 5.4 | 0.83
7600 | 3.1 | 0.88
7601 | 2.9 | 0.91
7602 | 2.9 | 0.91
7603 | 3.2 | 0.9
7604 | 3.5 | 0.9
7605 | 3.5 | 0.88
7606 | 3.2 | 0.9
7607 | 3.1 | 0.93
7608 | 2.5 | 0.95
7609 | 2.3 | 0.95
7610 | 1.8 | 0.94
7611 | 2.2 | 0.95
7612 | 4.5 | 0.89
7613 | 5.4 | 0.81
7614 | 4.8 | 0.82
7615 | 4 | 0.85
7616 | 3.7 | 0.85
7617 | 3.8 | 0.83
7618 | 3.8 | 0.82
7619 | 4.2 | 0.79
7620 | 4.9 | 0.75
7621 | 5.3 | 0.72
7622 | 5.7 | 0.67
7623 | 6 | 0.63
7624 | 6 | 0.61
7625 | 5.6 | 0.65
7626 | 4.8 | 0.7
7627 | 4.5 | 0.74
7628 | 4 | 0.75
7629 | 3.2 | 0.81
7630 | 2.8 | 0.82
7631 | 2.3 | 0.86
7632 | 2 | 0.85
7633 | 1.9 | 0.87
7634 | 1.8 | 0.87
7635 | 1.4 | 0.89
7636 | 1.4 | 0.89
7637 | 1.6 | 0.87
7638 | 1.6 | 0.85
7639 | 1.2 | 0.89
7640 | 1.4 | 0.87
7641 | 1.2 | 0.89
7642 | 2 | 0.85
7643 | 2.8 | 0.84
7644 | 3.9 | 0.8
7645 | 5 | 0.73
7646 | 6.1 | 0.67
7647 | 6.7 | 0.67
7648 | 6.6 | 0.66
7649 | 6.2 | 0.7
7650 | 5.2 | 0.76
7651 | 4.4 | 0.79
7652 | 4 | 0.78
7653 | 4.2 | 0.75
7654 | 3.5 | 0.78
7655 | 2.9 | 0.81
7656 | 2.6 | 0.82
7657 | 1.9 | 0.87
7658 | 1.8 | 0.89
7659 | 2.1 | 0.89
7660 | 2.1 | 0.89
7661 | 2 | 0.89
7662 | 1.7 | 0.91
7663 | 1.4 | 0.92
7664 | 1.4 | 0.92
7665 | 1.6 | 0.91
7666 | 1.7 | 0.93
7667 | 2.6 | 0.89
7668 | 3.9 | 0.85
7669 | 4.5 | 0.82
7670 | 5.1 | 0.83
7671 | 5.2 | 0.84
7672 | 5.3 | 0.84
7673 | 5.3 | 0.83
7674 | 5.3 | 0.64
7675 | 4.8 | 0.65
7676 | 5 | 0.69
7677 | 5 | 0.72
7678 | 4.2 | 0.87
7679 | 3.7 | 0.88
7680 | 3.4 | 0.81
7681 | 3.6 | 0.8
7682 | 3.5 | 0.8
7683 | 3.1 | 0.9
7684 | 3 | 0.89
7685 | 3.5 | 0.86
7686 | 3.3 | 0.86
7687 | 3.7 | 0.85
7688 | 3.9 | 0.92
7689 | 4.6 | 0.93
7690 | 5.1 | 0.95
7691 | 5.8 | 0.89
7692 | 6.4 | 0.86
7693 | 6.8 | 0.82
7694 | 5.9 | 0.83
7695 | 6.7 | 0.75
7696 | 6.6 | 0.78
7697 | 6.2 | 0.83
7698 | 6.3 | 0.8
7699 | 6.4 | 0.79
7700 | 6.3 | 0.79
7701 | 6 | 0.79
7702 | 5.8 | 0.77
7703 | 4.8 | 0.81
7704 | 3.3 | 0.88
7705 | 2.6 | 0.91
7706 | 2.7 | 0.89
7707 | 1.9 | 0.93
7708 | 1.8 | 0.93
7709 | 1.8 | 0.91
7710 | 1.6 | 0.93
7711 | 1.7 | 0.93
7712 | 1.2 | 0.92
7713 | 1.3 | 0.92
7714 | 3.5 | 0.85
7715 | 6.1 | 0.76
7716 | 6.1 | 0.85
7717 | 6.3 | 0.89
7718 | 6.3 | 0.91
7719 | 7.1 | 0.9
7720 | 7.4 | 0.9
7721 | 7 | 0.91
7722 | 7 | 0.93
7723 | 7.4 | 0.86
7724 | 7.6 | 0.87
7725 | 8 | 0.86
7726 | 8.1 | 0.81
7727 | 8 | 0.83
7728 | 8.3 | 0.81
7729 | 8.6 | 0.8
7730 | 8.6 | 0.78
7731 | 8.6 | 0.78
7732 | 8.9 | 0.86
7733 | 8.6 | 0.93
7734 | 8.7 | 0.93
7735 | 8.9 | 0.96
7736 | 8.2 | 0.99
7737 | 6.8 | 0.97
7738 | 5.4 | 0.95
7739 | 6.8 | 0.88
7740 | 8.8 | 0.81
7741 | 9.4 | 0.79
7742 | 9.4 | 0.78
7743 | 9.5 | 0.75
7744 | 9 | 0.8
7745 | 8.1 | 0.85
7746 | 7.3 | 0.9
7747 | 6.9 | 0.91
7748 | 7.4 | 0.88
7749 | 7 | 0.88
7750 | 6.8 | 0.91
7751 | 7.9 | 0.89
7752 | 7.9 | 0.89
7753 | 7.8 | 0.89
7754 | 7.7 | 0.89
7755 | 8 | 0.89
7756 | 8.2 | 0.9
7757 | 8.1 | 0.93
7758 | 8.5 | 0.9
7759 | 7.6 | 0.93
7760 | 8.3 | 0.96
7761 | 9 | 0.95
7762 | 7.1 | 0.97
7763 | 7.3 | 0.99
7764 | 7.7 | 0.96
7765 | 7.8 | 0.96
7766 | 7.5 | 0.97
7767 | 7.9 | 0.96
7768 | 7.6 | 0.99
7769 | 8.5 | 0.97
7770 | 7 | 0.99
7771 | 7.4 | 0.97
7772 | 7.4 | 0.97
7773 | 7.9 | 0.99
7774 | 8.4 | 0.99
7775 | 8.1 | 0.96
7776 | 7.9 | 0.96
7777 | 6.9 | 0.96
7778 | 6.8 | 0.99
7779 | 6.7 | 0.97
7780 | 7.1 | 0.97
7781 | 7 | 0.94
7782 | 7 | 0.94
7783 | 6.9 | 0.94
7784 | 6.8 | 0.96
7785 | 7.6 | 0.93
7786 | 7.9 | 0.91
7787 | 7.3 | 0.96
7788 | 7.6 | 0.96
7789 | 7.9 | 0.96
7790 | 7.7 | 0.96
7791 | 8.1 | 0.94
7792 | 7.8 | 0.91
7793 | 7.8 | 0.96
7794 | 7.5 | 0.97
7795 | 7.3 | 0.97
7796 | 6.9 | 0.93
7797 | 6.4 | 0.94
7798 | 6.2 | 0.95
7799 | 6.3 | 0.95
7800 | 6.4 | 0.95
7801 | 5.1 | 0.92
7802 | 6.1 | 0.97
7803 | 5.6 | 0.97
7804 | 5.5 | 0.97
7805 | 5.5 | 0.98
7806 | 5.3 | 0.98
7807 | 5 | 0.98
7808 | 4.3 | 0.98
7809 | 4 | 0.98
7810 | 4.3 | 0.98
7811 | 4.4 | 0.97
7812 | 4.6 | 0.97
7813 | 5.3 | 0.98
7814 | 6.4 | 0.95
7815 | 7.5 | 0.84
7816 | 6.9 | 0.84
7817 | 6.9 | 0.9
7818 | 6.3 | 0.92
7819 | 5.8 | 0.94
7820 | 5.8 | 0.94
7821 | 5.4 | 0.94
7822 | 5.4 | 0.95
7823 | 5.5 | 0.95
7824 | 5.4 | 0.95
7825 | 4.4 | 0.93
7826 | 4.1 | 0.97
7827 | 3.9 | 0.97
7828 | 4 | 0.97
7829 | 4 | 0.97
7830 | 4.1 | 0.97
7831 | 4.5 | 0.97
7832 | 4.6 | 0.93
7833 | 4.7 | 0.95
7834 | 5.1 | 0.94
7835 | 5.5 | 0.94
7836 | 6.1 | 0.95
7837 | 6.9 | 0.94
7838 | 7.1 | 0.94
7839 | 7.2 | 0.93
7840 | 7.4 | 0.93
7841 | 7.5 | 0.93
7842 | 7.4 | 0.93
7843 | 7.4 | 0.93
7844 | 7.2 | 0.93
7845 | 7.1 | 0.93
7846 | 6.9 | 0.93
7847 | 6.7 | 0.91
7848 | 6.1 | 0.92
7849 | 6 | 0.94
7850 | 6.2 | 0.91
7851 | 5.8 | 0.92
7852 | 5.6 | 0.92
7853 | 4.5 | 0.93
7854 | 4.2 | 0.97
7855 | 4.8 | 0.95
7856 | 5.5 | 0.95
7857 | 5.9 | 0.95
7858 | 6.4 | 0.94
7859 | 6.7 | 0.96
7860 | 7.9 | 0.93
7861 | 8.6 | 0.93
7862 | 8.4 | 0.96
7863 | 8.1 | 0.93
7864 | 8.3 | 0.96
7865 | 8.3 | 0.94
7866 | 8.3 | 0.96
7867 | 8.8 | 0.96
7868 | 9.1 | 0.97
7869 | 9.6 | 0.99
7870 | 9.9 | 0.99
7871 | 10.1 | 1
7872 | 10.3 | 1
7873 | 10.4 | 1
7874 | 10.3 | 0.99
7875 | 10.3 | 1
7876 | 10.1 | 0.99
7877 | 10.1 | 0.99
7878 | 10.1 | 0.99
7879 | 10.1 | 0.99
7880 | 10.1 | 1
7881 | 10 | 1
7882 | 10 | 0.99
7883 | 10.2 | 0.99
7884 | 10.2 | 0.99
7885 | 10.4 | 0.99
7886 | 10.7 | 0.95
7887 | 10.9 | 0.91
7888 | 10.3 | 0.88
7889 | 9.3 | 0.91
7890 | 8.4 | 0.96
7891 | 8.4 | 0.97
7892 | 7 | 0.97
7893 | 7.2 | 0.97
7894 | 7.9 | 0.97
7895 | 7.4 | 0.96
7896 | 7.7 | 0.96
7897 | 8.7 | 0.97
7898 | 8.8 | 0.97
7899 | 8.9 | 0.97
7900 | 8.6 | 0.97
7901 | 8.3 | 0.97
7902 | 8.3 | 0.97
7903 | 8.9 | 0.97
7904 | 10.3 | 0.99
7905 | 10.6 | 0.99
7906 | 10.4 | 0.99
7907 | 10.1 | 0.99
7908 | 9.8 | 0.96
7909 | 9.6 | 0.91
7910 | 9.5 | 0.91
7911 | 9.3 | 0.89
7912 | 8.6 | 0.94
7913 | 8.4 | 0.94
7914 | 8.1 | 0.96
7915 | 8.1 | 0.97
7916 | 8.3 | 0.99
7917 | 8.4 | 0.99
7918 | 8.5 | 0.99
7919 | 8.8 | 1
7920 | 8.9 | 0.99
7921 | 8.9 | 0.99
7922 | 8.9 | 0.99
7923 | 8.4 | 0.99
7924 | 8.1 | 1
7925 | 7.6 | 0.99
7926 | 7.2 | 0.99
7927 | 7 | 0.97
7928 | 6.9 | 0.99
7929 | 6.9 | 0.97
7930 | 7.1 | 0.93
7931 | 7.5 | 0.91
7932 | 7.9 | 0.83
7933 | 7.6 | 0.87
7934 | 8.1 | 0.87
7935 | 8 | 0.87
7936 | 8.1 | 0.89
7937 | 8.1 | 0.89
7938 | 7.7 | 0.9
7939 | 7.3 | 0.93
7940 | 6.9 | 0.94
7941 | 6.6 | 0.94
7942 | 6.1 | 0.94
7943 | 6.3 | 0.91
7944 | 6.6 | 0.95
7945 | 7 | 0.96
7946 | 7.1 | 0.97
7947 | 7.3 | 0.99
7948 | 7.6 | 0.99
7949 | 7.6 | 0.97
7950 | 7.6 | 0.96
7951 | 7.5 | 0.94
7952 | 7.6 | 0.93
7953 | 7.4 | 0.94
7954 | 7.9 | 0.91
7955 | 8.2 | 0.92
7956 | 8.6 | 0.9
7957 | 9.1 | 0.88
7958 | 9.2 | 0.91
7959 | 9.4 | 0.88
7960 | 9.4 | 0.83
7961 | 8.4 | 0.9
7962 | 8 | 0.92
7963 | 8 | 0.9
7964 | 7.9 | 0.91
7965 | 7.3 | 0.94
7966 | 6.8 | 0.97
7967 | 7.1 | 0.96
7968 | 7.2 | 0.96
7969 | 7.1 | 0.94
7970 | 7.2 | 0.94
7971 | 7 | 0.94
7972 | 7 | 0.91
7973 | 6.9 | 0.91
7974 | 6.8 | 0.91
7975 | 6.7 | 0.9
7976 | 6.7 | 0.88
7977 | 6.5 | 0.87
7978 | 6.2 | 0.83
7979 | 6.4 | 0.84
7980 | 7 | 0.85
7981 | 7.5 | 0.86
7982 | 7.4 | 0.87
7983 | 7.5 | 0.87
7984 | 7.9 | 0.84
7985 | 7.7 | 0.86
7986 | 7.6 | 0.87
7987 | 7.8 | 0.83
7988 | 7.8 | 0.79
7989 | 7.8 | 0.8
7990 | 8 | 0.86
7991 | 8 | 0.79
7992 | 7.9 | 0.82
7993 | 7.7 | 0.9
7994 | 8.2 | 0.86
7995 | 9 | 0.89
7996 | 8.8 | 0.88
7997 | 8.9 | 0.89
7998 | 9.2 | 0.89
7999 | 9.4 | 0.89
8000 | 9.5 | 0.91
8001 | 9.3 | 0.92
8002 | 9.4 | 0.89
8003 | 9.2 | 0.89
8004 | 9.2 | 0.89
8005 | 9.1 | 0.89
8006 | 8.9 | 0.89
8007 | 8.7 | 0.9
8008 | 8.8 | 0.89
8009 | 8.4 | 0.89
8010 | 8.3 | 0.87
8011 | 8 | 0.87
8012 | 7.7 | 0.89
8013 | 7.4 | 0.88
8014 | 7.4 | 0.87
8015 | 7.2 | 0.85
8016 | 7.1 | 0.84
8017 | 7 | 0.82
8018 | 6.5 | 0.87
8019 | 5.4 | 0.89
8020 | 4.3 | 0.92
8021 | 4.6 | 0.9
8022 | 4.9 | 0.89
8023 | 3.9 | 0.92
8024 | 2.9 | 0.95
8025 | 2.2 | 0.96
8026 | 2 | 0.96
8027 | 3.3 | 0.86
8028 | 4.4 | 0.82
8029 | 5 | 0.81
8030 | 5.6 | 0.75
8031 | 6.1 | 0.76
8032 | 5.6 | 0.8
8033 | 5.2 | 0.83
8034 | 4.2 | 0.85
8035 | 3.2 | 0.86
8036 | 2.7 | 0.89
8037 | 2.4 | 0.86
8038 | 2.5 | 0.84
8039 | 2.2 | 0.87
8040 | 2.2 | 0.87
8041 | 1.8 | 0.93
8042 | 1.4 | 0.94
8043 | 1.2 | 0.94
8044 | 0.9 | 0.94
8045 | 0.8 | 0.94
8046 | 0.8 | 0.92
8047 | 0.8 | 0.94
8048 | 0.8 | 0.92
8049 | 1 | 0.9
8050 | 2.1 | 0.85
8051 | 2.6 | 0.84
8052 | 4.4 | 0.77
8053 | 4.8 | 0.71
8054 | 6.2 | 0.72
8055 | 6.2 | 0.69
8056 | 6.8 | 0.71
8057 | 5 | 0.83
8058 | 4 | 0.87
8059 | 3.7 | 0.9
8060 | 2.1 | 0.91
8061 | 3.3 | 0.91
8062 | 2.7 | 0.91
8063 | 3.4 | 0.88
8064 | 4.4 | 0.87
8065 | 3 | 0.91
8066 | 2.4 | 0.91
8067 | 2.8 | 0.91
8068 | 3.2 | 0.91
8069 | 4 | 0.92
8070 | 4.1 | 0.92
8071 | 4.5 | 0.9
8072 | 5 | 0.89
8073 | 5.1 | 0.9
8074 | 5.4 | 0.89
8075 | 6.5 | 0.85
8076 | 7.1 | 0.83
8077 | 7.4 | 0.81
8078 | 7.6 | 0.79
8079 | 7.7 | 0.79
8080 | 7.7 | 0.8
8081 | 7.2 | 0.81
8082 | 6.9 | 0.82
8083 | 7.5 | 0.8
8084 | 7.7 | 0.76
8085 | 7.7 | 0.79
8086 | 7.7 | 0.8
8087 | 7.9 | 0.8
8088 | 8 | 0.8
8089 | 8.3 | 0.81
8090 | 8.3 | 0.79
8091 | 8.3 | 0.78
8092 | 8.4 | 0.82
8093 | 8.3 | 0.82
8094 | 8.3 | 0.82
8095 | 7.8 | 0.87
8096 | 8.2 | 0.85
8097 | 7.6 | 0.94
8098 | 7.8 | 0.97
8099 | 8.1 | 0.97
8100 | 8.6 | 0.99
8101 | 8.9 | 0.96
8102 | 9.2 | 0.8
8103 | 10.2 | 0.76
8104 | 9.7 | 0.77
8105 | 8.7 | 0.78
8106 | 7.5 | 0.73
8107 | 6.5 | 0.76
8108 | 5.7 | 0.82
8109 | 4.5 | 0.85
8110 | 3.4 | 0.91
8111 | 3.6 | 0.91
8112 | 3.6 | 0.93
8113 | 3.3 | 0.97
8114 | 5.1 | 0.92
8115 | 4.5 | 0.95
8116 | 4.3 | 0.93
8117 | 5.5 | 0.92
8118 | 5.5 | 0.91
8119 | 6.8 | 0.9
8120 | 7.5 | 0.9
8121 | 8.1 | 0.9
8122 | 8.2 | 0.93
8123 | 8.3 | 0.97
8124 | 8.9 | 0.97
8125 | 9.3 | 0.97
8126 | 9.9 | 0.97
8127 | 10.5 | 0.97
8128 | 10.7 | 0.97
8129 | 10.9 | 0.95
8130 | 10.8 | 0.94
8131 | 10.8 | 0.94
8132 | 10.8 | 0.95
8133 | 10.9 | 0.95
8134 | 11.1 | 0.96
8135 | 11.1 | 0.96
8136 | 11.1 | 0.97
8137 | 10.9 | 0.97
8138 | 11 | 0.97
8139 | 11.1 | 0.96
8140 | 11.1 | 0.97
8141 | 11.1 | 0.92
8142 | 10.4 | 0.95
8143 | 9.8 | 0.83
8144 | 9.9 | 0.92
8145 | 10 | 0.95
8146 | 9.9 | 0.87
8147 | 9.5 | 0.89
8148 | 10.6 | 0.74
8149 | 10 | 0.74
8150 | 10.1 | 0.73
8151 | 9.5 | 0.82
8152 | 10.1 | 0.73
8153 | 9.4 | 0.75
8154 | 9.1 | 0.73
8155 | 8.5 | 0.82
8156 | 7.3 | 0.84
8157 | 6.8 | 0.85
8158 | 6.2 | 0.86
8159 | 5.3 | 0.91
8160 | 5.3 | 0.92
8161 | 6.1 | 0.91
8162 | 6 | 0.92
8163 | 5.9 | 0.94
8164 | 6.5 | 0.92
8165 | 6.8 | 0.94
8166 | 4.9 | 0.98
8167 | 7 | 0.97
8168 | 6.7 | 0.96
8169 | 8 | 0.97
8170 | 8.1 | 0.99
8171 | 8.6 | 0.97
8172 | 8.9 | 0.96
8173 | 9.5 | 0.97
8174 | 9.4 | 0.99
8175 | 9.2 | 0.96
8176 | 9.2 | 0.96
8177 | 9.2 | 0.99
8178 | 9.3 | 0.95
8179 | 9.6 | 0.99
8180 | 10.3 | 0.99
8181 | 11.2 | 0.97
8182 | 11.7 | 0.98
8183 | 12.2 | 0.95
8184 | 11 | 0.75
8185 | 9.4 | 0.76
8186 | 8.9 | 0.72
8187 | 8.6 | 0.72
8188 | 7.9 | 0.72
8189 | 7.2 | 0.77
8190 | 6.4 | 0.85
8191 | 5.5 | 0.83
8192 | 6.1 | 0.77
8193 | 6.4 | 0.73
8194 | 5.8 | 0.8
8195 | 5.2 | 0.81
8196 | 6.3 | 0.76
8197 | 7.6 | 0.66
8198 | 7.1 | 0.68
8199 | 5.6 | 0.78
8200 | 6.4 | 0.79
8201 | 5.8 | 0.85
8202 | 6.2 | 0.85
8203 | 6.7 | 0.9
8204 | 6.7 | 0.82
8205 | 7.2 | 0.74
8206 | 7.6 | 0.76
8207 | 8.1 | 0.72
8208 | 7.8 | 0.73
8209 | 8.2 | 0.71
8210 | 8.3 | 0.67
8211 | 8 | 0.71
8212 | 8.1 | 0.7
8213 | 7.8 | 0.71
8214 | 7.2 | 0.74
8215 | 7.1 | 0.74
8216 | 7 | 0.75
8217 | 7.1 | 0.74
8218 | 7.3 | 0.74
8219 | 7 | 0.8
8220 | 7.8 | 0.75
8221 | 8.5 | 0.71
8222 | 9.1 | 0.71
8223 | 9.5 | 0.7
8224 | 8.8 | 0.73
8225 | 6.2 | 0.83
8226 | 4.4 | 0.89
8227 | 5.4 | 0.89
8228 | 5 | 0.95
8229 | 6.2 | 0.95
8230 | 7.1 | 0.93
8231 | 8.2 | 0.89
8232 | 8.5 | 0.89
8233 | 8.7 | 0.89
8234 | 8.6 | 0.96
8235 | 9 | 0.97
8236 | 9.6 | 0.99
8237 | 10.2 | 0.99
8238 | 10.8 | 1
8239 | 11.1 | 1
8240 | 11.6 | 0.99
8241 | 11.4 | 0.99
8242 | 11.4 | 1
8243 | 11.7 | 1
8244 | 11.8 | 0.98
8245 | 11.7 | 0.98
8246 | 7.8 | 0.86
8247 | 7.3 | 0.81
8248 | 6.5 | 0.84
8249 | 6.1 | 0.77
8250 | 5.2 | 0.76
8251 | 4.4 | 0.77
8252 | 4.3 | 0.82
8253 | 4.5 | 0.81
8254 | 3.4 | 0.86
8255 | 3 | 0.88
8256 | 3.2 | 0.91
8257 | 3.4 | 0.88
8258 | 3.6 | 0.85
8259 | 3.5 | 0.9
8260 | 2.9 | 0.91
8261 | 3.3 | 0.9
8262 | 2.9 | 0.91
8263 | 3 | 0.88
8264 | 2.3 | 0.93
8265 | 2.4 | 0.93
8266 | 2.2 | 0.87
8267 | 2.7 | 0.86
8268 | 3.4 | 0.83
8269 | 3.9 | 0.8
8270 | 4.5 | 0.81
8271 | 5.4 | 0.72
8272 | 4.9 | 0.76
8273 | 2.8 | 0.84
8274 | 2 | 0.87
8275 | 1.4 | 0.89
8276 | 1.7 | 0.87
8277 | 2 | 0.87
8278 | 2.5 | 0.89
8279 | 3.9 | 0.9
8280 | 4.5 | 0.97
8281 | 6.1 | 0.97
8282 | 7 | 0.97
8283 | 7.3 | 0.99
8284 | 7.2 | 0.99
8285 | 8.3 | 0.99
8286 | 8.7 | 0.99
8287 | 8.5 | 0.94
8288 | 8.1 | 0.96
8289 | 7.1 | 0.9
8290 | 7.2 | 0.94
8291 | 8 | 0.87
8292 | 8.4 | 0.88
8293 | 9.1 | 0.8
8294 | 9.4 | 0.78
8295 | 8.5 | 0.86
8296 | 8.3 | 0.92
8297 | 8.1 | 0.94
8298 | 8.2 | 0.87
8299 | 7.2 | 0.81
8300 | 6.9 | 0.82
8301 | 6.3 | 0.75
8302 | 5.9 | 0.73
8303 | 4.9 | 0.81
8304 | 5.4 | 0.69
8305 | 4.3 | 0.79
8306 | 4.3 | 0.76
8307 | 4.2 | 0.77
8308 | 4 | 0.78
8309 | 3.6 | 0.81
8310 | 3.5 | 0.83
8311 | 3.5 | 0.8
8312 | 4.1 | 0.74
8313 | 4 | 0.74
8314 | 4.3 | 0.74
8315 | 4.5 | 0.76
8316 | 6.3 | 0.67
8317 | 6.3 | 0.72
8318 | 7.2 | 0.7
8319 | 6.9 | 0.75
8320 | 5.6 | 0.89
8321 | 5.2 | 0.95
8322 | 5.1 | 0.97
8323 | 4.7 | 0.97
8324 | 4.2 | 0.93
8325 | 4.9 | 0.92
8326 | 4.7 | 0.89
8327 | 4.8 | 0.87
8328 | 3.9 | 0.85
8329 | 4.3 | 0.74
8330 | 4.6 | 0.71
8331 | 3.8 | 0.77
8332 | 4.4 | 0.72
8333 | 3.3 | 0.83
8334 | 3.5 | 0.88
8335 | 3.3 | 0.78
8336 | 1.7 | 0.85
8337 | 2.5 | 0.72
8338 | 2.7 | 0.75
8339 | 3.5 | 0.71
8340 | 5.2 | 0.66
8341 | 5.5 | 0.68
8342 | 5.1 | 0.55
8343 | 2 | 0.89
8344 | 1.2 | 0.98
8345 | 0.6 | 0.98
8346 | 0.6 | 0.96
8347 | 1.4 | 0.98
8348 | 2.3 | 0.95
8349 | 1.2 | 0.94
8350 | 1.8 | 0.93
8351 | 2.1 | 0.91
8352 | 2.4 | 0.82
8353 | 2.3 | 0.8
8354 | 2.4 | 0.82
8355 | 1.9 | 0.82
8356 | 2.6 | 0.72
8357 | 2.5 | 0.72
8358 | 1.7 | 0.8
8359 | 1.4 | 0.91
8360 | 1.3 | 0.92
8361 | 2.3 | 0.89
8362 | 2.5 | 0.91
8363 | 3.1 | 0.93
8364 | 3.7 | 0.9
8365 | 2.9 | 0.91
8366 | 3.6 | 0.86
8367 | 3.9 | 0.87
8368 | 5.1 | 0.89
8369 | 5.4 | 0.86
8370 | 5.4 | 0.71
8371 | 4.7 | 0.76
8372 | 5.1 | 0.79
8373 | 5.2 | 0.75
8374 | 4.8 | 0.78
8375 | 4.2 | 0.85
8376 | 3.8 | 0.88
8377 | 3.3 | 0.86
8378 | 2.9 | 0.84
8379 | 1.5 | 0.89
8380 | 2.3 | 0.89
8381 | 2.3 | 0.87
8382 | 2.4 | 0.86
8383 | 1.2 | 0.89
8384 | 2.7 | 0.91
8385 | 2.7 | 0.86
8386 | 2.1 | 0.89
8387 | 2.7 | 0.86
8388 | 3.9 | 0.8
8389 | 4.9 | 0.81
8390 | 5.1 | 0.75
8391 | 5.5 | 0.75
8392 | 5.3 | 0.74
8393 | 4.2 | 0.8
8394 | 3.3 | 0.85
8395 | 3.2 | 0.84
8396 | 2.6 | 0.88
8397 | 2.5 | 0.84
8398 | 2.2 | 0.86
8399 | 2.2 | 0.86
8400 | 1.7 | 0.87
8401 | 1.8 | 0.87
8402 | 1 | 0.88
8403 | 1.1 | 0.9
8404 | 1.8 | 0.89
8405 | 1.4 | 0.89
8406 | 2.1 | 0.84
8407 | 2.5 | 0.82
8408 | 1.1 | 0.89
8409 | 2.3 | 0.86
8410 | 2.8 | 0.86
8411 | 1.7 | 0.85
8412 | 4.3 | 0.82
8413 | 4.7 | 0.84
8414 | 5.9 | 0.79
8415 | 6.1 | 0.74
8416 | 6.2 | 0.79
8417 | 3 | 0.91
8418 | 3.1 | 0.91
8419 | 3.4 | 0.93
8420 | 3.6 | 0.91
8421 | 2.6 | 0.91
8422 | 2.8 | 0.86
8423 | 3.1 | 0.83
8424 | 3.8 | 0.82
8425 | 4.4 | 0.8
8426 | 5.4 | 0.81
8427 | 5.6 | 0.8
8428 | 6.4 | 0.84
8429 | 7.3 | 0.83
8430 | 7.9 | 0.84
8431 | 7.8 | 0.97
8432 | 8.6 | 0.99
8433 | 9.1 | 0.97
8434 | 9.2 | 0.99
8435 | 9.5 | 0.99
8436 | 9.6 | 0.99
8437 | 9.6 | 0.99
8438 | 9.6 | 0.99
8439 | 9.5 | 0.97
8440 | 9.6 | 0.99
8441 | 10.3 | 0.99
8442 | 11 | 0.95
8443 | 10.7 | 0.87
8444 | 8.7 | 0.94
8445 | 8.6 | 0.85
8446 | 8.3 | 0.92
8447 | 8.4 | 0.85
8448 | 8.3 | 0.87
8449 | 8.6 | 0.89
8450 | 8.6 | 0.92
8451 | 8.2 | 0.92
8452 | 8.6 | 0.94
8453 | 8.6 | 0.93
8454 | 8.7 | 0.96
8455 | 8.9 | 0.96
8456 | 8.6 | 0.93
8457 | 8.2 | 0.9
8458 | 8.4 | 0.94
8459 | 7.8 | 0.93
8460 | 8.8 | 0.96
8461 | 8.8 | 0.9
8462 | 8.1 | 0.94
8463 | 8.2 | 0.96
8464 | 8 | 0.97
8465 | 7.9 | 0.97
8466 | 7.6 | 0.99
8467 | 7.2 | 0.97
8468 | 6.4 | 0.95
8469 | 6.3 | 0.94
8470 | 6.1 | 0.97
8471 | 6.1 | 0.98
8472 | 6 | 0.98
8473 | 4.5 | 1
8474 | 4.6 | 0.97
8475 | 4.3 | 0.98
8476 | 2.9 | 0.98
8477 | 3.4 | 0.98
8478 | 1.7 | 0.98
8479 | 1.2 | 0.98
8480 | 0.9 | 0.98
8481 | 2.6 | 0.96
8482 | 2.6 | 1
8483 | 3.9 | 0.98
8484 | 6 | 0.98
8485 | 5.8 | 0.98
8486 | 6.1 | 0.97
8487 | 6.5 | 0.94
8488 | 6.1 | 0.95
8489 | 5.8 | 0.95
8490 | 4.6 | 0.97
8491 | 5.1 | 0.98
8492 | 4.6 | 0.97
8493 | 5.7 | 0.97
8494 | 5.5 | 0.95
8495 | 6.5 | 0.94
8496 | 5.7 | 0.95
8497 | 5.3 | 0.95
8498 | 4.1 | 0.97
8499 | 3.7 | 0.98
8500 | 4.4 | 0.97
8501 | 3.5 | 0.97
8502 | 3 | 0.95
8503 | 3.7 | 0.93
8504 | 2.9 | 0.95
8505 | 4.2 | 0.92
8506 | 2.7 | 0.95
8507 | 3.4 | 0.95
8508 | 3.8 | 0.97
8509 | 3.8 | 0.97
8510 | 4.7 | 0.98
8511 | 5.1 | 0.98
8512 | 5.6 | 0.98
8513 | 5.5 | 1
8514 | 4.8 | 0.97
8515 | 4.2 | 0.98
8516 | 4.4 | 0.98
8517 | 4.1 | 0.98
8518 | 3.8 | 0.98
8519 | 4.2 | 0.95
8520 | 4.5 | 0.9
8521 | 4.7 | 0.92
8522 | 4.4 | 0.92
8523 | 4.9 | 0.94
8524 | 4.3 | 0.93
8525 | 3.4 | 0.95
8526 | 4.2 | 0.93
8527 | 4.3 | 0.95
8528 | 4 | 0.95
8529 | 4 | 0.95
8530 | 4.4 | 0.93
8531 | 4.3 | 0.95
8532 | 6.8 | 0.9
8533 | 8 | 0.86
8534 | 8.1 | 0.81
8535 | 8.5 | 0.78
8536 | 7.5 | 0.86
8537 | 7.4 | 0.84
8538 | 6.4 | 0.86
8539 | 5.9 | 0.88
8540 | 6.6 | 0.9
8541 | 6.7 | 0.82
8542 | 6 | 0.88
8543 | 6.2 | 0.85
8544 | 5.9 | 0.86
8545 | 5.5 | 0.86
8546 | 5.7 | 0.86
8547 | 6.1 | 0.86
8548 | 5.2 | 0.89
8549 | 6 | 0.86
8550 | 5.1 | 0.87
8551 | 4.1 | 0.9
8552 | 5 | 0.86
8553 | 4.1 | 0.9
8554 | 4.5 | 0.89
8555 | 5.2 | 0.87
8556 | 5.6 | 0.91
8557 | 6.1 | 0.89
8558 | 6.5 | 0.91
8559 | 7.7 | 0.87
8560 | 7 | 0.91
8561 | 6.6 | 0.9
8562 | 6.3 | 0.91
8563 | 6.2 | 0.83
8564 | 5.1 | 0.89
8565 | 5.5 | 0.91
8566 | 5.8 | 0.98
8567 | 6.9 | 0.99
8568 | 6.9 | 0.99
8569 | 7.4 | 0.97
8570 | 8 | 0.94
8571 | 8.8 | 0.93
8572 | 8.4 | 0.9
8573 | 6.6 | 0.94
8574 | 6.8 | 0.94
8575 | 7.7 | 0.91
8576 | 7.6 | 0.87
8577 | 6.9 | 0.94
8578 | 7.1 | 0.94
8579 | 7.5 | 0.93
8580 | 8.5 | 0.86
8581 | 8.9 | 0.84
8582 | 9.1 | 0.84
8583 | 8.2 | 0.79
8584 | 7.3 | 0.8
8585 | 6.5 | 0.81
8586 | 6.3 | 0.8
8587 | 5.6 | 0.83
8588 | 4.9 | 0.87
8589 | 4.9 | 0.87
8590 | 5.3 | 0.83
8591 | 4.9 | 0.84
8592 | 4 | 0.87
8593 | 4 | 0.85
8594 | 3.8 | 0.85
8595 | 4.2 | 0.84
8596 | 4 | 0.85
8597 | 3 | 0.86
8598 | 2.7 | 0.89
8599 | 2.8 | 0.89
8600 | 1.9 | 0.93
8601 | 3.1 | 0.9
8602 | 2.9 | 0.89
8603 | 4 | 0.85
8604 | 4.7 | 0.92
8605 | 6.3 | 0.86
8606 | 6.9 | 0.84
8607 | 7.1 | 0.83
8608 | 7.3 | 0.81
8609 | 7.4 | 0.84
8610 | 7.4 | 0.81
8611 | 7.5 | 0.86
8612 | 7.8 | 0.87
8613 | 8 | 0.86
8614 | 8.1 | 0.89
8615 | 8.4 | 0.9
8616 | 8.7 | 0.92
8617 | 8.8 | 0.95
8618 | 8.9 | 0.95
8619 | 8.8 | 0.96
8620 | 8.9 | 0.97
8621 | 9.1 | 0.99
8622 | 8 | 0.96
8623 | 7.9 | 0.99
8624 | 8 | 0.97
8625 | 7.8 | 0.94
8626 | 8 | 0.96
8627 | 8.5 | 0.92
8628 | 9 | 0.88
8629 | 9.6 | 0.95
8630 | 10 | 0.96
8631 | 10.1 | 0.97
8632 | 10.6 | 0.99
8633 | 11.2 | 0.97
8634 | 11.3 | 0.95
8635 | 11.6 | 0.93
8636 | 11.4 | 0.95
8637 | 11.3 | 0.95
8638 | 11.3 | 0.96
8639 | 11.2 | 0.97
8640 | 11 | 0.97
8641 | 10.9 | 0.99
8642 | 10.9 | 0.99
8643 | 10.9 | 0.99
8644 | 10.6 | 0.99
8645 | 10.5 | 0.99
8646 | 10.3 | 0.99
8647 | 10.3 | 0.99
8648 | 10.2 | 0.99
8649 | 10.2 | 0.99
8650 | 10.2 | 0.99
8651 | 10.4 | 0.99
8652 | 10.4 | 1
8653 | 10.4 | 0.99
8654 | 10.3 | 0.99
8655 | 10.5 | 0.99
8656 | 10.4 | 0.99
8657 | 10.2 | 1
8658 | 10.1 | 1
8659 | 10 | 1
8660 | 9.7 | 0.97
8661 | 9.6 | 0.97
8662 | 9.4 | 0.96
8663 | 9.3 | 0.96
8664 | 9.1 | 0.96
8665 | 8.9 | 0.96
8666 | 9 | 0.92
8667 | 8.9 | 0.93
8668 | 8.9 | 0.93
8669 | 9 | 0.93
8670 | 9.1 | 0.93
8671 | 9.1 | 0.93
8672 | 9.2 | 0.92
8673 | 9.3 | 0.93
8674 | 9.4 | 0.91
8675 | 9.4 | 0.91
8676 | 9.8 | 0.91
8677 | 9.9 | 0.92
8678 | 9.9 | 0.91
8679 | 9.8 | 0.91
8680 | 9.8 | 0.93
8681 | 9.7 | 0.95
8682 | 9.6 | 0.93
8683 | 9.5 | 0.95
8684 | 9.4 | 0.96
8685 | 9.3 | 0.96
8686 | 9.4 | 0.97
8687 | 9.4 | 0.97
8688 | 9.4 | 0.99
8689 | 9.4 | 0.99
8690 | 9.3 | 0.96
8691 | 9.4 | 0.95
8692 | 9.4 | 0.95
8693 | 9.4 | 0.95
8694 | 9.4 | 0.95
8695 | 9.3 | 0.95
8696 | 9.4 | 0.96
8697 | 9.4 | 0.95
8698 | 9.4 | 0.95
8699 | 9.5 | 0.96
8700 | 9.5 | 0.95
8701 | 9.5 | 0.96
8702 | 9.8 | 0.95
8703 | 9.8 | 0.95
8704 | 9.5 | 0.96
8705 | 9.1 | 0.96
8706 | 8.8 | 0.97
8707 | 8.6 | 0.99
8708 | 8.5 | 0.97
8709 | 8.4 | 0.99
8710 | 8.4 | 0.99
8711 | 8.3 | 0.99
8712 | 8.3 | 0.99
8713 | 8.1 | 0.99
8714 | 8.2 | 0.99
8715 | 8.3 | 0.99
8716 | 8.4 | 0.99
8717 | 8.4 | 1
8718 | 8.6 | 0.99
8719 | 8.8 | 0.99
8720 | 9.1 | 0.97
8721 | 9.2 | 0.96
8722 | 9.3 | 0.97
8723 | 9.6 | 0.96
8724 | 9.8 | 0.96
8725 | 9.9 | 0.95
8726 | 9.8 | 0.96
8727 | 9.7 | 0.97
8728 | 9.7 | 0.97
8729 | 9.5 | 0.99
8730 | 9.3 | 0.99
8731 | 9.3 | 0.97
8732 | 9.2 | 1
8733 | 9.1 | 0.99
8734 | 9.1 | 0.99
8735 | 9.1 | 0.99
8736 | 8.9 | 1
8737 | 8.7 | 0.99
8738 | 8.5 | 0.99
8739 | 8.3 | 0.97
8740 | 8.2 | 0.97
8741 | 7.9 | 0.97
8742 | 8 | 0.96
8743 | 8.1 | 0.96
8744 | 8.1 | 0.96
8745 | 8.1 | 0.97
8746 | 7.9 | 0.96
8747 | 8 | 0.96
8748 | 7.9 | 0.91
8749 | 7.9 | 0.91
8750 | 8.2 | 0.89
8751 | 8.2 | 0.89
8752 | 8 | 0.89
8753 | 7.8 | 0.89
8754 | 7.6 | 0.9
8755 | 7.3 | 0.91
8756 | 6.7 | 0.94
8757 | 6.1 | 0.95
8758 | 6 | 0.95
8759 | 5.8 | 0.95
8760 | 5.8 | 0.97

## Run Shedule
Run Schedule Generator
Hour | -3 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00
Hour | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Typical Day 01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Typical Day 02 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Typical Day 03 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Typical Day 04 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Typical Day 05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Typical Day 06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Typical Day 07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Typical Day 08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Typical Day 09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Typical Day 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0
Day | Mon |  | Tue |  | Wed |  | Thu |  | Fri |  | Sat |  | Sun
Day num | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7
Typical Week 01 | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01
Typical Week 02 | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01
Typical Week 03 | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01
Typical Week 04 | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01
Typical Week 05 | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01
Typical Week 06 | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01
Typical Week 07 | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01
Typical Week 08 | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01
Typical Week 09 | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01
Typical Week 10 | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01 |  | Typical Day 01
Year | 2021
Week No. | Month |  | Week profile
1 | January |  | Typical Week 01
2 | January |  | Typical Week 01
3 | January |  | Typical Week 01
4 | January |  | Typical Week 01
5 | February |  | Typical Week 01
6 | February |  | Typical Week 01
7 | February |  | Typical Week 01
8 | February |  | Typical Week 01
9 | March |  | Typical Week 01
10 | March |  | Typical Week 01
11 | March |  | Typical Week 01
12 | March |  | Typical Week 01
13 | March |  | Typical Week 01
14 | April |  | Typical Week 01
15 | April |  | Typical Week 01
16 | April |  | Typical Week 03
17 | April |  | Typical Week 04
18 | May |  | Typical Week 05
19 | May |  | Typical Week 01
20 | May |  | Typical Week 02
21 | May |  | Typical Week 03
22 | May |  | Typical Week 04
23 | June |  | Typical Week 05
24 | June |  | Typical Week 01
25 | June |  | Typical Week 02
26 | June |  | Typical Week 03
27 | July |  | Typical Week 01
28 | July |  | Typical Week 01
29 | July |  | Typical Week 03
30 | July |  | Typical Week 04
31 | August |  | Typical Week 05
32 | August |  | Typical Week 01
33 | August |  | Typical Week 02
34 | August |  | Typical Week 03
35 | August |  | Typical Week 04
36 | September |  | Typical Week 05
37 | September |  | Typical Week 01
38 | September |  | Typical Week 02
39 | September |  | Typical Week 03
40 | October |  | Typical Week 01
41 | October |  | Typical Week 01
42 | October |  | Typical Week 01
43 | October |  | Typical Week 01
44 | November |  | Typical Week 01
45 | November |  | Typical Week 01
46 | November |  | Typical Week 01
47 | November |  | Typical Week 01
48 | November |  | Typical Week 01
49 | December |  | Typical Week 01
50 | December |  | Typical Week 01
51 | December |  | Typical Week 01
52 | December |  | Typical Week 01
53 | January |  | Typical Week 01

## Run Schedule Profile
Below is the run shedule expresssed as a 0 for periods where the unit does not run, a 1 where the unit is running at full capacity or a number between 0 and 1 which represent the % capacity. 0.5 would represent 50% setback i.e. 50% the maximum airflow
Hours
Date | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Week no | Day | Week profile name | Day profile name
2017-01-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | Typical Week 01 | Typical Day 01
2017-01-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Typical Week 01 | Typical Day 01
2017-01-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | Typical Week 01 | Typical Day 01
2017-01-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | Typical Week 01 | Typical Day 01
2017-01-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | Typical Week 01 | Typical Day 01
2017-01-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | Typical Week 01 | Typical Day 01
2017-01-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | Typical Week 01 | Typical Day 01
2017-01-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 7 | Typical Week 01 | Typical Day 01
2017-01-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | Typical Week 01 | Typical Day 01
2017-01-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | Typical Week 01 | Typical Day 01
2017-01-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | Typical Week 01 | Typical Day 01
2017-01-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 4 | Typical Week 01 | Typical Day 01
2017-01-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 5 | Typical Week 01 | Typical Day 01
2017-01-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 6 | Typical Week 01 | Typical Day 01
2017-01-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 7 | Typical Week 01 | Typical Day 01
2017-01-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | Typical Week 01 | Typical Day 01
2017-01-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | Typical Week 01 | Typical Day 01
2017-01-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | Typical Week 01 | Typical Day 01
2017-01-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 4 | Typical Week 01 | Typical Day 01
2017-01-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 5 | Typical Week 01 | Typical Day 01
2017-01-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 6 | Typical Week 01 | Typical Day 01
2017-01-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 7 | Typical Week 01 | Typical Day 01
2017-01-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 1 | Typical Week 01 | Typical Day 01
2017-01-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 2 | Typical Week 01 | Typical Day 01
2017-01-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 3 | Typical Week 01 | Typical Day 01
2017-01-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 4 | Typical Week 01 | Typical Day 01
2017-01-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 5 | Typical Week 01 | Typical Day 01
2017-01-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 6 | Typical Week 01 | Typical Day 01
2017-01-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 7 | Typical Week 01 | Typical Day 01
2017-01-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 1 | Typical Week 01 | Typical Day 01
2017-01-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 2 | Typical Week 01 | Typical Day 01
2017-02-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 3 | Typical Week 01 | Typical Day 01
2017-02-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 4 | Typical Week 01 | Typical Day 01
2017-02-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | Typical Week 01 | Typical Day 01
2017-02-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 6 | Typical Week 01 | Typical Day 01
2017-02-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 7 | Typical Week 01 | Typical Day 01
2017-02-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 1 | Typical Week 01 | Typical Day 01
2017-02-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 2 | Typical Week 01 | Typical Day 01
2017-02-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 3 | Typical Week 01 | Typical Day 01
2017-02-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 4 | Typical Week 01 | Typical Day 01
2017-02-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 5 | Typical Week 01 | Typical Day 01
2017-02-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 6 | Typical Week 01 | Typical Day 01
2017-02-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 7 | Typical Week 01 | Typical Day 01
2017-02-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 1 | Typical Week 01 | Typical Day 01
2017-02-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 2 | Typical Week 01 | Typical Day 01
2017-02-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 3 | Typical Week 01 | Typical Day 01
2017-02-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 4 | Typical Week 01 | Typical Day 01
2017-02-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 5 | Typical Week 01 | Typical Day 01
2017-02-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 6 | Typical Week 01 | Typical Day 01
2017-02-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 7 | Typical Week 01 | Typical Day 01
2017-02-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 1 | Typical Week 01 | Typical Day 01
2017-02-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 2 | Typical Week 01 | Typical Day 01
2017-02-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 3 | Typical Week 01 | Typical Day 01
2017-02-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 4 | Typical Week 01 | Typical Day 01
2017-02-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 5 | Typical Week 01 | Typical Day 01
2017-02-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 6 | Typical Week 01 | Typical Day 01
2017-02-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 7 | Typical Week 01 | Typical Day 01
2017-02-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 1 | Typical Week 01 | Typical Day 01
2017-02-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 2 | Typical Week 01 | Typical Day 01
2017-03-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 3 | Typical Week 01 | Typical Day 01
2017-03-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 4 | Typical Week 01 | Typical Day 01
2017-03-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 5 | Typical Week 01 | Typical Day 01
2017-03-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 6 | Typical Week 01 | Typical Day 01
2017-03-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 7 | Typical Week 01 | Typical Day 01
2017-03-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 1 | Typical Week 01 | Typical Day 01
2017-03-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 2 | Typical Week 01 | Typical Day 01
2017-03-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 3 | Typical Week 01 | Typical Day 01
2017-03-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 4 | Typical Week 01 | Typical Day 01
2017-03-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 5 | Typical Week 01 | Typical Day 01
2017-03-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 6 | Typical Week 01 | Typical Day 01
2017-03-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 7 | Typical Week 01 | Typical Day 01
2017-03-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 1 | Typical Week 01 | Typical Day 01
2017-03-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 2 | Typical Week 01 | Typical Day 01
2017-03-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 3 | Typical Week 01 | Typical Day 01
2017-03-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 4 | Typical Week 01 | Typical Day 01
2017-03-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 5 | Typical Week 01 | Typical Day 01
2017-03-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 6 | Typical Week 01 | Typical Day 01
2017-03-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 7 | Typical Week 01 | Typical Day 01
2017-03-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 1 | Typical Week 01 | Typical Day 01
2017-03-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 2 | Typical Week 01 | Typical Day 01
2017-03-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 3 | Typical Week 01 | Typical Day 01
2017-03-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 4 | Typical Week 01 | Typical Day 01
2017-03-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 5 | Typical Week 01 | Typical Day 01
2017-03-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 6 | Typical Week 01 | Typical Day 01
2017-03-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 7 | Typical Week 01 | Typical Day 01
2017-03-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 1 | Typical Week 01 | Typical Day 01
2017-03-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 2 | Typical Week 01 | Typical Day 01
2017-03-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 3 | Typical Week 01 | Typical Day 01
2017-03-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 4 | Typical Week 01 | Typical Day 01
2017-03-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 5 | Typical Week 01 | Typical Day 01
2017-04-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 6 | Typical Week 01 | Typical Day 01
2017-04-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 7 | Typical Week 01 | Typical Day 01
2017-04-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 1 | Typical Week 01 | Typical Day 01
2017-04-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 2 | Typical Week 01 | Typical Day 01
2017-04-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 3 | Typical Week 01 | Typical Day 01
2017-04-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 4 | Typical Week 01 | Typical Day 01
2017-04-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 5 | Typical Week 01 | Typical Day 01
2017-04-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 6 | Typical Week 01 | Typical Day 01
2017-04-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 7 | Typical Week 01 | Typical Day 01
2017-04-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 1 | Typical Week 01 | Typical Day 01
2017-04-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 2 | Typical Week 01 | Typical Day 01
2017-04-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 3 | Typical Week 01 | Typical Day 01
2017-04-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 4 | Typical Week 01 | Typical Day 01
2017-04-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 5 | Typical Week 01 | Typical Day 01
2017-04-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 6 | Typical Week 01 | Typical Day 01
2017-04-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 7 | Typical Week 03 | Typical Day 01
2017-04-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 1 | Typical Week 03 | Typical Day 01
2017-04-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 2 | Typical Week 03 | Typical Day 01
2017-04-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 3 | Typical Week 03 | Typical Day 01
2017-04-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 4 | Typical Week 03 | Typical Day 01
2017-04-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 5 | Typical Week 03 | Typical Day 01
2017-04-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 6 | Typical Week 03 | Typical Day 01
2017-04-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 7 | Typical Week 04 | Typical Day 01
2017-04-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 1 | Typical Week 04 | Typical Day 01
2017-04-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 2 | Typical Week 04 | Typical Day 01
2017-04-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 3 | Typical Week 04 | Typical Day 01
2017-04-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 4 | Typical Week 04 | Typical Day 01
2017-04-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 5 | Typical Week 04 | Typical Day 01
2017-04-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 6 | Typical Week 04 | Typical Day 01
2017-04-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 7 | Typical Week 05 | Typical Day 01
2017-05-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 1 | Typical Week 05 | Typical Day 01
2017-05-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 2 | Typical Week 05 | Typical Day 01
2017-05-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 3 | Typical Week 05 | Typical Day 01
2017-05-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 4 | Typical Week 05 | Typical Day 01
2017-05-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 5 | Typical Week 05 | Typical Day 01
2017-05-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 6 | Typical Week 05 | Typical Day 01
2017-05-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 7 | Typical Week 01 | Typical Day 01
2017-05-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 1 | Typical Week 01 | Typical Day 01
2017-05-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 2 | Typical Week 01 | Typical Day 01
2017-05-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 3 | Typical Week 01 | Typical Day 01
2017-05-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 4 | Typical Week 01 | Typical Day 01
2017-05-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 5 | Typical Week 01 | Typical Day 01
2017-05-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 6 | Typical Week 01 | Typical Day 01
2017-05-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 7 | Typical Week 02 | Typical Day 01
2017-05-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 1 | Typical Week 02 | Typical Day 01
2017-05-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 2 | Typical Week 02 | Typical Day 01
2017-05-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 3 | Typical Week 02 | Typical Day 01
2017-05-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 4 | Typical Week 02 | Typical Day 01
2017-05-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 5 | Typical Week 02 | Typical Day 01
2017-05-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 6 | Typical Week 02 | Typical Day 01
2017-05-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 7 | Typical Week 03 | Typical Day 01
2017-05-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 1 | Typical Week 03 | Typical Day 01
2017-05-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 2 | Typical Week 03 | Typical Day 01
2017-05-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 3 | Typical Week 03 | Typical Day 01
2017-05-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 4 | Typical Week 03 | Typical Day 01
2017-05-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 5 | Typical Week 03 | Typical Day 01
2017-05-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 6 | Typical Week 03 | Typical Day 01
2017-05-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 7 | Typical Week 04 | Typical Day 01
2017-05-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 1 | Typical Week 04 | Typical Day 01
2017-05-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 2 | Typical Week 04 | Typical Day 01
2017-05-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 3 | Typical Week 04 | Typical Day 01
2017-06-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 4 | Typical Week 04 | Typical Day 01
2017-06-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 5 | Typical Week 04 | Typical Day 01
2017-06-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 6 | Typical Week 04 | Typical Day 01
2017-06-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 7 | Typical Week 05 | Typical Day 01
2017-06-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 1 | Typical Week 05 | Typical Day 01
2017-06-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 2 | Typical Week 05 | Typical Day 01
2017-06-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 3 | Typical Week 05 | Typical Day 01
2017-06-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 4 | Typical Week 05 | Typical Day 01
2017-06-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 5 | Typical Week 05 | Typical Day 01
2017-06-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 6 | Typical Week 05 | Typical Day 01
2017-06-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 7 | Typical Week 01 | Typical Day 01
2017-06-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 1 | Typical Week 01 | Typical Day 01
2017-06-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 2 | Typical Week 01 | Typical Day 01
2017-06-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 3 | Typical Week 01 | Typical Day 01
2017-06-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 4 | Typical Week 01 | Typical Day 01
2017-06-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 5 | Typical Week 01 | Typical Day 01
2017-06-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 6 | Typical Week 01 | Typical Day 01
2017-06-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 7 | Typical Week 02 | Typical Day 01
2017-06-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 1 | Typical Week 02 | Typical Day 01
2017-06-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 2 | Typical Week 02 | Typical Day 01
2017-06-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 3 | Typical Week 02 | Typical Day 01
2017-06-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 4 | Typical Week 02 | Typical Day 01
2017-06-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 5 | Typical Week 02 | Typical Day 01
2017-06-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 6 | Typical Week 02 | Typical Day 01
2017-06-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 7 | Typical Week 03 | Typical Day 01
2017-06-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 1 | Typical Week 03 | Typical Day 01
2017-06-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 2 | Typical Week 03 | Typical Day 01
2017-06-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 3 | Typical Week 03 | Typical Day 01
2017-06-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 4 | Typical Week 03 | Typical Day 01
2017-06-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 5 | Typical Week 03 | Typical Day 01
2017-07-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 6 | Typical Week 03 | Typical Day 01
2017-07-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 7 | Typical Week 01 | Typical Day 01
2017-07-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 1 | Typical Week 01 | Typical Day 01
2017-07-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 2 | Typical Week 01 | Typical Day 01
2017-07-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 3 | Typical Week 01 | Typical Day 01
2017-07-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 4 | Typical Week 01 | Typical Day 01
2017-07-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 5 | Typical Week 01 | Typical Day 01
2017-07-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 6 | Typical Week 01 | Typical Day 01
2017-07-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 7 | Typical Week 01 | Typical Day 01
2017-07-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 1 | Typical Week 01 | Typical Day 01
2017-07-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 2 | Typical Week 01 | Typical Day 01
2017-07-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 3 | Typical Week 01 | Typical Day 01
2017-07-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 4 | Typical Week 01 | Typical Day 01
2017-07-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 5 | Typical Week 01 | Typical Day 01
2017-07-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 6 | Typical Week 01 | Typical Day 01
2017-07-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 7 | Typical Week 03 | Typical Day 01
2017-07-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 1 | Typical Week 03 | Typical Day 01
2017-07-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 2 | Typical Week 03 | Typical Day 01
2017-07-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 3 | Typical Week 03 | Typical Day 01
2017-07-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 4 | Typical Week 03 | Typical Day 01
2017-07-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 5 | Typical Week 03 | Typical Day 01
2017-07-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 6 | Typical Week 03 | Typical Day 01
2017-07-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 7 | Typical Week 04 | Typical Day 01
2017-07-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 1 | Typical Week 04 | Typical Day 01
2017-07-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 2 | Typical Week 04 | Typical Day 01
2017-07-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 3 | Typical Week 04 | Typical Day 01
2017-07-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 4 | Typical Week 04 | Typical Day 01
2017-07-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 5 | Typical Week 04 | Typical Day 01
2017-07-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 6 | Typical Week 04 | Typical Day 01
2017-07-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 7 | Typical Week 05 | Typical Day 01
2017-07-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 1 | Typical Week 05 | Typical Day 01
2017-08-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 2 | Typical Week 05 | Typical Day 01
2017-08-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 3 | Typical Week 05 | Typical Day 01
2017-08-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 4 | Typical Week 05 | Typical Day 01
2017-08-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 5 | Typical Week 05 | Typical Day 01
2017-08-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 6 | Typical Week 05 | Typical Day 01
2017-08-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 7 | Typical Week 01 | Typical Day 01
2017-08-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 1 | Typical Week 01 | Typical Day 01
2017-08-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 2 | Typical Week 01 | Typical Day 01
2017-08-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 3 | Typical Week 01 | Typical Day 01
2017-08-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 4 | Typical Week 01 | Typical Day 01
2017-08-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 5 | Typical Week 01 | Typical Day 01
2017-08-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 6 | Typical Week 01 | Typical Day 01
2017-08-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 7 | Typical Week 02 | Typical Day 01
2017-08-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 1 | Typical Week 02 | Typical Day 01
2017-08-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 2 | Typical Week 02 | Typical Day 01
2017-08-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 3 | Typical Week 02 | Typical Day 01
2017-08-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 4 | Typical Week 02 | Typical Day 01
2017-08-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 5 | Typical Week 02 | Typical Day 01
2017-08-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 6 | Typical Week 02 | Typical Day 01
2017-08-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 7 | Typical Week 03 | Typical Day 01
2017-08-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 1 | Typical Week 03 | Typical Day 01
2017-08-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 2 | Typical Week 03 | Typical Day 01
2017-08-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 3 | Typical Week 03 | Typical Day 01
2017-08-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 4 | Typical Week 03 | Typical Day 01
2017-08-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 5 | Typical Week 03 | Typical Day 01
2017-08-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 6 | Typical Week 03 | Typical Day 01
2017-08-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 7 | Typical Week 04 | Typical Day 01
2017-08-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 1 | Typical Week 04 | Typical Day 01
2017-08-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 2 | Typical Week 04 | Typical Day 01
2017-08-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 3 | Typical Week 04 | Typical Day 01
2017-08-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 4 | Typical Week 04 | Typical Day 01
2017-09-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 5 | Typical Week 04 | Typical Day 01
2017-09-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 6 | Typical Week 04 | Typical Day 01
2017-09-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 7 | Typical Week 05 | Typical Day 01
2017-09-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 1 | Typical Week 05 | Typical Day 01
2017-09-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 2 | Typical Week 05 | Typical Day 01
2017-09-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 3 | Typical Week 05 | Typical Day 01
2017-09-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 4 | Typical Week 05 | Typical Day 01
2017-09-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 5 | Typical Week 05 | Typical Day 01
2017-09-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 6 | Typical Week 05 | Typical Day 01
2017-09-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 7 | Typical Week 01 | Typical Day 01
2017-09-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 1 | Typical Week 01 | Typical Day 01
2017-09-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 2 | Typical Week 01 | Typical Day 01
2017-09-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 3 | Typical Week 01 | Typical Day 01
2017-09-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 4 | Typical Week 01 | Typical Day 01
2017-09-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 5 | Typical Week 01 | Typical Day 01
2017-09-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 6 | Typical Week 01 | Typical Day 01
2017-09-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 7 | Typical Week 02 | Typical Day 01
2017-09-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 1 | Typical Week 02 | Typical Day 01
2017-09-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 2 | Typical Week 02 | Typical Day 01
2017-09-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 3 | Typical Week 02 | Typical Day 01
2017-09-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 4 | Typical Week 02 | Typical Day 01
2017-09-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 5 | Typical Week 02 | Typical Day 01
2017-09-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 6 | Typical Week 02 | Typical Day 01
2017-09-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 7 | Typical Week 03 | Typical Day 01
2017-09-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 1 | Typical Week 03 | Typical Day 01
2017-09-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 2 | Typical Week 03 | Typical Day 01
2017-09-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 3 | Typical Week 03 | Typical Day 01
2017-09-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 4 | Typical Week 03 | Typical Day 01
2017-09-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 5 | Typical Week 03 | Typical Day 01
2017-09-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 6 | Typical Week 03 | Typical Day 01
2017-10-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 7 | Typical Week 01 | Typical Day 01
2017-10-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 1 | Typical Week 01 | Typical Day 01
2017-10-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 2 | Typical Week 01 | Typical Day 01
2017-10-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 3 | Typical Week 01 | Typical Day 01
2017-10-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 4 | Typical Week 01 | Typical Day 01
2017-10-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 5 | Typical Week 01 | Typical Day 01
2017-10-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 6 | Typical Week 01 | Typical Day 01
2017-10-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 7 | Typical Week 01 | Typical Day 01
2017-10-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 1 | Typical Week 01 | Typical Day 01
2017-10-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 2 | Typical Week 01 | Typical Day 01
2017-10-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 3 | Typical Week 01 | Typical Day 01
2017-10-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 4 | Typical Week 01 | Typical Day 01
2017-10-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 5 | Typical Week 01 | Typical Day 01
2017-10-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 6 | Typical Week 01 | Typical Day 01
2017-10-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 7 | Typical Week 01 | Typical Day 01
2017-10-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 1 | Typical Week 01 | Typical Day 01
2017-10-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 2 | Typical Week 01 | Typical Day 01
2017-10-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 3 | Typical Week 01 | Typical Day 01
2017-10-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 4 | Typical Week 01 | Typical Day 01
2017-10-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 5 | Typical Week 01 | Typical Day 01
2017-10-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 6 | Typical Week 01 | Typical Day 01
2017-10-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 7 | Typical Week 01 | Typical Day 01
2017-10-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 1 | Typical Week 01 | Typical Day 01
2017-10-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 2 | Typical Week 01 | Typical Day 01
2017-10-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 3 | Typical Week 01 | Typical Day 01
2017-10-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 4 | Typical Week 01 | Typical Day 01
2017-10-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 5 | Typical Week 01 | Typical Day 01
2017-10-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 6 | Typical Week 01 | Typical Day 01
2017-10-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 7 | Typical Week 01 | Typical Day 01
2017-10-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 1 | Typical Week 01 | Typical Day 01
2017-10-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 2 | Typical Week 01 | Typical Day 01
2017-11-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 3 | Typical Week 01 | Typical Day 01
2017-11-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 4 | Typical Week 01 | Typical Day 01
2017-11-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 5 | Typical Week 01 | Typical Day 01
2017-11-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 6 | Typical Week 01 | Typical Day 01
2017-11-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 7 | Typical Week 01 | Typical Day 01
2017-11-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 1 | Typical Week 01 | Typical Day 01
2017-11-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 2 | Typical Week 01 | Typical Day 01
2017-11-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 3 | Typical Week 01 | Typical Day 01
2017-11-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 4 | Typical Week 01 | Typical Day 01
2017-11-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 5 | Typical Week 01 | Typical Day 01
2017-11-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 6 | Typical Week 01 | Typical Day 01
2017-11-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 7 | Typical Week 01 | Typical Day 01
2017-11-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 1 | Typical Week 01 | Typical Day 01
2017-11-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 2 | Typical Week 01 | Typical Day 01
2017-11-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 3 | Typical Week 01 | Typical Day 01
2017-11-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 4 | Typical Week 01 | Typical Day 01
2017-11-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 5 | Typical Week 01 | Typical Day 01
2017-11-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 6 | Typical Week 01 | Typical Day 01
2017-11-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 7 | Typical Week 01 | Typical Day 01
2017-11-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 1 | Typical Week 01 | Typical Day 01
2017-11-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 2 | Typical Week 01 | Typical Day 01
2017-11-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 3 | Typical Week 01 | Typical Day 01
2017-11-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 4 | Typical Week 01 | Typical Day 01
2017-11-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 5 | Typical Week 01 | Typical Day 01
2017-11-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 6 | Typical Week 01 | Typical Day 01
2017-11-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 7 | Typical Week 01 | Typical Day 01
2017-11-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 1 | Typical Week 01 | Typical Day 01
2017-11-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 2 | Typical Week 01 | Typical Day 01
2017-11-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 3 | Typical Week 01 | Typical Day 01
2017-11-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 4 | Typical Week 01 | Typical Day 01
2017-12-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 5 | Typical Week 01 | Typical Day 01
2017-12-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 6 | Typical Week 01 | Typical Day 01
2017-12-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 7 | Typical Week 01 | Typical Day 01
2017-12-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 1 | Typical Week 01 | Typical Day 01
2017-12-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 2 | Typical Week 01 | Typical Day 01
2017-12-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 3 | Typical Week 01 | Typical Day 01
2017-12-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 4 | Typical Week 01 | Typical Day 01
2017-12-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 5 | Typical Week 01 | Typical Day 01
2017-12-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 6 | Typical Week 01 | Typical Day 01
2017-12-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 7 | Typical Week 01 | Typical Day 01
2017-12-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 1 | Typical Week 01 | Typical Day 01
2017-12-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 2 | Typical Week 01 | Typical Day 01
2017-12-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 3 | Typical Week 01 | Typical Day 01
2017-12-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 4 | Typical Week 01 | Typical Day 01
2017-12-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 5 | Typical Week 01 | Typical Day 01
2017-12-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 6 | Typical Week 01 | Typical Day 01
2017-12-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 7 | Typical Week 01 | Typical Day 01
2017-12-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 1 | Typical Week 01 | Typical Day 01
2017-12-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 2 | Typical Week 01 | Typical Day 01
2017-12-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 3 | Typical Week 01 | Typical Day 01
2017-12-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 4 | Typical Week 01 | Typical Day 01
2017-12-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 5 | Typical Week 01 | Typical Day 01
2017-12-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 6 | Typical Week 01 | Typical Day 01
2017-12-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 7 | Typical Week 01 | Typical Day 01
2017-12-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 1 | Typical Week 01 | Typical Day 01
2017-12-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 2 | Typical Week 01 | Typical Day 01
2017-12-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 3 | Typical Week 01 | Typical Day 01
2017-12-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 4 | Typical Week 01 | Typical Day 01
2017-12-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 5 | Typical Week 01 | Typical Day 01
2017-12-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 6 | Typical Week 01 | Typical Day 01
2017-12-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 53 | 7 | Typical Week 01 | Typical Day 01

## Load Schedule
Load Schedule Generator
USER MUST FILL IN THE CELL BELOW
IES Results Input |  |  | No
|  | Room heating plant sens. load (kW) | Room dehum. plant load (kW) |  | If IES override is not populated the insert gain estimated below and the gain profile will populate based on the run schedule profile
Typical Gains
Date | Time | Example Run.aps | Example Run.aps |  | People Sensible (W) |  |  | People Latent (W) |  |  | Lighting (W/m2) |  |  | Small Power (W/m2) |  |  | Process Equipment (W/m2) |  |  | Total Fabric Losses (W)
Fri, 01/Jan | 0:30 | 7.3127 | 0 |  | 0 |  |  | 0 |  |  | 0 |  |  | 1 |  |  | 0 |  |  | 0
| 1:30 | 7.5126 | 0
| 2:30 | 7.5798 | 0
| 3:30 | 7.5631 | 0
| 4:30 | 7.4796 | 0 | Hour | -3 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00
| 5:30 | 7.3438 | 0 | Hour | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
| 6:30 | 7.0129 | 0 | People Sensible (W)
| 7:30 | 6.6508 | 0 | People Latent (W)
| 8:30 | 6.3907 | 0 | Lighting (W/m2)
| 9:30 | 6.1488 | 0 | Small Power (W/m2) | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
| 10:30 | 6.021 | 0 | Process Equipment (W/m2)
| 11:30 | 5.8842 | 0 | Total Fabric Losses (W)
| 12:30 | 5.6485 | 0
| 13:30 | 5.3127 | 0
| 14:30 | 4.9666 | 0
| 15:30 | 5.0862 | 0
| 16:30 | 5.6389 | 0
| 17:30 | 5.9217 | 0
| 18:30 | 6.115 | 0
| 19:30 | 6.4717 | 0
| 20:30 | 6.7343 | 0
| 21:30 | 7.0415 | 0
| 22:30 | 7.4643 | 0
| 23:30 | 7.7046 | 0
Sat, 02/Jan | 0:30 | 7.8593 | 0
| 1:30 | 8.0672 | 0
| 2:30 | 8.2471 | 0
| 3:30 | 8.4818 | 0
| 4:30 | 8.5144 | 0
| 5:30 | 8.7144 | 0
| 6:30 | 9.1264 | 0
| 7:30 | 9.3199 | 0
| 8:30 | 9.4802 | 0
| 9:30 | 9.3657 | 0
| 10:30 | 8.9534 | 0
| 11:30 | 8.5539 | 0
| 12:30 | 8.1772 | 0
| 13:30 | 8.084 | 0
| 14:30 | 8.2065 | 0
| 15:30 | 8.2667 | 0
| 16:30 | 8.3738 | 0
| 17:30 | 8.6137 | 0
| 18:30 | 8.8129 | 0
| 19:30 | 8.8223 | 0
| 20:30 | 8.7896 | 0
| 21:30 | 8.7548 | 0
| 22:30 | 8.7376 | 0
| 23:30 | 8.7325 | 0
Sun, 03/Jan | 0:30 | 8.3918 | 0
| 1:30 | 7.7167 | 0
| 2:30 | 7.1935 | 0
| 3:30 | 7.1799 | 0
| 4:30 | 7.5393 | 0
| 5:30 | 7.8131 | 0
| 6:30 | 8.2189 | 0
| 7:30 | 8.7138 | 0
| 8:30 | 9.0899 | 0
| 9:30 | 9.5758 | 0
| 10:30 | 9.7271 | 0
| 11:30 | 9.6457 | 0
| 12:30 | 9.7812 | 0
| 13:30 | 9.985 | 0
| 14:30 | 10.2339 | 0
| 15:30 | 10.5869 | 0
| 16:30 | 10.8851 | 0
| 17:30 | 11.0958 | 0
| 18:30 | 11.2794 | 0
| 19:30 | 11.4166 | 0
| 20:30 | 11.7588 | 0
| 21:30 | 12.1055 | 0
| 22:30 | 12.1176 | 0
| 23:30 | 12.0795 | 0
Mon, 04/Jan | 0:30 | 12.239 | 0
| 1:30 | 12.3475 | 0
| 2:30 | 12.2854 | 0
| 3:30 | 12.1921 | 0
| 4:30 | 11.9764 | 0
| 5:30 | 11.7907 | 0
| 6:30 | 11.716 | 0
| 7:30 | 11.5548 | 0
| 8:30 | 778.9434 | 0
| 9:30 | 158.0735 | 0
| 10:30 | 110.042 | 0
| 11:30 | 93.9044 | 0
| 12:30 | 94.0488 | 0
| 13:30 | 103.9282 | 0
| 14:30 | 108.0095 | 0
| 15:30 | 108.2149 | 0
| 16:30 | 104.6196 | 0
| 17:30 | 96.1736 | 0
| 18:30 | 5.0824 | 0
| 19:30 | 5.717 | 0
| 20:30 | 6.5975 | 0
| 21:30 | 7.5621 | 0
| 22:30 | 8.4588 | 0
| 23:30 | 8.9906 | 0
Tue, 05/Jan | 0:30 | 9.4335 | 0
| 1:30 | 9.7572 | 0
| 2:30 | 10.0524 | 0
| 3:30 | 10.3142 | 0
| 4:30 | 10.5911 | 0
| 5:30 | 11.0131 | 0
| 6:30 | 11.4181 | 0
| 7:30 | 11.571 | 0
| 8:30 | 683.4838 | 0
| 9:30 | 152.5373 | 0
| 10:30 | 112.7693 | 0
| 11:30 | 93.099 | 0
| 12:30 | 79.2625 | 0
| 13:30 | 76.2548 | 0
| 14:30 | 81.6201 | 0
| 15:30 | 84.7547 | 0
| 16:30 | 87.829 | 0
| 17:30 | 88.1516 | 0
| 18:30 | 5.5818 | 0
| 19:30 | 6.1197 | 0
| 20:30 | 6.8358 | 0
| 21:30 | 7.4767 | 0
| 22:30 | 8.1728 | 0
| 23:30 | 8.7207 | 0
Wed, 06/Jan | 0:30 | 9.2334 | 0
| 1:30 | 9.7588 | 0
| 2:30 | 10.1414 | 0
| 3:30 | 10.3908 | 0
| 4:30 | 10.5584 | 0
| 5:30 | 10.4027 | 0
| 6:30 | 9.9866 | 0
| 7:30 | 9.5868 | 0
| 8:30 | 551.6541 | 0
| 9:30 | 97.1358 | 0
| 10:30 | 63.2583 | 0
| 11:30 | 44.6454 | 0
| 12:30 | 29.8778 | 0
| 13:30 | 21.3916 | 0
| 14:30 | 18.633 | 0
| 15:30 | 21.7904 | 0
| 16:30 | 28.3652 | 0
| 17:30 | 31.5716 | 0
| 18:30 | 2.9145 | 0
| 19:30 | 3.5974 | 0
| 20:30 | 4.2131 | 0
| 21:30 | 5.0349 | 0
| 22:30 | 5.4274 | 0
| 23:30 | 5.5946 | 0
Thu, 07/Jan | 0:30 | 5.9789 | 0
| 1:30 | 6.3154 | 0
| 2:30 | 6.7009 | 0
| 3:30 | 6.9602 | 0
| 4:30 | 7.164 | 0
| 5:30 | 7.4742 | 0
| 6:30 | 7.6931 | 0
| 7:30 | 7.918 | 0
| 8:30 | 461.3923 | 0
| 9:30 | 92.5547 | 0
| 10:30 | 61.6706 | 0
| 11:30 | 47.4854 | 0
| 12:30 | 38.2815 | 0
| 13:30 | 40.6613 | 0
| 14:30 | 47.7229 | 0
| 15:30 | 45.8 | 0
| 16:30 | 43.8276 | 0
| 17:30 | 44.4816 | 0
| 18:30 | 4.2887 | 0
| 19:30 | 4.888 | 0
| 20:30 | 5.3045 | 0
| 21:30 | 5.861 | 0
| 22:30 | 6.4214 | 0
| 23:30 | 6.946 | 0
Fri, 08/Jan | 0:30 | 7.4211 | 0
| 1:30 | 7.6711 | 0
| 2:30 | 7.6418 | 0
| 3:30 | 7.3719 | 0
| 4:30 | 7.1834 | 0
| 5:30 | 6.9331 | 0
| 6:30 | 6.9837 | 0
| 7:30 | 7.3099 | 0
| 8:30 | 418.9187 | 0
| 9:30 | 78.0256 | 0
| 10:30 | 57.2116 | 0
| 11:30 | 45.3638 | 0
| 12:30 | 34.4255 | 0
| 13:30 | 27.7818 | 0
| 14:30 | 25.9549 | 0
| 15:30 | 27.389 | 0
| 16:30 | 26.459 | 0
| 17:30 | 16.7538 | 0
| 18:30 | 1.65 | 0
| 19:30 | 2.0916 | 0
| 20:30 | 2.3572 | 0
| 21:30 | 2.5061 | 0
| 22:30 | 2.6956 | 0
| 23:30 | 2.7423 | 0
Sat, 09/Jan | 0:30 | 2.7742 | 0
| 1:30 | 2.8326 | 0
| 2:30 | 2.8996 | 0
| 3:30 | 2.9191 | 0
| 4:30 | 2.8868 | 0
| 5:30 | 2.8803 | 0
| 6:30 | 2.8513 | 0
| 7:30 | 2.8746 | 0
| 8:30 | 2.9491 | 0
| 9:30 | 2.9391 | 0
| 10:30 | 2.8623 | 0
| 11:30 | 2.7335 | 0
| 12:30 | 2.641 | 0
| 13:30 | 2.6152 | 0
| 14:30 | 2.5993 | 0
| 15:30 | 2.6925 | 0
| 16:30 | 2.8353 | 0
| 17:30 | 2.9387 | 0
| 18:30 | 3.0946 | 0
| 19:30 | 3.2136 | 0
| 20:30 | 3.2884 | 0
| 21:30 | 3.3314 | 0
| 22:30 | 3.3158 | 0
| 23:30 | 3.2988 | 0
Sun, 10/Jan | 0:30 | 3.2722 | 0
| 1:30 | 3.2706 | 0
| 2:30 | 3.2864 | 0
| 3:30 | 3.3214 | 0
| 4:30 | 3.3603 | 0
| 5:30 | 3.4026 | 0
| 6:30 | 3.462 | 0
| 7:30 | 3.5253 | 0
| 8:30 | 3.5799 | 0
| 9:30 | 3.5354 | 0
| 10:30 | 3.1663 | 0
| 11:30 | 2.6546 | 0
| 12:30 | 2.1914 | 0
| 13:30 | 1.8651 | 0
| 14:30 | 1.8536 | 0
| 15:30 | 1.988 | 0
| 16:30 | 1.9386 | 0
| 17:30 | 1.9614 | 0
| 18:30 | 2.0149 | 0
| 19:30 | 1.9167 | 0
| 20:30 | 2.1413 | 0
| 21:30 | 2.6525 | 0
| 22:30 | 3.2046 | 0
| 23:30 | 3.4881 | 0
Mon, 11/Jan | 0:30 | 3.5641 | 0
| 1:30 | 3.8274 | 0
| 2:30 | 4.1405 | 0
| 3:30 | 4.4047 | 0
| 4:30 | 4.6715 | 0
| 5:30 | 4.8647 | 0
| 6:30 | 4.9609 | 0
| 7:30 | 4.9847 | 0
| 8:30 | 336.0827 | 0
| 9:30 | 29.4873 | 0
| 10:30 | 14.255 | 0
| 11:30 | 9.931 | 0
| 12:30 | 7.2522 | 0
| 13:30 | 6.7113 | 0
| 14:30 | 8.5031 | 0
| 15:30 | 9.789 | 0
| 16:30 | 10.3667 | 0
| 17:30 | 10.8254 | 0
| 18:30 | 1.3889 | 0
| 19:30 | 2.0879 | 0
| 20:30 | 2.6786 | 0
| 21:30 | 3.2473 | 0
| 22:30 | 3.6391 | 0
| 23:30 | 3.9158 | 0
Tue, 12/Jan | 0:30 | 4.2363 | 0
| 1:30 | 4.5206 | 0
| 2:30 | 4.4264 | 0
| 3:30 | 4.1709 | 0
| 4:30 | 4.2029 | 0
| 5:30 | 4.2095 | 0
| 6:30 | 4.1513 | 0
| 7:30 | 4.0683 | 0
| 8:30 | 280.1473 | 0
| 9:30 | 28.42 | 0
| 10:30 | 18.0815 | 0
| 11:30 | 12.1136 | 0
| 12:30 | 10.0118 | 0
| 13:30 | 9.0924 | 0
| 14:30 | 9.0541 | 0
| 15:30 | 10.569 | 0
| 16:30 | 13.6276 | 0
| 17:30 | 16.9432 | 0
| 18:30 | 2.1389 | 0
| 19:30 | 2.7313 | 0
| 20:30 | 3.1981 | 0
| 21:30 | 3.4901 | 0
| 22:30 | 3.9535 | 0
| 23:30 | 4.3862 | 0
Wed, 13/Jan | 0:30 | 4.5689 | 0
| 1:30 | 4.6522 | 0
| 2:30 | 4.7671 | 0
| 3:30 | 4.9732 | 0
| 4:30 | 5.1437 | 0
| 5:30 | 5.2547 | 0
| 6:30 | 5.3677 | 0
| 7:30 | 5.4871 | 0
| 8:30 | 334.084 | 0
| 9:30 | 55.4523 | 0
| 10:30 | 41.8339 | 0
| 11:30 | 36.0342 | 0
| 12:30 | 33.0108 | 0
| 13:30 | 31.9495 | 0
| 14:30 | 31.5146 | 0
| 15:30 | 31.3122 | 0
| 16:30 | 31.9921 | 0
| 17:30 | 32.4638 | 0
| 18:30 | 3.4671 | 0
| 19:30 | 3.9854 | 0
| 20:30 | 4.1794 | 0
| 21:30 | 4.3679 | 0
| 22:30 | 4.6184 | 0
| 23:30 | 4.8111 | 0
Thu, 14/Jan | 0:30 | 5.0459 | 0
| 1:30 | 5.2408 | 0
| 2:30 | 5.4003 | 0
| 3:30 | 5.6351 | 0
| 4:30 | 6.0385 | 0
| 5:30 | 6.4492 | 0
| 6:30 | 6.7867 | 0
| 7:30 | 7.0969 | 0
| 8:30 | 403.0285 | 0
| 9:30 | 81.2418 | 0
| 10:30 | 51.5156 | 0
| 11:30 | 36.9434 | 0
| 12:30 | 28.3928 | 0
| 13:30 | 23.4548 | 0
| 14:30 | 20.5545 | 0
| 15:30 | 23.4899 | 0
| 16:30 | 31.9251 | 0
| 17:30 | 36.4814 | 0
| 18:30 | 3.7152 | 0
| 19:30 | 4.0556 | 0
| 20:30 | 4.2567 | 0
| 21:30 | 4.4888 | 0
| 22:30 | 4.7175 | 0
| 23:30 | 4.6768 | 0
Fri, 15/Jan | 0:30 | 4.4577 | 0
| 1:30 | 4.3805 | 0
| 2:30 | 4.4167 | 0
| 3:30 | 4.6722 | 0
| 4:30 | 5.0396 | 0
| 5:30 | 5.3358 | 0
| 6:30 | 5.5927 | 0
| 7:30 | 5.8285 | 0
| 8:30 | 335.334 | 0
| 9:30 | 55.6242 | 0
| 10:30 | 37.3143 | 0
| 11:30 | 27.9096 | 0
| 12:30 | 23.7305 | 0
| 13:30 | 21.2799 | 0
| 14:30 | 19.2797 | 0
| 15:30 | 22.792 | 0
| 16:30 | 27.3419 | 0
| 17:30 | 27.1965 | 0
| 18:30 | 3.0745 | 0
| 19:30 | 3.6293 | 0
| 20:30 | 3.8781 | 0
| 21:30 | 4.0448 | 0
| 22:30 | 4.3311 | 0
| 23:30 | 4.5282 | 0
Sat, 16/Jan | 0:30 | 4.6978 | 0
| 1:30 | 4.9156 | 0
| 2:30 | 5.1792 | 0
| 3:30 | 5.5036 | 0
| 4:30 | 5.7938 | 0
| 5:30 | 6.017 | 0
| 6:30 | 6.235 | 0
| 7:30 | 6.4673 | 0
| 8:30 | 6.6124 | 0
| 9:30 | 6.4861 | 0
| 10:30 | 6.1565 | 0
| 11:30 | 5.8042 | 0
| 12:30 | 5.4748 | 0
| 13:30 | 5.234 | 0
| 14:30 | 5.1135 | 0
| 15:30 | 5.2314 | 0
| 16:30 | 5.6033 | 0
| 17:30 | 6.0188 | 0
| 18:30 | 6.3541 | 0
| 19:30 | 6.5524 | 0
| 20:30 | 6.6083 | 0
| 21:30 | 6.6819 | 0
| 22:30 | 6.7977 | 0
| 23:30 | 6.9545 | 0
Sun, 17/Jan | 0:30 | 7.086 | 0
| 1:30 | 7.1712 | 0
| 2:30 | 7.2153 | 0
| 3:30 | 7.2858 | 0
| 4:30 | 7.3293 | 0
| 5:30 | 7.349 | 0
| 6:30 | 7.4554 | 0
| 7:30 | 7.5031 | 0
| 8:30 | 7.4933 | 0
| 9:30 | 7.4361 | 0
| 10:30 | 7.2258 | 0
| 11:30 | 7.0225 | 0
| 12:30 | 6.8558 | 0
| 13:30 | 6.7584 | 0
| 14:30 | 6.793 | 0
| 15:30 | 6.8801 | 0
| 16:30 | 7.0467 | 0
| 17:30 | 7.1976 | 0
| 18:30 | 7.2578 | 0
| 19:30 | 7.5579 | 0
| 20:30 | 7.7843 | 0
| 21:30 | 7.7042 | 0
| 22:30 | 7.6024 | 0
| 23:30 | 7.4909 | 0
Mon, 18/Jan | 0:30 | 7.4998 | 0
| 1:30 | 7.5199 | 0
| 2:30 | 7.486 | 0
| 3:30 | 7.5417 | 0
| 4:30 | 7.6566 | 0
| 5:30 | 7.773 | 0
| 6:30 | 7.9324 | 0
| 7:30 | 8.2655 | 0
| 8:30 | 534.1978 | 0
| 9:30 | 106.03 | 0
| 10:30 | 79.4672 | 0
| 11:30 | 65.1915 | 0
| 12:30 | 57.6108 | 0
| 13:30 | 53.4808 | 0
| 14:30 | 49.4129 | 0
| 15:30 | 50.7401 | 0
| 16:30 | 53.5985 | 0
| 17:30 | 52.0779 | 0
| 18:30 | 3.9354 | 0
| 19:30 | 4.3793 | 0
| 20:30 | 4.7659 | 0
| 21:30 | 5.1871 | 0
| 22:30 | 5.7616 | 0
| 23:30 | 6.4437 | 0
Tue, 19/Jan | 0:30 | 6.8661 | 0
| 1:30 | 7.0726 | 0
| 2:30 | 7.1933 | 0
| 3:30 | 7.2626 | 0
| 4:30 | 7.4921 | 0
| 5:30 | 7.9804 | 0
| 6:30 | 8.4215 | 0
| 7:30 | 8.7544 | 0
| 8:30 | 513.9212 | 0
| 9:30 | 108.9729 | 0
| 10:30 | 76.5183 | 0
| 11:30 | 64.032 | 0
| 12:30 | 55.3651 | 0
| 13:30 | 48.0866 | 0
| 14:30 | 44.0908 | 0
| 15:30 | 46.8838 | 0
| 16:30 | 63.0435 | 0
| 17:30 | 74.228 | 0
| 18:30 | 5.7026 | 0
| 19:30 | 6.3452 | 0
| 20:30 | 7.1922 | 0
| 21:30 | 8.0325 | 0
| 22:30 | 8.6058 | 0
| 23:30 | 9.3121 | 0
Wed, 20/Jan | 0:30 | 9.7347 | 0
| 1:30 | 10.1912 | 0
| 2:30 | 10.7197 | 0
| 3:30 | 11.1212 | 0
| 4:30 | 11.4784 | 0
| 5:30 | 11.7298 | 0
| 6:30 | 11.8918 | 0
| 7:30 | 12.0889 | 0
| 8:30 | 645.8813 | 0
| 9:30 | 157.6028 | 0
| 10:30 | 107.6017 | 0
| 11:30 | 71.2664 | 0
| 12:30 | 53.6622 | 0
| 13:30 | 46.8513 | 0
| 14:30 | 46.1352 | 0
| 15:30 | 48.6089 | 0
| 16:30 | 49.5975 | 0
| 17:30 | 49.1639 | 0
| 18:30 | 4.3195 | 0
| 19:30 | 4.7976 | 0
| 20:30 | 5.1831 | 0
| 21:30 | 5.5994 | 0
| 22:30 | 5.8452 | 0
| 23:30 | 5.9145 | 0
Thu, 21/Jan | 0:30 | 6.0345 | 0
| 1:30 | 6.0708 | 0
| 2:30 | 6.0229 | 0
| 3:30 | 5.8991 | 0
| 4:30 | 5.8097 | 0
| 5:30 | 5.856 | 0
| 6:30 | 5.8629 | 0
| 7:30 | 5.7538 | 0
| 8:30 | 351.6651 | 0
| 9:30 | 45.0716 | 0
| 10:30 | 25.5692 | 0
| 11:30 | 16.4378 | 0
| 12:30 | 12.4505 | 0
| 13:30 | 9.4405 | 0
| 14:30 | 8.7281 | 0
| 15:30 | 9.1389 | 0
| 16:30 | 9.4823 | 0
| 17:30 | 9.8233 | 0
| 18:30 | 0.9831 | 0
| 19:30 | 1.6384 | 0
| 20:30 | 2.1666 | 0
| 21:30 | 2.7556 | 0
| 22:30 | 3.2252 | 0
| 23:30 | 3.6103 | 0
Fri, 22/Jan | 0:30 | 3.6478 | 0
| 1:30 | 3.6637 | 0
| 2:30 | 3.915 | 0
| 3:30 | 3.9779 | 0
| 4:30 | 4.1233 | 0
| 5:30 | 4.18 | 0
| 6:30 | 4.1311 | 0
| 7:30 | 4.2682 | 0
| 8:30 | 276.1882 | 0
| 9:30 | 29.087 | 0
| 10:30 | 18.3054 | 0
| 11:30 | 12.0488 | 0
| 12:30 | 9.307 | 0
| 13:30 | 9.2602 | 0
| 14:30 | 9.2399 | 0
| 15:30 | 10.4482 | 0
| 16:30 | 12.018 | 0
| 17:30 | 12.8676 | 0
| 18:30 | 1.6491 | 0
| 19:30 | 2.2868 | 0
| 20:30 | 2.7726 | 0
| 21:30 | 3.0834 | 0
| 22:30 | 3.4327 | 0
| 23:30 | 3.7731 | 0
Sat, 23/Jan | 0:30 | 3.9839 | 0
| 1:30 | 4.1893 | 0
| 2:30 | 4.38 | 0
| 3:30 | 4.5729 | 0
| 4:30 | 4.7625 | 0
| 5:30 | 4.9365 | 0
| 6:30 | 5.1137 | 0
| 7:30 | 5.2934 | 0
| 8:30 | 5.4364 | 0
| 9:30 | 5.4421 | 0
| 10:30 | 5.3687 | 0
| 11:30 | 5.2637 | 0
| 12:30 | 5.1647 | 0
| 13:30 | 5.0374 | 0
| 14:30 | 5.0331 | 0
| 15:30 | 5.3523 | 0
| 16:30 | 5.6492 | 0
| 17:30 | 5.772 | 0
| 18:30 | 5.895 | 0
| 19:30 | 5.9973 | 0
| 20:30 | 6.0673 | 0
| 21:30 | 6.1211 | 0
| 22:30 | 6.194 | 0
| 23:30 | 6.2542 | 0
Sun, 24/Jan | 0:30 | 6.3159 | 0
| 1:30 | 6.3851 | 0
| 2:30 | 6.4846 | 0
| 3:30 | 6.6039 | 0
| 4:30 | 6.7666 | 0
| 5:30 | 6.993 | 0
| 6:30 | 7.2153 | 0
| 7:30 | 7.3654 | 0
| 8:30 | 7.506 | 0
| 9:30 | 7.6322 | 0
| 10:30 | 7.5198 | 0
| 11:30 | 7.41 | 0
| 12:30 | 7.3816 | 0
| 13:30 | 7.3501 | 0
| 14:30 | 7.3657 | 0
| 15:30 | 7.5457 | 0
| 16:30 | 7.9131 | 0
| 17:30 | 8.2435 | 0
| 18:30 | 8.416 | 0
| 19:30 | 8.4894 | 0
| 20:30 | 8.5296 | 0
| 21:30 | 8.576 | 0
| 22:30 | 8.669 | 0
| 23:30 | 8.7783 | 0
Mon, 25/Jan | 0:30 | 8.9274 | 0
| 1:30 | 9.0686 | 0
| 2:30 | 9.2136 | 0
| 3:30 | 9.33 | 0
| 4:30 | 9.5387 | 0
| 5:30 | 9.7084 | 0
| 6:30 | 9.7544 | 0
| 7:30 | 9.8733 | 0
| 8:30 | 621.063 | 0
| 9:30 | 121.6384 | 0
| 10:30 | 79.379 | 0
| 11:30 | 56.7335 | 0
| 12:30 | 51.2376 | 0
| 13:30 | 46.0704 | 0
| 14:30 | 41.2801 | 0
| 15:30 | 44.3863 | 0
| 16:30 | 54.2825 | 0
| 17:30 | 62.1818 | 0
| 18:30 | 4.4543 | 0
| 19:30 | 4.9428 | 0
| 20:30 | 5.5621 | 0
| 21:30 | 6.1169 | 0
| 22:30 | 6.6549 | 0
| 23:30 | 7.189 | 0
Tue, 26/Jan | 0:30 | 7.7446 | 0
| 1:30 | 8.1918 | 0
| 2:30 | 8.5498 | 0
| 3:30 | 8.8923 | 0
| 4:30 | 9.1286 | 0
| 5:30 | 9.3197 | 0
| 6:30 | 9.4171 | 0
| 7:30 | 9.7746 | 0
| 8:30 | 566.3692 | 0
| 9:30 | 106.5466 | 0
| 10:30 | 67.5435 | 0
| 11:30 | 54.4747 | 0
| 12:30 | 47.0896 | 0
| 13:30 | 42.8827 | 0
| 14:30 | 44.0922 | 0
| 15:30 | 48.4895 | 0
| 16:30 | 53.0625 | 0
| 17:30 | 55.3511 | 0
| 18:30 | 4.555 | 0
| 19:30 | 5.0276 | 0
| 20:30 | 5.5017 | 0
| 21:30 | 5.9654 | 0
| 22:30 | 6.4153 | 0
| 23:30 | 6.8884 | 0
Wed, 27/Jan | 0:30 | 7.3232 | 0
| 1:30 | 7.6573 | 0
| 2:30 | 7.9512 | 0
| 3:30 | 8.1251 | 0
| 4:30 | 8.1877 | 0
| 5:30 | 8.3499 | 0
| 6:30 | 8.536 | 0
| 7:30 | 8.6331 | 0
| 8:30 | 491.5797 | 0
| 9:30 | 101.0938 | 0
| 10:30 | 75.2703 | 0
| 11:30 | 61.9238 | 0
| 12:30 | 54.4497 | 0
| 13:30 | 50.7503 | 0
| 14:30 | 49.8842 | 0
| 15:30 | 51.1493 | 0
| 16:30 | 52.8928 | 0
| 17:30 | 54.0847 | 0
| 18:30 | 4.7553 | 0
| 19:30 | 5.2581 | 0
| 20:30 | 5.6474 | 0
| 21:30 | 6.1367 | 0
| 22:30 | 6.5478 | 0
| 23:30 | 6.837 | 0
Thu, 28/Jan | 0:30 | 7.2465 | 0
| 1:30 | 7.4929 | 0
| 2:30 | 7.659 | 0
| 3:30 | 7.8573 | 0
| 4:30 | 8.0453 | 0
| 5:30 | 8.224 | 0
| 6:30 | 8.3663 | 0
| 7:30 | 8.4603 | 0
| 8:30 | 473.2281 | 0
| 9:30 | 100.3798 | 0
| 10:30 | 73.8025 | 0
| 11:30 | 58.6028 | 0
| 12:30 | 50.6132 | 0
| 13:30 | 47.4271 | 0
| 14:30 | 46.3046 | 0
| 15:30 | 46.9887 | 0
| 16:30 | 48.2471 | 0
| 17:30 | 49.9973 | 0
| 18:30 | 4.673 | 0
| 19:30 | 5.1791 | 0
| 20:30 | 5.6023 | 0
| 21:30 | 6.1715 | 0
| 22:30 | 6.5766 | 0
| 23:30 | 6.7782 | 0
Fri, 29/Jan | 0:30 | 7.0898 | 0
| 1:30 | 7.7371 | 0
| 2:30 | 8.2717 | 0
| 3:30 | 8.3822 | 0
| 4:30 | 8.3926 | 0
| 5:30 | 8.3272 | 0
| 6:30 | 8.2803 | 0
| 7:30 | 8.2759 | 0
| 8:30 | 462.732 | 0
| 9:30 | 98.3712 | 0
| 10:30 | 74.0091 | 0
| 11:30 | 59.7936 | 0
| 12:30 | 46.5166 | 0
| 13:30 | 35.1588 | 0
| 14:30 | 31.3289 | 0
| 15:30 | 33.2293 | 0
| 16:30 | 37.4589 | 0
| 17:30 | 39.4426 | 0
| 18:30 | 3.8611 | 0
| 19:30 | 4.3786 | 0
| 20:30 | 4.716 | 0
| 21:30 | 5.1379 | 0
| 22:30 | 5.4978 | 0
| 23:30 | 5.7309 | 0
Sat, 30/Jan | 0:30 | 5.9243 | 0
| 1:30 | 6.1734 | 0
| 2:30 | 6.365 | 0
| 3:30 | 6.4755 | 0
| 4:30 | 6.5785 | 0
| 5:30 | 6.705 | 0
| 6:30 | 6.8593 | 0
| 7:30 | 6.9473 | 0
| 8:30 | 7.0667 | 0
| 9:30 | 7.1009 | 0
| 10:30 | 6.9128 | 0
| 11:30 | 6.7568 | 0
| 12:30 | 6.6667 | 0
| 13:30 | 6.6381 | 0
| 14:30 | 6.7425 | 0
| 15:30 | 6.8839 | 0
| 16:30 | 7.1306 | 0
| 17:30 | 7.4672 | 0
| 18:30 | 7.7195 | 0
| 19:30 | 7.978 | 0
| 20:30 | 8.1759 | 0
| 21:30 | 8.2566 | 0
| 22:30 | 8.3631 | 0
| 23:30 | 8.5139 | 0
Sun, 31/Jan | 0:30 | 8.6479 | 0
| 1:30 | 8.765 | 0
| 2:30 | 8.863 | 0
| 3:30 | 8.9691 | 0
| 4:30 | 9.1208 | 0
| 5:30 | 9.2928 | 0
| 6:30 | 9.5165 | 0
| 7:30 | 9.6707 | 0
| 8:30 | 9.7014 | 0
| 9:30 | 9.6603 | 0
| 10:30 | 9.4734 | 0
| 11:30 | 9.1456 | 0
| 12:30 | 8.7927 | 0
| 13:30 | 8.4737 | 0
| 14:30 | 8.3758 | 0
| 15:30 | 8.597 | 0
| 16:30 | 8.9776 | 0
| 17:30 | 9.3767 | 0
| 18:30 | 9.8842 | 0
| 19:30 | 10.4279 | 0
| 20:30 | 10.8574 | 0
| 21:30 | 11.1811 | 0
| 22:30 | 11.2255 | 0
| 23:30 | 10.906 | 0
Mon, 01/Feb | 0:30 | 10.2633 | 0
| 1:30 | 9.4779 | 0
| 2:30 | 8.7447 | 0
| 3:30 | 8.2093 | 0
| 4:30 | 7.9146 | 0
| 5:30 | 7.7875 | 0
| 6:30 | 7.8983 | 0
| 7:30 | 8.1155 | 0
| 8:30 | 567.0003 | 0
| 9:30 | 92.3487 | 0
| 10:30 | 61.716 | 0
| 11:30 | 44.5137 | 0
| 12:30 | 33.8593 | 0
| 13:30 | 27.95 | 0
| 14:30 | 24.9036 | 0
| 15:30 | 25.0734 | 0
| 16:30 | 29.345 | 0
| 17:30 | 32.0324 | 0
| 18:30 | 2.3276 | 0
| 19:30 | 3.0127 | 0
| 20:30 | 3.6051 | 0
| 21:30 | 4.1683 | 0
| 22:30 | 4.7414 | 0
| 23:30 | 5.2147 | 0
Tue, 02/Feb | 0:30 | 5.5126 | 0
| 1:30 | 5.7856 | 0
| 2:30 | 5.9841 | 0
| 3:30 | 6.2214 | 0
| 4:30 | 6.4365 | 0
| 5:30 | 6.6262 | 0
| 6:30 | 6.7886 | 0
| 7:30 | 6.9672 | 0
| 8:30 | 447.3574 | 0
| 9:30 | 69.0247 | 0
| 10:30 | 42.8863 | 0
| 11:30 | 26.2971 | 0
| 12:30 | 17.8031 | 0
| 13:30 | 15.8317 | 0
| 14:30 | 16.4494 | 0
| 15:30 | 19.8825 | 0
| 16:30 | 20.6745 | 0
| 17:30 | 20.9515 | 0
| 18:30 | 2.3277 | 0
| 19:30 | 3.0447 | 0
| 20:30 | 3.4146 | 0
| 21:30 | 3.8737 | 0
| 22:30 | 4.0908 | 0
| 23:30 | 4.046 | 0
Wed, 03/Feb | 0:30 | 4.045 | 0
| 1:30 | 4.1378 | 0
| 2:30 | 4.2807 | 0
| 3:30 | 4.4572 | 0
| 4:30 | 4.651 | 0
| 5:30 | 4.8225 | 0
| 6:30 | 4.8955 | 0
| 7:30 | 4.8878 | 0
| 8:30 | 323.08 | 0
| 9:30 | 36.1489 | 0
| 10:30 | 21.4557 | 0
| 11:30 | 13.9578 | 0
| 12:30 | 10.7124 | 0
| 13:30 | 9.2798 | 0
| 14:30 | 8.4849 | 0
| 15:30 | 9.0254 | 0
| 16:30 | 10.5075 | 0
| 17:30 | 11.2641 | 0
| 18:30 | 1.3975 | 0
| 19:30 | 2.0529 | 0
| 20:30 | 2.5195 | 0
| 21:30 | 2.9125 | 0
| 22:30 | 3.312 | 0
| 23:30 | 3.5833 | 0
Thu, 04/Feb | 0:30 | 3.8316 | 0
| 1:30 | 4.0348 | 0
| 2:30 | 4.1486 | 0
| 3:30 | 4.2984 | 0
| 4:30 | 4.523 | 0
| 5:30 | 4.6468 | 0
| 6:30 | 4.7529 | 0
| 7:30 | 4.9665 | 0
| 8:30 | 312.514 | 0
| 9:30 | 43.3055 | 0
| 10:30 | 27.685 | 0
| 11:30 | 20.1638 | 0
| 12:30 | 16.9039 | 0
| 13:30 | 15.535 | 0
| 14:30 | 15.0382 | 0
| 15:30 | 16.4018 | 0
| 16:30 | 18.5812 | 0
| 17:30 | 19.8794 | 0
| 18:30 | 2.4456 | 0
| 19:30 | 3.0084 | 0
| 20:30 | 3.3139 | 0
| 21:30 | 3.603 | 0
| 22:30 | 3.9363 | 0
| 23:30 | 4.0947 | 0
Fri, 05/Feb | 0:30 | 4.4223 | 0
| 1:30 | 4.8199 | 0
| 2:30 | 4.907 | 0
| 3:30 | 4.9934 | 0
| 4:30 | 5.2189 | 0
| 5:30 | 5.3565 | 0
| 6:30 | 5.4407 | 0
| 7:30 | 5.5763 | 0
| 8:30 | 325.835 | 0
| 9:30 | 40.3501 | 0
| 10:30 | 23.3124 | 0
| 11:30 | 16.2569 | 0
| 12:30 | 12.8064 | 0
| 13:30 | 12.3127 | 0
| 14:30 | 12.7255 | 0
| 15:30 | 16.0237 | 0
| 16:30 | 21.6034 | 0
| 17:30 | 22.7171 | 0
| 18:30 | 2.6238 | 0
| 19:30 | 3.366 | 0
| 20:30 | 3.7223 | 0
| 21:30 | 3.9014 | 0
| 22:30 | 4.1107 | 0
| 23:30 | 4.2132 | 0
Sat, 06/Feb | 0:30 | 4.2793 | 0
| 1:30 | 4.4696 | 0
| 2:30 | 4.6157 | 0
| 3:30 | 4.6666 | 0
| 4:30 | 4.7848 | 0
| 5:30 | 4.8085 | 0
| 6:30 | 4.9042 | 0
| 7:30 | 5.0014 | 0
| 8:30 | 5.0116 | 0
| 9:30 | 4.9936 | 0
| 10:30 | 4.8285 | 0
| 11:30 | 4.4025 | 0
| 12:30 | 4.1233 | 0
| 13:30 | 4.0562 | 0
| 14:30 | 4.0511 | 0
| 15:30 | 4.2497 | 0
| 16:30 | 4.5268 | 0
| 17:30 | 4.8023 | 0
| 18:30 | 5.0364 | 0
| 19:30 | 5.2604 | 0
| 20:30 | 5.3622 | 0
| 21:30 | 5.3888 | 0
| 22:30 | 5.4972 | 0
| 23:30 | 5.5894 | 0
Sun, 07/Feb | 0:30 | 5.698 | 0
| 1:30 | 5.8362 | 0
| 2:30 | 5.9012 | 0
| 3:30 | 5.9974 | 0
| 4:30 | 6.1263 | 0
| 5:30 | 6.1923 | 0
| 6:30 | 6.2668 | 0
| 7:30 | 6.3699 | 0
| 8:30 | 6.4464 | 0
| 9:30 | 6.4907 | 0
| 10:30 | 6.5657 | 0
| 11:30 | 6.5995 | 0
| 12:30 | 6.6023 | 0
| 13:30 | 6.68 | 0
| 14:30 | 6.7185 | 0
| 15:30 | 6.8313 | 0
| 16:30 | 7.0388 | 0
| 17:30 | 7.1592 | 0
| 18:30 | 7.2261 | 0
| 19:30 | 7.292 | 0
| 20:30 | 7.3335 | 0
| 21:30 | 7.4547 | 0
| 22:30 | 7.6779 | 0
| 23:30 | 7.7663 | 0
Mon, 08/Feb | 0:30 | 7.9264 | 0
| 1:30 | 8.1662 | 0
| 2:30 | 8.2001 | 0
| 3:30 | 8.3223 | 0
| 4:30 | 8.5856 | 0
| 5:30 | 8.7308 | 0
| 6:30 | 8.9039 | 0
| 7:30 | 9.1071 | 0
| 8:30 | 569.9843 | 0
| 9:30 | 114.3591 | 0
| 10:30 | 88.445 | 0
| 11:30 | 73.9502 | 0
| 12:30 | 65.7098 | 0
| 13:30 | 66.3854 | 0
| 14:30 | 68.2798 | 0
| 15:30 | 67.4429 | 0
| 16:30 | 68.2215 | 0
| 17:30 | 69.1791 | 0
| 18:30 | 4.8942 | 0
| 19:30 | 5.4289 | 0
| 20:30 | 6.0205 | 0
| 21:30 | 6.5041 | 0
| 22:30 | 7.1134 | 0
| 23:30 | 7.6003 | 0
Tue, 09/Feb | 0:30 | 7.9825 | 0
| 1:30 | 8.4295 | 0
| 2:30 | 8.7437 | 0
| 3:30 | 8.9909 | 0
| 4:30 | 9.3895 | 0
| 5:30 | 9.6762 | 0
| 6:30 | 9.6923 | 0
| 7:30 | 9.7973 | 0
| 8:30 | 567.8326 | 0
| 9:30 | 131.1342 | 0
| 10:30 | 103.1694 | 0
| 11:30 | 87.362 | 0
| 12:30 | 77.4166 | 0
| 13:30 | 73.4397 | 0
| 14:30 | 71.0001 | 0
| 15:30 | 71.1523 | 0
| 16:30 | 72.7098 | 0
| 17:30 | 72.6032 | 0
| 18:30 | 5.3182 | 0
| 19:30 | 5.8397 | 0
| 20:30 | 6.3707 | 0
| 21:30 | 6.9514 | 0
| 22:30 | 7.4928 | 0
| 23:30 | 8.077 | 0
Wed, 10/Feb | 0:30 | 8.5525 | 0
| 1:30 | 8.9708 | 0
| 2:30 | 9.3393 | 0
| 3:30 | 9.6347 | 0
| 4:30 | 9.8799 | 0
| 5:30 | 10.1409 | 0
| 6:30 | 10.4063 | 0
| 7:30 | 10.6156 | 0
| 8:30 | 581.9517 | 0
| 9:30 | 133.7904 | 0
| 10:30 | 94.9788 | 0
| 11:30 | 76.867 | 0
| 12:30 | 67.5159 | 0
| 13:30 | 63.3182 | 0
| 14:30 | 65.2179 | 0
| 15:30 | 71.9441 | 0
| 16:30 | 82.6058 | 0
| 17:30 | 87.4272 | 0
| 18:30 | 6.0905 | 0
| 19:30 | 6.6858 | 0
| 20:30 | 7.3353 | 0
| 21:30 | 8.0829 | 0
| 22:30 | 8.7052 | 0
| 23:30 | 9.2809 | 0
Thu, 11/Feb | 0:30 | 9.627 | 0
| 1:30 | 9.934 | 0
| 2:30 | 10.1645 | 0
| 3:30 | 10.3351 | 0
| 4:30 | 10.5841 | 0
| 5:30 | 10.7591 | 0
| 6:30 | 10.9619 | 0
| 7:30 | 11.1916 | 0
| 8:30 | 604.1102 | 0
| 9:30 | 148.907 | 0
| 10:30 | 113.442 | 0
| 11:30 | 90.7703 | 0
| 12:30 | 79.1 | 0
| 13:30 | 78.9235 | 0
| 14:30 | 77.2306 | 0
| 15:30 | 76.7721 | 0
| 16:30 | 80.583 | 0
| 17:30 | 85.0945 | 0
| 18:30 | 5.994 | 0
| 19:30 | 6.5219 | 0
| 20:30 | 7.149 | 0
| 21:30 | 7.788 | 0
| 22:30 | 8.3433 | 0
| 23:30 | 8.9641 | 0
Fri, 12/Feb | 0:30 | 9.4628 | 0
| 1:30 | 9.7268 | 0
| 2:30 | 9.8977 | 0
| 3:30 | 10.1231 | 0
| 4:30 | 10.4221 | 0
| 5:30 | 10.5707 | 0
| 6:30 | 10.7831 | 0
| 7:30 | 11.1202 | 0
| 8:30 | 596.6053 | 0
| 9:30 | 147.0536 | 0
| 10:30 | 109.8827 | 0
| 11:30 | 87.1343 | 0
| 12:30 | 77.2107 | 0
| 13:30 | 74.9787 | 0
| 14:30 | 67.0147 | 0
| 15:30 | 63.5918 | 0
| 16:30 | 70.7614 | 0
| 17:30 | 77.5051 | 0
| 18:30 | 5.7895 | 0
| 19:30 | 6.2786 | 0
| 20:30 | 6.7644 | 0
| 21:30 | 7.3384 | 0
| 22:30 | 7.8986 | 0
| 23:30 | 8.484 | 0
Sat, 13/Feb | 0:30 | 9.0226 | 0
| 1:30 | 9.3976 | 0
| 2:30 | 9.6561 | 0
| 3:30 | 9.8475 | 0
| 4:30 | 10.0282 | 0
| 5:30 | 10.1781 | 0
| 6:30 | 10.2971 | 0
| 7:30 | 10.4462 | 0
| 8:30 | 10.5498 | 0
| 9:30 | 10.6348 | 0
| 10:30 | 10.6745 | 0
| 11:30 | 10.5933 | 0
| 12:30 | 10.4174 | 0
| 13:30 | 10.0362 | 0
| 14:30 | 9.8403 | 0
| 15:30 | 9.9974 | 0
| 16:30 | 10.312 | 0
| 17:30 | 10.6896 | 0
| 18:30 | 10.9277 | 0
| 19:30 | 11.1023 | 0
| 20:30 | 11.1581 | 0
| 21:30 | 11.2303 | 0
| 22:30 | 11.3413 | 0
| 23:30 | 11.4464 | 0
Sun, 14/Feb | 0:30 | 11.6468 | 0
| 1:30 | 11.8345 | 0
| 2:30 | 11.9309 | 0
| 3:30 | 12.0608 | 0
| 4:30 | 12.2051 | 0
| 5:30 | 12.203 | 0
| 6:30 | 12.1949 | 0
| 7:30 | 12.2434 | 0
| 8:30 | 12.225 | 0
| 9:30 | 12.0094 | 0
| 10:30 | 11.5575 | 0
| 11:30 | 11.1375 | 0
| 12:30 | 10.9034 | 0
| 13:30 | 10.8239 | 0
| 14:30 | 10.7791 | 0
| 15:30 | 10.7967 | 0
| 16:30 | 11.0091 | 0
| 17:30 | 11.2794 | 0
| 18:30 | 11.5335 | 0
| 19:30 | 11.7882 | 0
| 20:30 | 11.9551 | 0
| 21:30 | 12.161 | 0
| 22:30 | 12.4233 | 0
| 23:30 | 12.6819 | 0
Mon, 15/Feb | 0:30 | 13.0419 | 0
| 1:30 | 13.4706 | 0
| 2:30 | 13.7984 | 0
| 3:30 | 14.0452 | 0
| 4:30 | 14.2538 | 0
| 5:30 | 14.3655 | 0
| 6:30 | 14.5018 | 0
| 7:30 | 14.6371 | 0
| 8:30 | 905.7228 | 0
| 9:30 | 208.2318 | 0
| 10:30 | 146.8097 | 0
| 11:30 | 116.6194 | 0
| 12:30 | 103.4009 | 0
| 13:30 | 92.1313 | 0
| 14:30 | 78.7062 | 0
| 15:30 | 76.5499 | 0
| 16:30 | 90.9478 | 0
| 17:30 | 107.5211 | 0
| 18:30 | 5.9467 | 0
| 19:30 | 6.69 | 0
| 20:30 | 7.6157 | 0
| 21:30 | 8.7319 | 0
| 22:30 | 9.53 | 0
| 23:30 | 9.9361 | 0
Tue, 16/Feb | 0:30 | 10.3416 | 0
| 1:30 | 10.7364 | 0
| 2:30 | 11.0035 | 0
| 3:30 | 11.2713 | 0
| 4:30 | 11.5109 | 0
| 5:30 | 11.5937 | 0
| 6:30 | 11.7 | 0
| 7:30 | 11.8154 | 0
| 8:30 | 690.2592 | 0
| 9:30 | 139.2693 | 0
| 10:30 | 94.2868 | 0
| 11:30 | 76.6405 | 0
| 12:30 | 68.4486 | 0
| 13:30 | 59.9916 | 0
| 14:30 | 50.2052 | 0
| 15:30 | 49.2654 | 0
| 16:30 | 61.403 | 0
| 17:30 | 77.0966 | 0
| 18:30 | 5.4731 | 0
| 19:30 | 6.1198 | 0
| 20:30 | 6.6735 | 0
| 21:30 | 7.2458 | 0
| 22:30 | 8.0503 | 0
| 23:30 | 8.6674 | 0
Wed, 17/Feb | 0:30 | 9.0381 | 0
| 1:30 | 9.23 | 0
| 2:30 | 9.4205 | 0
| 3:30 | 9.6251 | 0
| 4:30 | 9.8365 | 0
| 5:30 | 9.968 | 0
| 6:30 | 10.2104 | 0
| 7:30 | 10.5043 | 0
| 8:30 | 592.1083 | 0
| 9:30 | 114.8244 | 0
| 10:30 | 72.1623 | 0
| 11:30 | 54.8653 | 0
| 12:30 | 44.2401 | 0
| 13:30 | 37.8538 | 0
| 14:30 | 35.1672 | 0
| 15:30 | 35.5337 | 0
| 16:30 | 43.8074 | 0
| 17:30 | 57.3833 | 0
| 18:30 | 5.1037 | 0
| 19:30 | 5.882 | 0
| 20:30 | 6.6306 | 0
| 21:30 | 7.2845 | 0
| 22:30 | 7.8094 | 0
| 23:30 | 8.4644 | 0
Thu, 18/Feb | 0:30 | 9.129 | 0
| 1:30 | 9.7478 | 0
| 2:30 | 10.1863 | 0
| 3:30 | 10.4812 | 0
| 4:30 | 10.6961 | 0
| 5:30 | 10.9973 | 0
| 6:30 | 11.6349 | 0
| 7:30 | 12.0245 | 0
| 8:30 | 627.2136 | 0
| 9:30 | 125.9799 | 0
| 10:30 | 78.1503 | 0
| 11:30 | 52.3061 | 0
| 12:30 | 37.2167 | 0
| 13:30 | 31.7403 | 0
| 14:30 | 32.1765 | 0
| 15:30 | 39.5036 | 0
| 16:30 | 49.9703 | 0
| 17:30 | 57.0951 | 0
| 18:30 | 5.0669 | 0
| 19:30 | 5.597 | 0
| 20:30 | 6.006 | 0
| 21:30 | 6.3516 | 0
| 22:30 | 6.3592 | 0
| 23:30 | 6.414 | 0
Fri, 19/Feb | 0:30 | 6.5766 | 0
| 1:30 | 6.7343 | 0
| 2:30 | 6.8485 | 0
| 3:30 | 6.9826 | 0
| 4:30 | 7.0988 | 0
| 5:30 | 7.1 | 0
| 6:30 | 7.0842 | 0
| 7:30 | 7.1587 | 0
| 8:30 | 414.5862 | 0
| 9:30 | 71.9837 | 0
| 10:30 | 50.1165 | 0
| 11:30 | 38.4965 | 0
| 12:30 | 32.7393 | 0
| 13:30 | 28.8235 | 0
| 14:30 | 26.2334 | 0
| 15:30 | 25.4372 | 0
| 16:30 | 25.9093 | 0
| 17:30 | 26.9829 | 0
| 18:30 | 3.0157 | 0
| 19:30 | 3.7405 | 0
| 20:30 | 4.1573 | 0
| 21:30 | 4.64 | 0
| 22:30 | 5.0388 | 0
| 23:30 | 5.3508 | 0
Sat, 20/Feb | 0:30 | 5.5656 | 0
| 1:30 | 6.161 | 0
| 2:30 | 7.0758 | 0
| 3:30 | 7.7029 | 0
| 4:30 | 7.8416 | 0
| 5:30 | 7.6641 | 0
| 6:30 | 7.801 | 0
| 7:30 | 8.0034 | 0
| 8:30 | 7.8558 | 0
| 9:30 | 7.6772 | 0
| 10:30 | 7.2974 | 0
| 11:30 | 6.7207 | 0
| 12:30 | 6.2087 | 0
| 13:30 | 5.8482 | 0
| 14:30 | 5.8215 | 0
| 15:30 | 5.9887 | 0
| 16:30 | 6.245 | 0
| 17:30 | 6.4667 | 0
| 18:30 | 6.7379 | 0
| 19:30 | 7.0589 | 0
| 20:30 | 7.2947 | 0
| 21:30 | 7.5264 | 0
| 22:30 | 7.7985 | 0
| 23:30 | 7.988 | 0
Sun, 21/Feb | 0:30 | 8.2409 | 0
| 1:30 | 8.5532 | 0
| 2:30 | 8.8362 | 0
| 3:30 | 8.9917 | 0
| 4:30 | 9.1037 | 0
| 5:30 | 9.2892 | 0
| 6:30 | 9.4954 | 0
| 7:30 | 9.709 | 0
| 8:30 | 9.6133 | 0
| 9:30 | 9.1916 | 0
| 10:30 | 8.6312 | 0
| 11:30 | 7.8843 | 0
| 12:30 | 7.1914 | 0
| 13:30 | 6.827 | 0
| 14:30 | 6.6025 | 0
| 15:30 | 6.6166 | 0
| 16:30 | 6.9007 | 0
| 17:30 | 7.3272 | 0
| 18:30 | 7.7873 | 0
| 19:30 | 8.2301 | 0
| 20:30 | 8.6712 | 0
| 21:30 | 8.8431 | 0
| 22:30 | 8.8222 | 0
| 23:30 | 8.8328 | 0
Mon, 22/Feb | 0:30 | 8.975 | 0
| 1:30 | 9.2056 | 0
| 2:30 | 9.3354 | 0
| 3:30 | 9.4135 | 0
| 4:30 | 9.7056 | 0
| 5:30 | 10.014 | 0
| 6:30 | 10.1522 | 0
| 7:30 | 10.3205 | 0
| 8:30 | 643.761 | 0
| 9:30 | 104.8445 | 0
| 10:30 | 58.518 | 0
| 11:30 | 40.317 | 0
| 12:30 | 33.7881 | 0
| 13:30 | 33.445 | 0
| 14:30 | 31.2487 | 0
| 15:30 | 32.0495 | 0
| 16:30 | 35.2887 | 0
| 17:30 | 37.3912 | 0
| 18:30 | 2.7834 | 0
| 19:30 | 3.4035 | 0
| 20:30 | 3.8795 | 0
| 21:30 | 4.3462 | 0
| 22:30 | 4.7708 | 0
| 23:30 | 5.1044 | 0
Tue, 23/Feb | 0:30 | 5.3552 | 0
| 1:30 | 5.6255 | 0
| 2:30 | 5.7132 | 0
| 3:30 | 5.7181 | 0
| 4:30 | 5.7767 | 0
| 5:30 | 5.7834 | 0
| 6:30 | 5.7928 | 0
| 7:30 | 5.8537 | 0
| 8:30 | 388.9348 | 0
| 9:30 | 43.4824 | 0
| 10:30 | 22.0473 | 0
| 11:30 | 14.9219 | 0
| 12:30 | 13.2582 | 0
| 13:30 | 11.6568 | 0
| 14:30 | 9.8574 | 0
| 15:30 | 9.8972 | 0
| 16:30 | 11.6124 | 0
| 17:30 | 13.4605 | 0
| 18:30 | 1.6177 | 0
| 19:30 | 2.3097 | 0
| 20:30 | 2.9424 | 0
| 21:30 | 3.4876 | 0
| 22:30 | 3.9081 | 0
| 23:30 | 4.132 | 0
Wed, 24/Feb | 0:30 | 4.4494 | 0
| 1:30 | 4.9052 | 0
| 2:30 | 5.2116 | 0
| 3:30 | 5.5329 | 0
| 4:30 | 5.7195 | 0
| 5:30 | 5.748 | 0
| 6:30 | 5.9517 | 0
| 7:30 | 6.2889 | 0
| 8:30 | 377.1475 | 0
| 9:30 | 44.4873 | 0
| 10:30 | 21.0071 | 0
| 11:30 | 11.3512 | 0
| 12:30 | 9.4289 | 0
| 13:30 | 8.6968 | 0
| 14:30 | 7.6263 | 0
| 15:30 | 7.4164 | 0
| 16:30 | 10.9632 | 0
| 17:30 | 17.3889 | 0
| 18:30 | 2.4699 | 0
| 19:30 | 3.3489 | 0
| 20:30 | 3.9767 | 0
| 21:30 | 4.4373 | 0
| 22:30 | 4.5081 | 0
| 23:30 | 4.3116 | 0
Thu, 25/Feb | 0:30 | 4.7304 | 0
| 1:30 | 5.2905 | 0
| 2:30 | 5.5264 | 0
| 3:30 | 5.5663 | 0
| 4:30 | 5.5799 | 0
| 5:30 | 5.6699 | 0
| 6:30 | 5.7521 | 0
| 7:30 | 5.8612 | 0
| 8:30 | 343.2862 | 0
| 9:30 | 45.774 | 0
| 10:30 | 28.0294 | 0
| 11:30 | 18.6642 | 0
| 12:30 | 14.42 | 0
| 13:30 | 12.4163 | 0
| 14:30 | 10.894 | 0
| 15:30 | 12.0522 | 0
| 16:30 | 14.1237 | 0
| 17:30 | 13.9594 | 0
| 18:30 | 2.3118 | 0
| 19:30 | 3.4073 | 0
| 20:30 | 3.7407 | 0
| 21:30 | 4.1416 | 0
| 22:30 | 4.509 | 0
| 23:30 | 4.5127 | 0
Fri, 26/Feb | 0:30 | 4.6072 | 0
| 1:30 | 4.9974 | 0
| 2:30 | 5.3833 | 0
| 3:30 | 5.6 | 0
| 4:30 | 5.9196 | 0
| 5:30 | 6.187 | 0
| 6:30 | 6.478 | 0
| 7:30 | 6.7498 | 0
| 8:30 | 371.4135 | 0
| 9:30 | 44.9901 | 0
| 10:30 | 18.8979 | 0
| 11:30 | 9.4669 | 0
| 12:30 | 8.1212 | 0
| 13:30 | 6.55 | 0
| 14:30 | 8.2399 | 0
| 15:30 | 13.0237 | 0
| 16:30 | 17.3186 | 0
| 17:30 | 21.7422 | 0
| 18:30 | 2.6374 | 0
| 19:30 | 3.5329 | 0
| 20:30 | 3.9099 | 0
| 21:30 | 4.2651 | 0
| 22:30 | 4.8496 | 0
| 23:30 | 5.3168 | 0
Sat, 27/Feb | 0:30 | 5.65 | 0
| 1:30 | 5.7521 | 0
| 2:30 | 5.4767 | 0
| 3:30 | 5.2721 | 0
| 4:30 | 5.3102 | 0
| 5:30 | 5.283 | 0
| 6:30 | 5.2537 | 0
| 7:30 | 5.2593 | 0
| 8:30 | 5.2399 | 0
| 9:30 | 5.1897 | 0
| 10:30 | 5.0715 | 0
| 11:30 | 4.8459 | 0
| 12:30 | 4.5992 | 0
| 13:30 | 4.5183 | 0
| 14:30 | 4.5875 | 0
| 15:30 | 4.7829 | 0
| 16:30 | 5.0491 | 0
| 17:30 | 5.1967 | 0
| 18:30 | 5.053 | 0
| 19:30 | 5.0957 | 0
| 20:30 | 5.2187 | 0
| 21:30 | 5.1356 | 0
| 22:30 | 5.2121 | 0
| 23:30 | 5.3884 | 0
Sun, 28/Feb | 0:30 | 5.6518 | 0
| 1:30 | 5.863 | 0
| 2:30 | 5.9365 | 0
| 3:30 | 6.1593 | 0
| 4:30 | 6.4061 | 0
| 5:30 | 6.448 | 0
| 6:30 | 6.6446 | 0
| 7:30 | 6.8382 | 0
| 8:30 | 6.65 | 0
| 9:30 | 6.3413 | 0
| 10:30 | 5.9755 | 0
| 11:30 | 5.5647 | 0
| 12:30 | 5.2327 | 0
| 13:30 | 5.0788 | 0
| 14:30 | 5.1241 | 0
| 15:30 | 5.2494 | 0
| 16:30 | 5.511 | 0
| 17:30 | 5.7785 | 0
| 18:30 | 6.1523 | 0
| 19:30 | 6.5624 | 0
| 20:30 | 6.7957 | 0
| 21:30 | 7.0221 | 0
| 22:30 | 7.314 | 0
| 23:30 | 7.6905 | 0
Mon, 01/Mar | 0:30 | 8.1472 | 0
| 1:30 | 8.6487 | 0
| 2:30 | 9.1082 | 0
| 3:30 | 9.5098 | 0
| 4:30 | 9.8565 | 0
| 5:30 | 10.1406 | 0
| 6:30 | 10.4214 | 0
| 7:30 | 10.69 | 0
| 8:30 | 628.4586 | 0
| 9:30 | 116.7014 | 0
| 10:30 | 76.6585 | 0
| 11:30 | 61.8097 | 0
| 12:30 | 49.8438 | 0
| 13:30 | 39.7302 | 0
| 14:30 | 32.8963 | 0
| 15:30 | 23.8988 | 0
| 16:30 | 31.2671 | 0
| 17:30 | 52.6945 | 0
| 18:30 | 4.7115 | 0
| 19:30 | 5.5757 | 0
| 20:30 | 6.3701 | 0
| 21:30 | 7.1185 | 0
| 22:30 | 7.9759 | 0
| 23:30 | 8.6861 | 0
Tue, 02/Mar | 0:30 | 9.2193 | 0
| 1:30 | 9.6747 | 0
| 2:30 | 9.9498 | 0
| 3:30 | 10.0925 | 0
| 4:30 | 10.1581 | 0
| 5:30 | 10.2145 | 0
| 6:30 | 10.1883 | 0
| 7:30 | 10.1067 | 0
| 8:30 | 565.5331 | 0
| 9:30 | 105.0798 | 0
| 10:30 | 65.9897 | 0
| 11:30 | 46.4582 | 0
| 12:30 | 33.5541 | 0
| 13:30 | 29.7878 | 0
| 14:30 | 31.1583 | 0
| 15:30 | 34.5076 | 0
| 16:30 | 36.7242 | 0
| 17:30 | 34.7549 | 0
| 18:30 | 3.321 | 0
| 19:30 | 4.0421 | 0
| 20:30 | 4.4146 | 0
| 21:30 | 4.8684 | 0
| 22:30 | 5.1987 | 0
| 23:30 | 5.5056 | 0
Wed, 03/Mar | 0:30 | 5.8239 | 0
| 1:30 | 6.1842 | 0
| 2:30 | 6.5642 | 0
| 3:30 | 7.0632 | 0
| 4:30 | 7.5373 | 0
| 5:30 | 7.7529 | 0
| 6:30 | 8.0095 | 0
| 7:30 | 8.1736 | 0
| 8:30 | 450.0876 | 0
| 9:30 | 70.051 | 0
| 10:30 | 45.9697 | 0
| 11:30 | 33.3761 | 0
| 12:30 | 27.661 | 0
| 13:30 | 28.5348 | 0
| 14:30 | 31.7979 | 0
| 15:30 | 37.9578 | 0
| 16:30 | 46.0277 | 0
| 17:30 | 50.2555 | 0
| 18:30 | 4.7075 | 0
| 19:30 | 5.5741 | 0
| 20:30 | 6.2826 | 0
| 21:30 | 7.0116 | 0
| 22:30 | 7.5227 | 0
| 23:30 | 7.8971 | 0
Thu, 04/Mar | 0:30 | 8.4205 | 0
| 1:30 | 8.9098 | 0
| 2:30 | 9.1997 | 0
| 3:30 | 9.4058 | 0
| 4:30 | 9.6097 | 0
| 5:30 | 9.8419 | 0
| 6:30 | 10.063 | 0
| 7:30 | 10.082 | 0
| 8:30 | 537.1797 | 0
| 9:30 | 108.1754 | 0
| 10:30 | 70.2246 | 0
| 11:30 | 51.4994 | 0
| 12:30 | 38.5131 | 0
| 13:30 | 28.2551 | 0
| 14:30 | 24.9544 | 0
| 15:30 | 29.9618 | 0
| 16:30 | 38.0602 | 0
| 17:30 | 48.5919 | 0
| 18:30 | 4.7994 | 0
| 19:30 | 5.5091 | 0
| 20:30 | 5.9744 | 0
| 21:30 | 6.6023 | 0
| 22:30 | 7.0948 | 0
| 23:30 | 7.4212 | 0
Fri, 05/Mar | 0:30 | 7.7563 | 0
| 1:30 | 8.1141 | 0
| 2:30 | 8.4432 | 0
| 3:30 | 8.748 | 0
| 4:30 | 9.0395 | 0
| 5:30 | 9.2251 | 0
| 6:30 | 9.3737 | 0
| 7:30 | 9.4165 | 0
| 8:30 | 501.9047 | 0
| 9:30 | 93.9468 | 0
| 10:30 | 57.6584 | 0
| 11:30 | 39.4339 | 0
| 12:30 | 25.1124 | 0
| 13:30 | 16.8496 | 0
| 14:30 | 11.4553 | 0
| 15:30 | 9.1237 | 0
| 16:30 | 11.8695 | 0
| 17:30 | 17.0772 | 0
| 18:30 | 2.4538 | 0
| 19:30 | 3.3815 | 0
| 20:30 | 3.9507 | 0
| 21:30 | 4.5051 | 0
| 22:30 | 4.9512 | 0
| 23:30 | 5.1949 | 0
Sat, 06/Mar | 0:30 | 5.4652 | 0
| 1:30 | 5.6188 | 0
| 2:30 | 5.7392 | 0
| 3:30 | 5.7756 | 0
| 4:30 | 5.6177 | 0
| 5:30 | 5.5151 | 0
| 6:30 | 5.552 | 0
| 7:30 | 5.598 | 0
| 8:30 | 5.5353 | 0
| 9:30 | 5.3871 | 0
| 10:30 | 5.2317 | 0
| 11:30 | 5.0788 | 0
| 12:30 | 4.8803 | 0
| 13:30 | 4.7026 | 0
| 14:30 | 4.64 | 0
| 15:30 | 4.6306 | 0
| 16:30 | 4.7147 | 0
| 17:30 | 4.9095 | 0
| 18:30 | 5.2224 | 0
| 19:30 | 5.5528 | 0
| 20:30 | 5.7219 | 0
| 21:30 | 5.8653 | 0
| 22:30 | 6.1364 | 0
| 23:30 | 6.3845 | 0
Sun, 07/Mar | 0:30 | 6.5114 | 0
| 1:30 | 6.5267 | 0
| 2:30 | 6.443 | 0
| 3:30 | 6.3915 | 0
| 4:30 | 6.3856 | 0
| 5:30 | 6.4451 | 0
| 6:30 | 6.4606 | 0
| 7:30 | 6.3468 | 0
| 8:30 | 6.1976 | 0
| 9:30 | 5.9783 | 0
| 10:30 | 5.6944 | 0
| 11:30 | 5.2679 | 0
| 12:30 | 4.7471 | 0
| 13:30 | 4.6958 | 0
| 14:30 | 4.8841 | 0
| 15:30 | 4.8158 | 0
| 16:30 | 4.8525 | 0
| 17:30 | 5.1134 | 0
| 18:30 | 5.4913 | 0
| 19:30 | 5.9396 | 0
| 20:30 | 6.325 | 0
| 21:30 | 6.6212 | 0
| 22:30 | 6.9545 | 0
| 23:30 | 7.218 | 0
Mon, 08/Mar | 0:30 | 7.4042 | 0
| 1:30 | 7.5996 | 0
| 2:30 | 7.7673 | 0
| 3:30 | 7.9431 | 0
| 4:30 | 8.147 | 0
| 5:30 | 8.3205 | 0
| 6:30 | 8.5422 | 0
| 7:30 | 8.7578 | 0
| 8:30 | 529.2142 | 0
| 9:30 | 67.3502 | 0
| 10:30 | 35.6982 | 0
| 11:30 | 23.2078 | 0
| 12:30 | 16.6289 | 0
| 13:30 | 13.9683 | 0
| 14:30 | 12.7799 | 0
| 15:30 | 12.4888 | 0
| 16:30 | 13.468 | 0
| 17:30 | 15.2689 | 0
| 18:30 | 1.8239 | 0
| 19:30 | 2.4924 | 0
| 20:30 | 3.1422 | 0
| 21:30 | 3.765 | 0
| 22:30 | 4.1845 | 0
| 23:30 | 4.5282 | 0
Tue, 09/Mar | 0:30 | 4.7322 | 0
| 1:30 | 4.8816 | 0
| 2:30 | 5.0795 | 0
| 3:30 | 5.2328 | 0
| 4:30 | 5.3457 | 0
| 5:30 | 5.4423 | 0
| 6:30 | 5.5676 | 0
| 7:30 | 5.6294 | 0
| 8:30 | 363.1379 | 0
| 9:30 | 39.0318 | 0
| 10:30 | 20.1806 | 0
| 11:30 | 13.1075 | 0
| 12:30 | 12.8689 | 0
| 13:30 | 15.6444 | 0
| 14:30 | 17.2809 | 0
| 15:30 | 25.4184 | 0
| 16:30 | 32.2679 | 0
| 17:30 | 33.0796 | 0
| 18:30 | 3.4276 | 0
| 19:30 | 4.39 | 0
| 20:30 | 4.9233 | 0
| 21:30 | 5.5753 | 0
| 22:30 | 6.1092 | 0
| 23:30 | 6.414 | 0
Wed, 10/Mar | 0:30 | 6.7919 | 0
| 1:30 | 7.2342 | 0
| 2:30 | 7.5306 | 0
| 3:30 | 7.7735 | 0
| 4:30 | 7.9705 | 0
| 5:30 | 8.0996 | 0
| 6:30 | 8.201 | 0
| 7:30 | 8.1501 | 0
| 8:30 | 452.2547 | 0
| 9:30 | 65.3832 | 0
| 10:30 | 33.3522 | 0
| 11:30 | 18.58 | 0
| 12:30 | 13.4401 | 0
| 13:30 | 11.0723 | 0
| 14:30 | 8.4405 | 0
| 15:30 | 7.4514 | 0
| 16:30 | 9.39 | 0
| 17:30 | 13.1556 | 0
| 18:30 | 2.22 | 0
| 19:30 | 3.1325 | 0
| 20:30 | 3.6687 | 0
| 21:30 | 4.0851 | 0
| 22:30 | 4.7164 | 0
| 23:30 | 5.0611 | 0
Thu, 11/Mar | 0:30 | 5.1682 | 0
| 1:30 | 5.2475 | 0
| 2:30 | 5.2578 | 0
| 3:30 | 5.1625 | 0
| 4:30 | 5.1247 | 0
| 5:30 | 5.0543 | 0
| 6:30 | 5.0602 | 0
| 7:30 | 5.2126 | 0
| 8:30 | 318.5837 | 0
| 9:30 | 37.0132 | 0
| 10:30 | 21.3309 | 0
| 11:30 | 14.2752 | 0
| 12:30 | 10.7732 | 0
| 13:30 | 8.6185 | 0
| 14:30 | 7.5454 | 0
| 15:30 | 8.1971 | 0
| 16:30 | 9.9191 | 0
| 17:30 | 10.7304 | 0
| 18:30 | 1.4258 | 0
| 19:30 | 2.1225 | 0
| 20:30 | 2.7541 | 0
| 21:30 | 3.2121 | 0
| 22:30 | 3.545 | 0
| 23:30 | 3.8312 | 0
Fri, 12/Mar | 0:30 | 4.0718 | 0
| 1:30 | 4.2851 | 0
| 2:30 | 4.4214 | 0
| 3:30 | 4.5346 | 0
| 4:30 | 4.6823 | 0
| 5:30 | 4.8407 | 0
| 6:30 | 4.9941 | 0
| 7:30 | 5.0578 | 0
| 8:30 | 298.0823 | 0
| 9:30 | 31.1946 | 0
| 10:30 | 15.4196 | 0
| 11:30 | 11.1752 | 0
| 12:30 | 8.1184 | 0
| 13:30 | 6.2696 | 0
| 14:30 | 5.201 | 0
| 15:30 | 5.3899 | 0
| 16:30 | 7.1865 | 0
| 17:30 | 9.6508 | 0
| 18:30 | 1.2752 | 0
| 19:30 | 2.1202 | 0
| 20:30 | 2.6921 | 0
| 21:30 | 3.1477 | 0
| 22:30 | 3.5585 | 0
| 23:30 | 3.8171 | 0
Sat, 13/Mar | 0:30 | 4.0483 | 0
| 1:30 | 4.274 | 0
| 2:30 | 4.4349 | 0
| 3:30 | 4.6045 | 0
| 4:30 | 4.7782 | 0
| 5:30 | 4.8832 | 0
| 6:30 | 4.9632 | 0
| 7:30 | 4.9888 | 0
| 8:30 | 4.8169 | 0
| 9:30 | 4.5997 | 0
| 10:30 | 4.4146 | 0
| 11:30 | 4.2049 | 0
| 12:30 | 4.0243 | 0
| 13:30 | 3.9136 | 0
| 14:30 | 3.8737 | 0
| 15:30 | 3.8674 | 0
| 16:30 | 3.9262 | 0
| 17:30 | 4.0766 | 0
| 18:30 | 4.2473 | 0
| 19:30 | 4.4496 | 0
| 20:30 | 4.6168 | 0
| 21:30 | 5.2026 | 0
| 22:30 | 5.9135 | 0
| 23:30 | 6.1891 | 0
Sun, 14/Mar | 0:30 | 6.4044 | 0
| 1:30 | 6.5951 | 0
| 2:30 | 6.7848 | 0
| 3:30 | 6.9783 | 0
| 4:30 | 7.1691 | 0
| 5:30 | 7.3394 | 0
| 6:30 | 7.4283 | 0
| 7:30 | 7.5005 | 0
| 8:30 | 7.4592 | 0
| 9:30 | 7.3273 | 0
| 10:30 | 7.1731 | 0
| 11:30 | 6.9193 | 0
| 12:30 | 6.5784 | 0
| 13:30 | 6.1909 | 0
| 14:30 | 5.8604 | 0
| 15:30 | 5.612 | 0
| 16:30 | 5.3542 | 0
| 17:30 | 5.2156 | 0
| 18:30 | 5.2186 | 0
| 19:30 | 5.2746 | 0
| 20:30 | 5.3511 | 0
| 21:30 | 5.4402 | 0
| 22:30 | 5.5455 | 0
| 23:30 | 5.6071 | 0
Mon, 15/Mar | 0:30 | 5.8081 | 0
| 1:30 | 6.0319 | 0
| 2:30 | 6.0446 | 0
| 3:30 | 5.9878 | 0
| 4:30 | 6.0562 | 0
| 5:30 | 6.1954 | 0
| 6:30 | 6.2386 | 0
| 7:30 | 6.3052 | 0
| 8:30 | 431.0723 | 0
| 9:30 | 61.4408 | 0
| 10:30 | 46.0772 | 0
| 11:30 | 41.2422 | 0
| 12:30 | 43.0453 | 0
| 13:30 | 40.9931 | 0
| 14:30 | 27.5737 | 0
| 15:30 | 22.0402 | 0
| 16:30 | 22.1108 | 0
| 17:30 | 24.4182 | 0
| 18:30 | 2.9665 | 0
| 19:30 | 3.8207 | 0
| 20:30 | 4.2185 | 0
| 21:30 | 4.6863 | 0
| 22:30 | 4.9825 | 0
| 23:30 | 5.3252 | 0
Tue, 16/Mar | 0:30 | 5.5992 | 0
| 1:30 | 5.9552 | 0
| 2:30 | 6.2815 | 0
| 3:30 | 6.5263 | 0
| 4:30 | 6.7912 | 0
| 5:30 | 6.9713 | 0
| 6:30 | 7.1675 | 0
| 7:30 | 7.1841 | 0
| 8:30 | 413.386 | 0
| 9:30 | 56.77 | 0
| 10:30 | 35.8605 | 0
| 11:30 | 27.3915 | 0
| 12:30 | 25.1714 | 0
| 13:30 | 23.8784 | 0
| 14:30 | 21.8194 | 0
| 15:30 | 23.7638 | 0
| 16:30 | 26.8939 | 0
| 17:30 | 28.8251 | 0
| 18:30 | 3.158 | 0
| 19:30 | 3.8827 | 0
| 20:30 | 4.2497 | 0
| 21:30 | 4.6808 | 0
| 22:30 | 5.0238 | 0
| 23:30 | 5.2528 | 0
Wed, 17/Mar | 0:30 | 5.5438 | 0
| 1:30 | 5.8747 | 0
| 2:30 | 6.0856 | 0
| 3:30 | 6.3638 | 0
| 4:30 | 6.7776 | 0
| 5:30 | 7.1077 | 0
| 6:30 | 7.2966 | 0
| 7:30 | 7.2563 | 0
| 8:30 | 6.9519 | 0
| 9:30 | 6.5483 | 0
| 10:30 | 6.1194 | 0
| 11:30 | 5.7596 | 0
| 12:30 | 5.6024 | 0
| 13:30 | 5.6123 | 0
| 14:30 | 5.6382 | 0
| 15:30 | 5.7922 | 0
| 16:30 | 6.0522 | 0
| 17:30 | 6.2242 | 0
| 18:30 | 6.447 | 0
| 19:30 | 6.7632 | 0
| 20:30 | 6.9861 | 0
| 21:30 | 7.1073 | 0
| 22:30 | 7.3037 | 0
| 23:30 | 7.4884 | 0
Thu, 18/Mar | 0:30 | 7.5921 | 0
| 1:30 | 7.711 | 0
| 2:30 | 7.8078 | 0
| 3:30 | 7.8826 | 0
| 4:30 | 7.9925 | 0
| 5:30 | 8.1009 | 0
| 6:30 | 8.2038 | 0
| 7:30 | 8.318 | 0
| 8:30 | 509.6267 | 0
| 9:30 | 88.7835 | 0
| 10:30 | 62.5849 | 0
| 11:30 | 49.3003 | 0
| 12:30 | 40.2159 | 0
| 13:30 | 35.299 | 0
| 14:30 | 31.2606 | 0
| 15:30 | 28.1602 | 0
| 16:30 | 26.7599 | 0
| 17:30 | 25.0157 | 0
| 18:30 | 2.37 | 0
| 19:30 | 2.4898 | 0
| 20:30 | 2.3524 | 0
| 21:30 | 2.5621 | 0
| 22:30 | 2.6735 | 0
| 23:30 | 2.7535 | 0
Fri, 19/Mar | 0:30 | 2.9213 | 0
| 1:30 | 3.1808 | 0
| 2:30 | 3.2787 | 0
| 3:30 | 3.3682 | 0
| 4:30 | 3.5065 | 0
| 5:30 | 3.5902 | 0
| 6:30 | 3.6241 | 0
| 7:30 | 3.5737 | 0
| 8:30 | 250.0526 | 0
| 9:30 | 11.3356 | 0
| 10:30 | 7.9308 | 0
| 11:30 | 6.989 | 0
| 12:30 | 6.2433 | 0
| 13:30 | 5.7037 | 0
| 14:30 | 5.5772 | 0
| 15:30 | 5.7766 | 0
| 16:30 | 6.0862 | 0
| 17:30 | 6.5441 | 0
| 18:30 | 0.4159 | 0
| 19:30 | 1.2604 | 0
| 20:30 | 1.8491 | 0
| 21:30 | 2.4556 | 0
| 22:30 | 2.8127 | 0
| 23:30 | 3.0824 | 0
Sat, 20/Mar | 0:30 | 3.4713 | 0
| 1:30 | 3.6327 | 0
| 2:30 | 3.5303 | 0
| 3:30 | 3.5776 | 0
| 4:30 | 3.7106 | 0
| 5:30 | 3.8116 | 0
| 6:30 | 3.9997 | 0
| 7:30 | 3.9651 | 0
| 8:30 | 3.6733 | 0
| 9:30 | 3.4261 | 0
| 10:30 | 3.119 | 0
| 11:30 | 2.8505 | 0
| 12:30 | 2.4768 | 0
| 13:30 | 2.1664 | 0
| 14:30 | 2.023 | 0
| 15:30 | 2.3732 | 0
| 16:30 | 3.0591 | 0
| 17:30 | 3.4944 | 0
| 18:30 | 3.8572 | 0
| 19:30 | 4.193 | 0
| 20:30 | 4.438 | 0
| 21:30 | 4.64 | 0
| 22:30 | 4.8837 | 0
| 23:30 | 4.9899 | 0
Sun, 21/Mar | 0:30 | 5.088 | 0
| 1:30 | 5.2093 | 0
| 2:30 | 5.3401 | 0
| 3:30 | 5.6902 | 0
| 4:30 | 6.0868 | 0
| 5:30 | 6.2783 | 0
| 6:30 | 6.3766 | 0
| 7:30 | 6.3491 | 0
| 8:30 | 5.983 | 0
| 9:30 | 5.4075 | 0
| 10:30 | 4.751 | 0
| 11:30 | 4.1642 | 0
| 12:30 | 3.6601 | 0
| 13:30 | 3.3864 | 0
| 14:30 | 3.1165 | 0
| 15:30 | 2.84 | 0
| 16:30 | 3.5345 | 0
| 17:30 | 4.1976 | 0
| 18:30 | 4.5304 | 0
| 19:30 | 5.0747 | 0
| 20:30 | 5.5706 | 0
| 21:30 | 6.0039 | 0
| 22:30 | 6.3139 | 0
| 23:30 | 6.4489 | 0
Mon, 22/Mar | 0:30 | 6.4484 | 0
| 1:30 | 6.5418 | 0
| 2:30 | 6.6825 | 0
| 3:30 | 6.7745 | 0
| 4:30 | 6.765 | 0
| 5:30 | 6.7322 | 0
| 6:30 | 6.8628 | 0
| 7:30 | 6.956 | 0
| 8:30 | 427.5606 | 0
| 9:30 | 44.7878 | 0
| 10:30 | 18.9128 | 0
| 11:30 | 12.5166 | 0
| 12:30 | 12.2088 | 0
| 13:30 | 11.3409 | 0
| 14:30 | 10.1143 | 0
| 15:30 | 9.6657 | 0
| 16:30 | 9.4621 | 0
| 17:30 | 11.738 | 0
| 18:30 | 1.9492 | 0
| 19:30 | 2.6601 | 0
| 20:30 | 3.2249 | 0
| 21:30 | 3.8122 | 0
| 22:30 | 4.3965 | 0
| 23:30 | 4.7612 | 0
Tue, 23/Mar | 0:30 | 4.9954 | 0
| 1:30 | 5.0871 | 0
| 2:30 | 5.2265 | 0
| 3:30 | 5.3981 | 0
| 4:30 | 5.6152 | 0
| 5:30 | 5.8234 | 0
| 6:30 | 6.1131 | 0
| 7:30 | 6.3255 | 0
| 8:30 | 369.0463 | 0
| 9:30 | 44.5469 | 0
| 10:30 | 24.2164 | 0
| 11:30 | 13.0933 | 0
| 12:30 | 8.5019 | 0
| 13:30 | 6.5003 | 0
| 14:30 | 5.2059 | 0
| 15:30 | 4.5344 | 0
| 16:30 | 7.234 | 0
| 17:30 | 10.9019 | 0
| 18:30 | 1.6812 | 0
| 19:30 | 2.2305 | 0
| 20:30 | 2.472 | 0
| 21:30 | 2.7376 | 0
| 22:30 | 2.9744 | 0
| 23:30 | 3.0778 | 0
Wed, 24/Mar | 0:30 | 3.094 | 0
| 1:30 | 3.0642 | 0
| 2:30 | 3.0399 | 0
| 3:30 | 3.4939 | 0
| 4:30 | 4.1071 | 0
| 5:30 | 4.3557 | 0
| 6:30 | 4.7989 | 0
| 7:30 | 4.9344 | 0
| 8:30 | 294.2288 | 0
| 9:30 | 42.9399 | 0
| 10:30 | 27.6794 | 0
| 11:30 | 18.4736 | 0
| 12:30 | 14.825 | 0
| 13:30 | 10.9483 | 0
| 14:30 | 8.77 | 0
| 15:30 | 8.589 | 0
| 16:30 | 9.6672 | 0
| 17:30 | 11.7465 | 0
| 18:30 | 2.0851 | 0
| 19:30 | 2.8225 | 0
| 20:30 | 3.3479 | 0
| 21:30 | 3.5545 | 0
| 22:30 | 3.7873 | 0
| 23:30 | 4.1573 | 0
Thu, 25/Mar | 0:30 | 4.442 | 0
| 1:30 | 4.8215 | 0
| 2:30 | 5.2451 | 0
| 3:30 | 5.5322 | 0
| 4:30 | 5.7029 | 0
| 5:30 | 5.8823 | 0
| 6:30 | 6.0776 | 0
| 7:30 | 6.0921 | 0
| 8:30 | 330.1475 | 0
| 9:30 | 37.8209 | 0
| 10:30 | 17.321 | 0
| 11:30 | 10.6351 | 0
| 12:30 | 8.5536 | 0
| 13:30 | 7.3376 | 0
| 14:30 | 6.3045 | 0
| 15:30 | 6.7436 | 0
| 16:30 | 8.3184 | 0
| 17:30 | 11.276 | 0
| 18:30 | 2.2079 | 0
| 19:30 | 3.0138 | 0
| 20:30 | 3.5346 | 0
| 21:30 | 3.9969 | 0
| 22:30 | 4.3819 | 0
| 23:30 | 4.684 | 0
Fri, 26/Mar | 0:30 | 4.9076 | 0
| 1:30 | 5.0659 | 0
| 2:30 | 5.1885 | 0
| 3:30 | 5.4475 | 0
| 4:30 | 5.707 | 0
| 5:30 | 5.8625 | 0
| 6:30 | 5.923 | 0
| 7:30 | 5.811 | 0
| 8:30 | 314.0782 | 0
| 9:30 | 33.8363 | 0
| 10:30 | 17.5402 | 0
| 11:30 | 11.906 | 0
| 12:30 | 8.8108 | 0
| 13:30 | 6.5071 | 0
| 14:30 | 4.7366 | 0
| 15:30 | 3.6584 | 0
| 16:30 | 6.7789 | 0
| 17:30 | 9.9215 | 0
| 18:30 | 1.8434 | 0
| 19:30 | 2.8054 | 0
| 20:30 | 3.4757 | 0
| 21:30 | 3.7891 | 0
| 22:30 | 4.005 | 0
| 23:30 | 4.3979 | 0
Sat, 27/Mar | 0:30 | 4.7949 | 0
| 1:30 | 5.1337 | 0
| 2:30 | 5.4442 | 0
| 3:30 | 5.5878 | 0
| 4:30 | 5.705 | 0
| 5:30 | 5.6594 | 0
| 6:30 | 5.6024 | 0
| 7:30 | 5.4618 | 0
| 8:30 | 4.9616 | 0
| 9:30 | 4.3119 | 0
| 10:30 | 3.6996 | 0
| 11:30 | 3.2116 | 0
| 12:30 | 2.965 | 0
| 13:30 | 2.813 | 0
| 14:30 | 2.571 | 0
| 15:30 | 2.5532 | 0
| 16:30 | 2.8569 | 0
| 17:30 | 3.102 | 0
| 18:30 | 3.3945 | 0
| 19:30 | 3.8885 | 0
| 20:30 | 4.1872 | 0
| 21:30 | 4.3828 | 0
| 22:30 | 4.5967 | 0
| 23:30 | 4.7347 | 0
Sun, 28/Mar | 0:30 | 4.8433 | 0
| 1:30 | 5.099 | 0
| 2:30 | 5.3221 | 0
| 3:30 | 5.286 | 0
| 4:30 | 5.4271 | 0
| 5:30 | 5.746 | 0
| 6:30 | 6.0082 | 0
| 7:30 | 5.9775 | 0
| 8:30 | 5.5765 | 0
| 9:30 | 5.0754 | 0
| 10:30 | 4.5939 | 0
| 11:30 | 4.2136 | 0
| 12:30 | 4.0754 | 0
| 13:30 | 3.9512 | 0
| 14:30 | 3.6525 | 0
| 15:30 | 3.586 | 0
| 16:30 | 4.0985 | 0
| 17:30 | 4.6778 | 0
| 18:30 | 5.1279 | 0
| 19:30 | 5.758 | 0
| 20:30 | 6.3136 | 0
| 21:30 | 6.6671 | 0
| 22:30 | 7.0852 | 0
| 23:30 | 7.5083 | 0
Mon, 29/Mar | 0:30 | 7.8659 | 0
| 1:30 | 8.2722 | 0
| 2:30 | 8.5683 | 0
| 3:30 | 8.7618 | 0
| 4:30 | 8.9123 | 0
| 5:30 | 9.1276 | 0
| 6:30 | 9.2941 | 0
| 7:30 | 9.0259 | 0
| 8:30 | 504.7358 | 0
| 9:30 | 62.8894 | 0
| 10:30 | 31.641 | 0
| 11:30 | 17.6269 | 0
| 12:30 | 13.9904 | 0
| 13:30 | 11.0032 | 0
| 14:30 | 7.7651 | 0
| 15:30 | 7.2177 | 0
| 16:30 | 8.7626 | 0
| 17:30 | 11.5952 | 0
| 18:30 | 2.2154 | 0
| 19:30 | 3.3043 | 0
| 20:30 | 3.8818 | 0
| 21:30 | 4.5714 | 0
| 22:30 | 5.0612 | 0
| 23:30 | 5.3328 | 0
Tue, 30/Mar | 0:30 | 5.7345 | 0
| 1:30 | 5.9744 | 0
| 2:30 | 6.1303 | 0
| 3:30 | 6.3683 | 0
| 4:30 | 6.6125 | 0
| 5:30 | 6.746 | 0
| 6:30 | 6.877 | 0
| 7:30 | 6.8351 | 0
| 8:30 | 388.1849 | 0
| 9:30 | 44.6259 | 0
| 10:30 | 22.7757 | 0
| 11:30 | 13.5454 | 0
| 12:30 | 9.1803 | 0
| 13:30 | 6.2428 | 0
| 14:30 | 3.9089 | 0
| 15:30 | 3.5245 | 0
| 16:30 | 6.4756 | 0
| 17:30 | 11.3053 | 0
| 18:30 | 1.9095 | 0
| 19:30 | 3.0132 | 0
| 20:30 | 3.773 | 0
| 21:30 | 4.2312 | 0
| 22:30 | 4.651 | 0
| 23:30 | 4.9452 | 0
Wed, 31/Mar | 0:30 | 5.1998 | 0
| 1:30 | 5.5086 | 0
| 2:30 | 5.8805 | 0
| 3:30 | 6.0735 | 0
| 4:30 | 6.3115 | 0
| 5:30 | 6.5587 | 0
| 6:30 | 6.5659 | 0
| 7:30 | 6.3908 | 0
| 8:30 | 362.5009 | 0
| 9:30 | 42.437 | 0
| 10:30 | 19.9958 | 0
| 11:30 | 13.5044 | 0
| 12:30 | 9.5844 | 0
| 13:30 | 6.4051 | 0
| 14:30 | 2.9981 | 0
| 15:30 | 1.9939 | 0
| 16:30 | 4.3504 | 0
| 17:30 | 7.2698 | 0
| 18:30 | 1.1919 | 0
| 19:30 | 2.1805 | 0
| 20:30 | 2.8819 | 0
| 21:30 | 3.3818 | 0
| 22:30 | 3.6429 | 0
| 23:30 | 3.7546 | 0
Thu, 01/Apr | 0:30 | 3.7993 | 0
| 1:30 | 3.7358 | 0
| 2:30 | 3.4319 | 0
| 3:30 | 3.1179 | 0
| 4:30 | 2.8777 | 0
| 5:30 | 2.7512 | 0
| 6:30 | 2.709 | 0
| 7:30 | 2.6743 | 0
| 8:30 | 198.1625 | 0
| 9:30 | 9.0418 | 0
| 10:30 | 5.6742 | 0
| 11:30 | 3.8864 | 0
| 12:30 | 3.6076 | 0
| 13:30 | 3.6477 | 0
| 14:30 | 3.319 | 0
| 15:30 | 2.6406 | 0
| 16:30 | 2.6053 | 0
| 17:30 | 3.5623 | 0
| 18:30 | 0.0364 | 0
| 19:30 | 0.5273 | 0
| 20:30 | 1.3237 | 0
| 21:30 | 1.7016 | 0
| 22:30 | 2.134 | 0
| 23:30 | 2.634 | 0
Fri, 02/Apr | 0:30 | 2.8861 | 0
| 1:30 | 3.116 | 0
| 2:30 | 3.4319 | 0
| 3:30 | 3.6286 | 0
| 4:30 | 3.882 | 0
| 5:30 | 4.0425 | 0
| 6:30 | 3.9539 | 0
| 7:30 | 3.8974 | 0
| 8:30 | 241.2491 | 0
| 9:30 | 17.5975 | 0
| 10:30 | 9.6769 | 0
| 11:30 | 9.4339 | 0
| 12:30 | 8.7093 | 0
| 13:30 | 7.3211 | 0
| 14:30 | 5.7083 | 0
| 15:30 | 4.1331 | 0
| 16:30 | 3.8848 | 0
| 17:30 | 3.1517 | 0
| 18:30 | 0.0411 | 0
| 19:30 | 0.3331 | 0
| 20:30 | 0.8949 | 0
| 21:30 | 1.5265 | 0
| 22:30 | 2.1137 | 0
| 23:30 | 2.3054 | 0
Sat, 03/Apr | 0:30 | 2.3055 | 0
| 1:30 | 2.5204 | 0
| 2:30 | 2.6158 | 0
| 3:30 | 2.2604 | 0
| 4:30 | 2.1186 | 0
| 5:30 | 2.333 | 0
| 6:30 | 2.433 | 0
| 7:30 | 2.5645 | 0
| 8:30 | 2.5072 | 0
| 9:30 | 2.0871 | 0
| 10:30 | 1.7074 | 0
| 11:30 | 1.4027 | 0
| 12:30 | 1.0733 | 0
| 13:30 | 0.9238 | 0
| 14:30 | 0.9167 | 0
| 15:30 | 0.8608 | 0
| 16:30 | 0.8358 | 0
| 17:30 | 0.9707 | 0
| 18:30 | 1.2624 | 0
| 19:30 | 1.5688 | 0
| 20:30 | 1.9564 | 0
| 21:30 | 2.2845 | 0
| 22:30 | 2.6582 | 0
| 23:30 | 2.9255 | 0
Sun, 04/Apr | 0:30 | 3.0268 | 0
| 1:30 | 3.3368 | 0
| 2:30 | 3.6176 | 0
| 3:30 | 3.8233 | 0
| 4:30 | 3.9877 | 0
| 5:30 | 4.1835 | 0
| 6:30 | 4.1647 | 0
| 7:30 | 4.1003 | 0
| 8:30 | 4.2538 | 0
| 9:30 | 4.2571 | 0
| 10:30 | 4.2465 | 0
| 11:30 | 4.2412 | 0
| 12:30 | 4.1026 | 0
| 13:30 | 3.9736 | 0
| 14:30 | 3.9496 | 0
| 15:30 | 3.9431 | 0
| 16:30 | 3.9848 | 0
| 17:30 | 4.1376 | 0
| 18:30 | 4.2348 | 0
| 19:30 | 4.2865 | 0
| 20:30 | 4.4095 | 0
| 21:30 | 4.5589 | 0
| 22:30 | 4.5709 | 0
| 23:30 | 4.4957 | 0
Mon, 05/Apr | 0:30 | 4.502 | 0
| 1:30 | 4.6381 | 0
| 2:30 | 4.6954 | 0
| 3:30 | 4.6906 | 0
| 4:30 | 4.8143 | 0
| 5:30 | 4.9199 | 0
| 6:30 | 4.9633 | 0
| 7:30 | 5.0242 | 0
| 8:30 | 339.5613 | 0
| 9:30 | 25.465 | 0
| 10:30 | 10.0224 | 0
| 11:30 | 7.5688 | 0
| 12:30 | 5.7569 | 0
| 13:30 | 5.1053 | 0
| 14:30 | 5.5946 | 0
| 15:30 | 5.072 | 0
| 16:30 | 4.2829 | 0
| 17:30 | 5.762 | 0
| 18:30 | 0.8823 | 0
| 19:30 | 1.5874 | 0
| 20:30 | 2.0891 | 0
| 21:30 | 2.6275 | 0
| 22:30 | 3.2245 | 0
| 23:30 | 3.8942 | 0
Tue, 06/Apr | 0:30 | 4.2675 | 0
| 1:30 | 4.5871 | 0
| 2:30 | 4.7986 | 0
| 3:30 | 4.8392 | 0
| 4:30 | 4.9631 | 0
| 5:30 | 4.9868 | 0
| 6:30 | 4.877 | 0
| 7:30 | 4.8883 | 0
| 8:30 | 310.4039 | 0
| 9:30 | 30.5609 | 0
| 10:30 | 13.1605 | 0
| 11:30 | 8.6827 | 0
| 12:30 | 5.2837 | 0
| 13:30 | 2.6883 | 0
| 14:30 | 0.548 | 0
| 15:30 | 0.0096 | 0
| 16:30 | 1.9859 | 0
| 17:30 | 4.3675 | 0
| 18:30 | 0.2509 | 0
| 19:30 | 0.926 | 0
| 20:30 | 1.6135 | 0
| 21:30 | 2.2606 | 0
| 22:30 | 2.7955 | 0
| 23:30 | 3.3619 | 0
Wed, 07/Apr | 0:30 | 3.674 | 0
| 1:30 | 4.0159 | 0
| 2:30 | 4.3274 | 0
| 3:30 | 4.3169 | 0
| 4:30 | 4.297 | 0
| 5:30 | 4.3983 | 0
| 6:30 | 4.5098 | 0
| 7:30 | 4.6271 | 0
| 8:30 | 290.01 | 0
| 9:30 | 41.0234 | 0
| 10:30 | 28.4096 | 0
| 11:30 | 22.4418 | 0
| 12:30 | 17.2456 | 0
| 13:30 | 14.0056 | 0
| 14:30 | 10.974 | 0
| 15:30 | 9.1014 | 0
| 16:30 | 9.4354 | 0
| 17:30 | 10.2733 | 0
| 18:30 | 1.6852 | 0
| 19:30 | 2.3179 | 0
| 20:30 | 2.9179 | 0
| 21:30 | 3.2987 | 0
| 22:30 | 3.5227 | 0
| 23:30 | 3.7402 | 0
Thu, 08/Apr | 0:30 | 3.9934 | 0
| 1:30 | 4.1772 | 0
| 2:30 | 4.3807 | 0
| 3:30 | 4.487 | 0
| 4:30 | 4.5933 | 0
| 5:30 | 4.751 | 0
| 6:30 | 4.8442 | 0
| 7:30 | 4.9113 | 0
| 8:30 | 292.3258 | 0
| 9:30 | 39.758 | 0
| 10:30 | 23.9661 | 0
| 11:30 | 16.023 | 0
| 12:30 | 11.3479 | 0
| 13:30 | 7.7475 | 0
| 14:30 | 3.5503 | 0
| 15:30 | 0.7064 | 0
| 16:30 | 0.3615 | 0
| 17:30 | 1.2071 | 0
| 18:30 | 0.5317 | 0
| 19:30 | 1.3495 | 0
| 20:30 | 2.0205 | 0
| 21:30 | 2.9164 | 0
| 22:30 | 3.478 | 0
| 23:30 | 4.0216 | 0
Fri, 09/Apr | 0:30 | 4.4558 | 0
| 1:30 | 4.8652 | 0
| 2:30 | 5.1927 | 0
| 3:30 | 5.3151 | 0
| 4:30 | 5.3974 | 0
| 5:30 | 5.4653 | 0
| 6:30 | 5.5303 | 0
| 7:30 | 5.5062 | 0
| 8:30 | 307.8673 | 0
| 9:30 | 35.2499 | 0
| 10:30 | 15.5707 | 0
| 11:30 | 9.5729 | 0
| 12:30 | 5.7147 | 0
| 13:30 | 3.2721 | 0
| 14:30 | 2.4014 | 0
| 15:30 | 2.3346 | 0
| 16:30 | 3.827 | 0
| 17:30 | 6.185 | 0
| 18:30 | 0.5748 | 0
| 19:30 | 1.4864 | 0
| 20:30 | 2.3049 | 0
| 21:30 | 2.763 | 0
| 22:30 | 3.1913 | 0
| 23:30 | 3.6074 | 0
Sat, 10/Apr | 0:30 | 3.8475 | 0
| 1:30 | 4.3842 | 0
| 2:30 | 4.8181 | 0
| 3:30 | 4.8421 | 0
| 4:30 | 4.8883 | 0
| 5:30 | 4.9789 | 0
| 6:30 | 4.9611 | 0
| 7:30 | 4.9261 | 0
| 8:30 | 4.8692 | 0
| 9:30 | 4.5685 | 0
| 10:30 | 4.1318 | 0
| 11:30 | 3.8686 | 0
| 12:30 | 3.6055 | 0
| 13:30 | 3.3366 | 0
| 14:30 | 3.071 | 0
| 15:30 | 2.6742 | 0
| 16:30 | 2.459 | 0
| 17:30 | 2.5418 | 0
| 18:30 | 2.7091 | 0
| 19:30 | 2.9634 | 0
| 20:30 | 3.308 | 0
| 21:30 | 3.6253 | 0
| 22:30 | 4.0196 | 0
| 23:30 | 4.321 | 0
Sun, 11/Apr | 0:30 | 4.3939 | 0
| 1:30 | 4.5824 | 0
| 2:30 | 4.8418 | 0
| 3:30 | 4.951 | 0
| 4:30 | 5.1701 | 0
| 5:30 | 5.6155 | 0
| 6:30 | 5.9411 | 0
| 7:30 | 6.1386 | 0
| 8:30 | 6.3445 | 0
| 9:30 | 6.4523 | 0
| 10:30 | 6.3243 | 0
| 11:30 | 6.0592 | 0
| 12:30 | 6.0917 | 0
| 13:30 | 5.7174 | 0
| 14:30 | 5.1199 | 0
| 15:30 | 4.8151 | 0
| 16:30 | 4.5682 | 0
| 17:30 | 4.7416 | 0
| 18:30 | 5.2091 | 0
| 19:30 | 5.7413 | 0
| 20:30 | 6.2758 | 0
| 21:30 | 6.76 | 0
| 22:30 | 7.2619 | 0
| 23:30 | 7.6428 | 0
Mon, 12/Apr | 0:30 | 7.8951 | 0
| 1:30 | 8.2455 | 0
| 2:30 | 8.5974 | 0
| 3:30 | 8.8811 | 0
| 4:30 | 9.1775 | 0
| 5:30 | 9.4354 | 0
| 6:30 | 9.6149 | 0
| 7:30 | 9.4134 | 0
| 8:30 | 8.9145 | 0
| 9:30 | 8.4356 | 0
| 10:30 | 7.8927 | 0
| 11:30 | 7.5275 | 0
| 12:30 | 7.1127 | 0
| 13:30 | 6.5101 | 0
| 14:30 | 5.8396 | 0
| 15:30 | 5.2616 | 0
| 16:30 | 4.9545 | 0
| 17:30 | 4.8705 | 0
| 18:30 | 5.0109 | 0
| 19:30 | 5.4726 | 0
| 20:30 | 6.4053 | 0
| 21:30 | 7.1222 | 0
| 22:30 | 7.6494 | 0
| 23:30 | 8.0988 | 0
Tue, 13/Apr | 0:30 | 8.3663 | 0
| 1:30 | 8.6917 | 0
| 2:30 | 8.9346 | 0
| 3:30 | 9.1253 | 0
| 4:30 | 9.3777 | 0
| 5:30 | 9.6113 | 0
| 6:30 | 9.7238 | 0
| 7:30 | 9.7278 | 0
| 8:30 | 592.7491 | 0
| 9:30 | 91.4973 | 0
| 10:30 | 54.9589 | 0
| 11:30 | 37.4333 | 0
| 12:30 | 29.2734 | 0
| 13:30 | 26.265 | 0
| 14:30 | 18.8468 | 0
| 15:30 | 13.1855 | 0
| 16:30 | 13.254 | 0
| 17:30 | 15.0091 | 0
| 18:30 | 2.1248 | 0
| 19:30 | 2.8429 | 0
| 20:30 | 3.48 | 0
| 21:30 | 4.078 | 0
| 22:30 | 4.4422 | 0
| 23:30 | 4.8387 | 0
Wed, 14/Apr | 0:30 | 5.2464 | 0
| 1:30 | 5.7119 | 0
| 2:30 | 6.2055 | 0
| 3:30 | 6.5617 | 0
| 4:30 | 6.922 | 0
| 5:30 | 7.2931 | 0
| 6:30 | 7.434 | 0
| 7:30 | 7.3894 | 0
| 8:30 | 439.2906 | 0
| 9:30 | 55.3266 | 0
| 10:30 | 24.2768 | 0
| 11:30 | 14.6652 | 0
| 12:30 | 9.6434 | 0
| 13:30 | 6.1832 | 0
| 14:30 | 3.1361 | 0
| 15:30 | 1.6502 | 0
| 16:30 | 1.5458 | 0
| 17:30 | 4.479 | 0
| 18:30 | 1.1929 | 0
| 19:30 | 1.8634 | 0
| 20:30 | 2.5526 | 0
| 21:30 | 3.0711 | 0
| 22:30 | 3.4895 | 0
| 23:30 | 4.1475 | 0
Thu, 15/Apr | 0:30 | 4.6503 | 0
| 1:30 | 4.8268 | 0
| 2:30 | 4.9131 | 0
| 3:30 | 4.9641 | 0
| 4:30 | 5.1537 | 0
| 5:30 | 5.4201 | 0
| 6:30 | 5.3936 | 0
| 7:30 | 5.0406 | 0
| 8:30 | 304.6899 | 0
| 9:30 | 16.7396 | 0
| 10:30 | 8.5831 | 0
| 11:30 | 5.2942 | 0
| 12:30 | 2.1849 | 0
| 13:30 | 0.1597 | 0
| 14:30 | 0.0152 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0761 | 0
| 21:30 | 0.3633 | 0
| 22:30 | 0.8183 | 0
| 23:30 | 1.1985 | 0
Fri, 16/Apr | 0:30 | 1.3619 | 0
| 1:30 | 1.6414 | 0
| 2:30 | 2.1054 | 0
| 3:30 | 2.3817 | 0
| 4:30 | 2.5124 | 0
| 5:30 | 2.6486 | 0
| 6:30 | 2.7744 | 0
| 7:30 | 2.6913 | 0
| 8:30 | 186.4968 | 0
| 9:30 | 6.3604 | 0
| 10:30 | 3.6127 | 0
| 11:30 | 2.0382 | 0
| 12:30 | 0.8486 | 0
| 13:30 | 0.0569 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0345 | 0
| 22:30 | 0.3358 | 0
| 23:30 | 0.9191 | 0
Sat, 17/Apr | 0:30 | 1.2153 | 0
| 1:30 | 1.5059 | 0
| 2:30 | 1.7766 | 0
| 3:30 | 1.9548 | 0
| 4:30 | 2.0984 | 0
| 5:30 | 2.2506 | 0
| 6:30 | 2.3531 | 0
| 7:30 | 2.343 | 0
| 8:30 | 2.1214 | 0
| 9:30 | 1.5727 | 0
| 10:30 | 1.0491 | 0
| 11:30 | 0.8004 | 0
| 12:30 | 0.8198 | 0
| 13:30 | 1.0074 | 0
| 14:30 | 1.0326 | 0
| 15:30 | 0.8785 | 0
| 16:30 | 0.7536 | 0
| 17:30 | 0.7058 | 0
| 18:30 | 0.8541 | 0
| 19:30 | 1.2762 | 0
| 20:30 | 1.82 | 0
| 21:30 | 2.0611 | 0
| 22:30 | 2.4509 | 0
| 23:30 | 3.1727 | 0
Sun, 18/Apr | 0:30 | 3.4764 | 0
| 1:30 | 3.5919 | 0
| 2:30 | 3.7875 | 0
| 3:30 | 4.0405 | 0
| 4:30 | 4.3483 | 0
| 5:30 | 4.6713 | 0
| 6:30 | 4.898 | 0
| 7:30 | 4.9028 | 0
| 8:30 | 4.3549 | 0
| 9:30 | 3.5304 | 0
| 10:30 | 2.9061 | 0
| 11:30 | 2.4511 | 0
| 12:30 | 1.9831 | 0
| 13:30 | 1.5561 | 0
| 14:30 | 1.3683 | 0
| 15:30 | 1.2537 | 0
| 16:30 | 1.2508 | 0
| 17:30 | 1.4658 | 0
| 18:30 | 1.5886 | 0
| 19:30 | 1.9366 | 0
| 20:30 | 2.6454 | 0
| 21:30 | 3.039 | 0
| 22:30 | 3.4707 | 0
| 23:30 | 3.8612 | 0
Mon, 19/Apr | 0:30 | 3.7455 | 0
| 1:30 | 3.7306 | 0
| 2:30 | 4.0264 | 0
| 3:30 | 4.1076 | 0
| 4:30 | 4.2282 | 0
| 5:30 | 4.5554 | 0
| 6:30 | 4.5725 | 0
| 7:30 | 4.39 | 0
| 8:30 | 298.7014 | 0
| 9:30 | 20.0592 | 0
| 10:30 | 8.7868 | 0
| 11:30 | 5.0323 | 0
| 12:30 | 3.3449 | 0
| 13:30 | 2.6944 | 0
| 14:30 | 1.8568 | 0
| 15:30 | 1.8241 | 0
| 16:30 | 2.9088 | 0
| 17:30 | 4.3015 | 0
| 18:30 | 0.2835 | 0
| 19:30 | 1.2592 | 0
| 20:30 | 1.9316 | 0
| 21:30 | 2.4658 | 0
| 22:30 | 3.1172 | 0
| 23:30 | 3.8171 | 0
Tue, 20/Apr | 0:30 | 4.2986 | 0
| 1:30 | 4.666 | 0
| 2:30 | 5.0832 | 0
| 3:30 | 5.4192 | 0
| 4:30 | 5.8408 | 0
| 5:30 | 6.2087 | 0
| 6:30 | 6.4461 | 0
| 7:30 | 6.3384 | 0
| 8:30 | 357.4237 | 0
| 9:30 | 45.1559 | 0
| 10:30 | 22.8335 | 0
| 11:30 | 16.6493 | 0
| 12:30 | 12.1987 | 0
| 13:30 | 8.9386 | 0
| 14:30 | 7.3371 | 0
| 15:30 | 5.8735 | 0
| 16:30 | 6.9711 | 0
| 17:30 | 9.0991 | 0
| 18:30 | 2.0313 | 0
| 19:30 | 2.512 | 0
| 20:30 | 3.2775 | 0
| 21:30 | 3.835 | 0
| 22:30 | 4.2678 | 0
| 23:30 | 4.6724 | 0
Wed, 21/Apr | 0:30 | 4.8818 | 0
| 1:30 | 5.1154 | 0
| 2:30 | 5.4519 | 0
| 3:30 | 5.6392 | 0
| 4:30 | 5.7511 | 0
| 5:30 | 5.9451 | 0
| 6:30 | 5.9679 | 0
| 7:30 | 5.8253 | 0
| 8:30 | 340.5911 | 0
| 9:30 | 47.0447 | 0
| 10:30 | 27.321 | 0
| 11:30 | 18.5797 | 0
| 12:30 | 11.9148 | 0
| 13:30 | 8.583 | 0
| 14:30 | 7.8652 | 0
| 15:30 | 5.5577 | 0
| 16:30 | 6.509 | 0
| 17:30 | 9.6979 | 0
| 18:30 | 1.7846 | 0
| 19:30 | 2.365 | 0
| 20:30 | 3.022 | 0
| 21:30 | 3.3134 | 0
| 22:30 | 3.5428 | 0
| 23:30 | 3.7159 | 0
Thu, 22/Apr | 0:30 | 3.91 | 0
| 1:30 | 4.1129 | 0
| 2:30 | 4.2978 | 0
| 3:30 | 4.4659 | 0
| 4:30 | 4.7206 | 0
| 5:30 | 4.9758 | 0
| 6:30 | 4.9742 | 0
| 7:30 | 4.8765 | 0
| 8:30 | 281.6158 | 0
| 9:30 | 27.5149 | 0
| 10:30 | 15.2785 | 0
| 11:30 | 12.372 | 0
| 12:30 | 10.5393 | 0
| 13:30 | 8.4932 | 0
| 14:30 | 5.2614 | 0
| 15:30 | 1.7514 | 0
| 16:30 | 1.4213 | 0
| 17:30 | 3.4585 | 0
| 18:30 | 1.2897 | 0
| 19:30 | 1.8759 | 0
| 20:30 | 2.6353 | 0
| 21:30 | 3.1533 | 0
| 22:30 | 3.348 | 0
| 23:30 | 3.601 | 0
Fri, 23/Apr | 0:30 | 3.5818 | 0
| 1:30 | 3.5845 | 0
| 2:30 | 3.7827 | 0
| 3:30 | 3.9005 | 0
| 4:30 | 4.1082 | 0
| 5:30 | 4.4723 | 0
| 6:30 | 4.5653 | 0
| 7:30 | 4.5722 | 0
| 8:30 | 261.961 | 0
| 9:30 | 27.5376 | 0
| 10:30 | 15.8584 | 0
| 11:30 | 13.2389 | 0
| 12:30 | 10.6477 | 0
| 13:30 | 9.3352 | 0
| 14:30 | 8.3744 | 0
| 15:30 | 4.3953 | 0
| 16:30 | 1.9505 | 0
| 17:30 | 4.395 | 0
| 18:30 | 1.7373 | 0
| 19:30 | 2.2735 | 0
| 20:30 | 3.1083 | 0
| 21:30 | 3.7517 | 0
| 22:30 | 4.1361 | 0
| 23:30 | 4.3904 | 0
Sat, 24/Apr | 0:30 | 4.4595 | 0
| 1:30 | 4.5495 | 0
| 2:30 | 4.8138 | 0
| 3:30 | 5.007 | 0
| 4:30 | 5.3392 | 0
| 5:30 | 5.8788 | 0
| 6:30 | 6.1974 | 0
| 7:30 | 5.9527 | 0
| 8:30 | 5.3354 | 0
| 9:30 | 4.6199 | 0
| 10:30 | 3.8107 | 0
| 11:30 | 3.1906 | 0
| 12:30 | 2.7109 | 0
| 13:30 | 2.1863 | 0
| 14:30 | 1.829 | 0
| 15:30 | 1.5981 | 0
| 16:30 | 1.4214 | 0
| 17:30 | 1.3042 | 0
| 18:30 | 1.2976 | 0
| 19:30 | 1.627 | 0
| 20:30 | 2.2827 | 0
| 21:30 | 2.7746 | 0
| 22:30 | 3.1284 | 0
| 23:30 | 3.4369 | 0
Sun, 25/Apr | 0:30 | 3.6018 | 0
| 1:30 | 3.8948 | 0
| 2:30 | 4.226 | 0
| 3:30 | 4.464 | 0
| 4:30 | 4.74 | 0
| 5:30 | 5.0328 | 0
| 6:30 | 5.1783 | 0
| 7:30 | 5.1927 | 0
| 8:30 | 5.0195 | 0
| 9:30 | 4.4804 | 0
| 10:30 | 4.0974 | 0
| 11:30 | 3.9416 | 0
| 12:30 | 3.6326 | 0
| 13:30 | 3.3345 | 0
| 14:30 | 3.1161 | 0
| 15:30 | 3.0149 | 0
| 16:30 | 3.1248 | 0
| 17:30 | 3.301 | 0
| 18:30 | 3.6169 | 0
| 19:30 | 4.2866 | 0
| 20:30 | 4.9535 | 0
| 21:30 | 5.4256 | 0
| 22:30 | 5.7884 | 0
| 23:30 | 6.1249 | 0
Mon, 26/Apr | 0:30 | 6.3168 | 0
| 1:30 | 6.4725 | 0
| 2:30 | 6.6509 | 0
| 3:30 | 6.755 | 0
| 4:30 | 6.9292 | 0
| 5:30 | 7.196 | 0
| 6:30 | 7.3137 | 0
| 7:30 | 7.1297 | 0
| 8:30 | 415.1795 | 0
| 9:30 | 45.0533 | 0
| 10:30 | 19.342 | 0
| 11:30 | 11.6618 | 0
| 12:30 | 8.1 | 0
| 13:30 | 4.7552 | 0
| 14:30 | 2.374 | 0
| 15:30 | 2.0399 | 0
| 16:30 | 2.6636 | 0
| 17:30 | 3.063 | 0
| 18:30 | 0.0964 | 0
| 19:30 | 0.8368 | 0
| 20:30 | 1.6847 | 0
| 21:30 | 2.4717 | 0
| 22:30 | 3.1121 | 0
| 23:30 | 3.491 | 0
Tue, 27/Apr | 0:30 | 3.6495 | 0
| 1:30 | 3.9704 | 0
| 2:30 | 4.3348 | 0
| 3:30 | 4.6999 | 0
| 4:30 | 5.0193 | 0
| 5:30 | 5.2576 | 0
| 6:30 | 5.3855 | 0
| 7:30 | 5.3943 | 0
| 8:30 | 322.7587 | 0
| 9:30 | 29.5516 | 0
| 10:30 | 14.9322 | 0
| 11:30 | 10.5829 | 0
| 12:30 | 9.5106 | 0
| 13:30 | 9.001 | 0
| 14:30 | 6.6928 | 0
| 15:30 | 6.282 | 0
| 16:30 | 5.7327 | 0
| 17:30 | 7.297 | 0
| 18:30 | 2.0408 | 0
| 19:30 | 2.6342 | 0
| 20:30 | 3.6413 | 0
| 21:30 | 4.3515 | 0
| 22:30 | 5.0909 | 0
| 23:30 | 5.8679 | 0
Wed, 28/Apr | 0:30 | 6.2154 | 0
| 1:30 | 6.6704 | 0
| 2:30 | 7.2348 | 0
| 3:30 | 7.6266 | 0
| 4:30 | 7.8658 | 0
| 5:30 | 8.1234 | 0
| 6:30 | 8.1756 | 0
| 7:30 | 7.8563 | 0
| 8:30 | 421.9622 | 0
| 9:30 | 64.5215 | 0
| 10:30 | 37.2302 | 0
| 11:30 | 27.8032 | 0
| 12:30 | 23.291 | 0
| 13:30 | 21.6799 | 0
| 14:30 | 20.4902 | 0
| 15:30 | 18.4474 | 0
| 16:30 | 15.9549 | 0
| 17:30 | 13.207 | 0
| 18:30 | 1.7545 | 0
| 19:30 | 1.9644 | 0
| 20:30 | 2.2574 | 0
| 21:30 | 2.3875 | 0
| 22:30 | 2.5544 | 0
| 23:30 | 2.7788 | 0
Thu, 29/Apr | 0:30 | 2.9032 | 0
| 1:30 | 3.0176 | 0
| 2:30 | 3.1867 | 0
| 3:30 | 3.2999 | 0
| 4:30 | 3.4027 | 0
| 5:30 | 3.5117 | 0
| 6:30 | 3.5652 | 0
| 7:30 | 3.5794 | 0
| 8:30 | 229.0695 | 0
| 9:30 | 17.4866 | 0
| 10:30 | 9.4861 | 0
| 11:30 | 7.1618 | 0
| 12:30 | 5.7068 | 0
| 13:30 | 4.4779 | 0
| 14:30 | 4.0286 | 0
| 15:30 | 3.7133 | 0
| 16:30 | 3.5693 | 0
| 17:30 | 3.8519 | 0
| 18:30 | 0.1034 | 0
| 19:30 | 0.5193 | 0
| 20:30 | 1.0804 | 0
| 21:30 | 1.4924 | 0
| 22:30 | 1.907 | 0
| 23:30 | 2.2473 | 0
Fri, 30/Apr | 0:30 | 2.4194 | 0
| 1:30 | 2.5979 | 0
| 2:30 | 2.8159 | 0
| 3:30 | 3.0377 | 0
| 4:30 | 3.1848 | 0
| 5:30 | 3.2561 | 0
| 6:30 | 3.3704 | 0
| 7:30 | 3.5026 | 0
| 8:30 | 204.3574 | 0
| 9:30 | 12.6343 | 0
| 10:30 | 6.6978 | 0
| 11:30 | 3.9807 | 0
| 12:30 | 2.5174 | 0
| 13:30 | 1.2888 | 0
| 14:30 | 0.6556 | 0
| 15:30 | 0.6739 | 0
| 16:30 | 2.0697 | 0
| 17:30 | 3.5268 | 0
| 18:30 | 0.0256 | 0
| 19:30 | 0.5486 | 0
| 20:30 | 1.4063 | 0
| 21:30 | 2.0761 | 0
| 22:30 | 2.6947 | 0
| 23:30 | 3.0883 | 0
Sat, 01/May | 0:30 | 3.2849 | 0
| 1:30 | 3.3385 | 0
| 2:30 | 3.3434 | 0
| 3:30 | 3.4431 | 0
| 4:30 | 3.6185 | 0
| 5:30 | 3.8812 | 0
| 6:30 | 4.1683 | 0
| 7:30 | 4.3106 | 0
| 8:30 | 4.2129 | 0
| 9:30 | 3.8125 | 0
| 10:30 | 3.3051 | 0
| 11:30 | 3.1861 | 0
| 12:30 | 2.9201 | 0
| 13:30 | 2.5067 | 0
| 14:30 | 2.5765 | 0
| 15:30 | 2.5299 | 0
| 16:30 | 2.5977 | 0
| 17:30 | 2.9336 | 0
| 18:30 | 2.9462 | 0
| 19:30 | 3.2299 | 0
| 20:30 | 3.8989 | 0
| 21:30 | 4.5054 | 0
| 22:30 | 5.0453 | 0
| 23:30 | 5.6185 | 0
Sun, 02/May | 0:30 | 6.0189 | 0
| 1:30 | 6.066 | 0
| 2:30 | 6.0886 | 0
| 3:30 | 6.0694 | 0
| 4:30 | 6.0043 | 0
| 5:30 | 6.0576 | 0
| 6:30 | 5.9628 | 0
| 7:30 | 5.8299 | 0
| 8:30 | 5.4598 | 0
| 9:30 | 4.9687 | 0
| 10:30 | 4.5444 | 0
| 11:30 | 4.0077 | 0
| 12:30 | 3.5412 | 0
| 13:30 | 3.2777 | 0
| 14:30 | 3.3552 | 0
| 15:30 | 3.3385 | 0
| 16:30 | 3.3527 | 0
| 17:30 | 4.1967 | 0
| 18:30 | 4.8309 | 0
| 19:30 | 4.9104 | 0
| 20:30 | 5.3563 | 0
| 21:30 | 5.9105 | 0
| 22:30 | 6.3059 | 0
| 23:30 | 6.7339 | 0
Mon, 03/May | 0:30 | 6.9627 | 0
| 1:30 | 7.1605 | 0
| 2:30 | 7.4837 | 0
| 3:30 | 7.6592 | 0
| 4:30 | 7.967 | 0
| 5:30 | 8.2776 | 0
| 6:30 | 8.2569 | 0
| 7:30 | 8.0091 | 0
| 8:30 | 7.4542 | 0
| 9:30 | 6.6439 | 0
| 10:30 | 5.863 | 0
| 11:30 | 5.3417 | 0
| 12:30 | 5.0068 | 0
| 13:30 | 4.566 | 0
| 14:30 | 4.2547 | 0
| 15:30 | 4.1502 | 0
| 16:30 | 4.4182 | 0
| 17:30 | 4.6549 | 0
| 18:30 | 4.598 | 0
| 19:30 | 4.9163 | 0
| 20:30 | 5.7602 | 0
| 21:30 | 6.8259 | 0
| 22:30 | 7.5811 | 0
| 23:30 | 8.1405 | 0
Tue, 04/May | 0:30 | 8.6472 | 0
| 1:30 | 9.1049 | 0
| 2:30 | 9.5313 | 0
| 3:30 | 9.7797 | 0
| 4:30 | 9.9819 | 0
| 5:30 | 10.3077 | 0
| 6:30 | 10.4447 | 0
| 7:30 | 10.1218 | 0
| 8:30 | 579.1728 | 0
| 9:30 | 82.8823 | 0
| 10:30 | 43.0263 | 0
| 11:30 | 26.6355 | 0
| 12:30 | 16.1309 | 0
| 13:30 | 10.7896 | 0
| 14:30 | 9.8562 | 0
| 15:30 | 11.281 | 0
| 16:30 | 12.9081 | 0
| 17:30 | 16.8621 | 0
| 18:30 | 2.9277 | 0
| 19:30 | 4.1494 | 0
| 20:30 | 5.0108 | 0
| 21:30 | 5.8055 | 0
| 22:30 | 6.3073 | 0
| 23:30 | 6.7748 | 0
Wed, 05/May | 0:30 | 7.2222 | 0
| 1:30 | 7.6353 | 0
| 2:30 | 7.9814 | 0
| 3:30 | 8.25 | 0
| 4:30 | 8.5723 | 0
| 5:30 | 8.9176 | 0
| 6:30 | 9.0101 | 0
| 7:30 | 8.8925 | 0
| 8:30 | 492.5256 | 0
| 9:30 | 64.1062 | 0
| 10:30 | 25.3807 | 0
| 11:30 | 14.9799 | 0
| 12:30 | 11.2209 | 0
| 13:30 | 8.4312 | 0
| 14:30 | 7.2475 | 0
| 15:30 | 7.4033 | 0
| 16:30 | 9.1685 | 0
| 17:30 | 11.2773 | 0
| 18:30 | 1.8707 | 0
| 19:30 | 2.511 | 0
| 20:30 | 3.3779 | 0
| 21:30 | 3.8986 | 0
| 22:30 | 4.4876 | 0
| 23:30 | 4.9378 | 0
Thu, 06/May | 0:30 | 5.191 | 0
| 1:30 | 5.5846 | 0
| 2:30 | 5.9957 | 0
| 3:30 | 6.2425 | 0
| 4:30 | 6.785 | 0
| 5:30 | 7.5025 | 0
| 6:30 | 7.7454 | 0
| 7:30 | 7.5586 | 0
| 8:30 | 409.5591 | 0
| 9:30 | 49.5978 | 0
| 10:30 | 25.3958 | 0
| 11:30 | 17.0544 | 0
| 12:30 | 12.0891 | 0
| 13:30 | 9.5512 | 0
| 14:30 | 7.0322 | 0
| 15:30 | 4.7418 | 0
| 16:30 | 3.9623 | 0
| 17:30 | 6.4469 | 0
| 18:30 | 1.7613 | 0
| 19:30 | 2.4576 | 0
| 20:30 | 3.4933 | 0
| 21:30 | 4.0632 | 0
| 22:30 | 4.547 | 0
| 23:30 | 5.0895 | 0
Fri, 07/May | 0:30 | 5.22 | 0
| 1:30 | 5.3664 | 0
| 2:30 | 5.8215 | 0
| 3:30 | 6.0359 | 0
| 4:30 | 6.4204 | 0
| 5:30 | 6.8764 | 0
| 6:30 | 6.9998 | 0
| 7:30 | 6.4588 | 0
| 8:30 | 330.4721 | 0
| 9:30 | 25.0454 | 0
| 10:30 | 14.3863 | 0
| 11:30 | 11.3564 | 0
| 12:30 | 8.9794 | 0
| 13:30 | 8.9718 | 0
| 14:30 | 9.2773 | 0
| 15:30 | 8.6248 | 0
| 16:30 | 7.5907 | 0
| 17:30 | 8.6139 | 0
| 18:30 | 1.4917 | 0
| 19:30 | 2.0011 | 0
| 20:30 | 2.7799 | 0
| 21:30 | 3.3089 | 0
| 22:30 | 3.7224 | 0
| 23:30 | 4.2853 | 0
Sat, 08/May | 0:30 | 4.7364 | 0
| 1:30 | 5.1394 | 0
| 2:30 | 5.6401 | 0
| 3:30 | 5.9769 | 0
| 4:30 | 6.1413 | 0
| 5:30 | 6.5028 | 0
| 6:30 | 6.654 | 0
| 7:30 | 6.3602 | 0
| 8:30 | 5.5597 | 0
| 9:30 | 4.4902 | 0
| 10:30 | 3.6799 | 0
| 11:30 | 2.8757 | 0
| 12:30 | 2.1234 | 0
| 13:30 | 1.861 | 0
| 14:30 | 1.6956 | 0
| 15:30 | 1.6341 | 0
| 16:30 | 1.9078 | 0
| 17:30 | 2.0949 | 0
| 18:30 | 2.0769 | 0
| 19:30 | 2.1456 | 0
| 20:30 | 2.5269 | 0
| 21:30 | 3.0898 | 0
| 22:30 | 3.4827 | 0
| 23:30 | 4.0474 | 0
Sun, 09/May | 0:30 | 4.4083 | 0
| 1:30 | 4.2903 | 0
| 2:30 | 4.2826 | 0
| 3:30 | 4.363 | 0
| 4:30 | 4.7506 | 0
| 5:30 | 5.3302 | 0
| 6:30 | 5.4695 | 0
| 7:30 | 5.0289 | 0
| 8:30 | 4.375 | 0
| 9:30 | 3.7796 | 0
| 10:30 | 3.1636 | 0
| 11:30 | 2.5613 | 0
| 12:30 | 1.9873 | 0
| 13:30 | 1.4489 | 0
| 14:30 | 1.1415 | 0
| 15:30 | 1.0417 | 0
| 16:30 | 1.0005 | 0
| 17:30 | 1.1257 | 0
| 18:30 | 1.2921 | 0
| 19:30 | 1.5489 | 0
| 20:30 | 2.2141 | 0
| 21:30 | 2.9636 | 0
| 22:30 | 3.5597 | 0
| 23:30 | 4.132 | 0
Mon, 10/May | 0:30 | 4.5632 | 0
| 1:30 | 4.647 | 0
| 2:30 | 4.7534 | 0
| 3:30 | 4.8913 | 0
| 4:30 | 4.8928 | 0
| 5:30 | 4.9576 | 0
| 6:30 | 4.9863 | 0
| 7:30 | 4.9559 | 0
| 8:30 | 321.7336 | 0
| 9:30 | 22.1787 | 0
| 10:30 | 10.5632 | 0
| 11:30 | 7.1459 | 0
| 12:30 | 3.694 | 0
| 13:30 | 2.21 | 0
| 14:30 | 1.6734 | 0
| 15:30 | 0.4376 | 0
| 16:30 | 0.3195 | 0
| 17:30 | 0.362 | 0
| 18:30 | 0.1539 | 0
| 19:30 | 0.9614 | 0
| 20:30 | 1.5812 | 0
| 21:30 | 2.0397 | 0
| 22:30 | 2.7682 | 0
| 23:30 | 3.3516 | 0
Tue, 11/May | 0:30 | 3.6996 | 0
| 1:30 | 3.9855 | 0
| 2:30 | 4.1707 | 0
| 3:30 | 4.3261 | 0
| 4:30 | 4.4824 | 0
| 5:30 | 4.5927 | 0
| 6:30 | 4.505 | 0
| 7:30 | 4.1437 | 0
| 8:30 | 251.2833 | 0
| 9:30 | 10.2119 | 0
| 10:30 | 3.7955 | 0
| 11:30 | 1.3767 | 0
| 12:30 | 0.1218 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0.0072 | 0
| 20:30 | 0.2736 | 0
| 21:30 | 0.8494 | 0
| 22:30 | 1.2891 | 0
| 23:30 | 1.6982 | 0
Wed, 12/May | 0:30 | 1.793 | 0
| 1:30 | 1.9929 | 0
| 2:30 | 2.4296 | 0
| 3:30 | 2.5425 | 0
| 4:30 | 2.5255 | 0
| 5:30 | 2.7756 | 0
| 6:30 | 2.8454 | 0
| 7:30 | 2.8936 | 0
| 8:30 | 195.8622 | 0
| 9:30 | 10.4641 | 0
| 10:30 | 6.6763 | 0
| 11:30 | 5.0134 | 0
| 12:30 | 3.2083 | 0
| 13:30 | 0.3341 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0.0097 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0556 | 0
| 21:30 | 0.2354 | 0
| 22:30 | 0.6113 | 0
| 23:30 | 0.9242 | 0
Thu, 13/May | 0:30 | 1.0672 | 0
| 1:30 | 1.4964 | 0
| 2:30 | 1.9255 | 0
| 3:30 | 2.087 | 0
| 4:30 | 2.1996 | 0
| 5:30 | 2.1256 | 0
| 6:30 | 1.8572 | 0
| 7:30 | 1.528 | 0
| 8:30 | 122.2168 | 0
| 9:30 | 1.5953 | 0
| 10:30 | 0.5684 | 0
| 11:30 | 0.127 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0.0103 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.001 | 0
| 21:30 | 0.0941 | 0
| 22:30 | 0.4558 | 0
| 23:30 | 0.8446 | 0
Fri, 14/May | 0:30 | 0.8839 | 0
| 1:30 | 1.0723 | 0
| 2:30 | 1.2239 | 0
| 3:30 | 1.2548 | 0
| 4:30 | 1.507 | 0
| 5:30 | 1.6705 | 0
| 6:30 | 1.5308 | 0
| 7:30 | 1.2491 | 0
| 8:30 | 108.9718 | 0
| 9:30 | 3.8413 | 0
| 10:30 | 3.4777 | 0
| 11:30 | 2.9235 | 0
| 12:30 | 2.1067 | 0
| 13:30 | 1.172 | 0
| 14:30 | 1.1318 | 0
| 15:30 | 1.6557 | 0
| 16:30 | 0.9896 | 0
| 17:30 | 0.8189 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0815 | 0
| 21:30 | 0.3195 | 0
| 22:30 | 0.6406 | 0
| 23:30 | 0.9616 | 0
Sat, 15/May | 0:30 | 1.1315 | 0
| 1:30 | 1.291 | 0
| 2:30 | 1.4019 | 0
| 3:30 | 1.4891 | 0
| 4:30 | 1.7211 | 0
| 5:30 | 1.9507 | 0
| 6:30 | 2.0313 | 0
| 7:30 | 2.0695 | 0
| 8:30 | 1.9178 | 0
| 9:30 | 1.7295 | 0
| 10:30 | 1.588 | 0
| 11:30 | 1.3471 | 0
| 12:30 | 1.0807 | 0
| 13:30 | 0.8091 | 0
| 14:30 | 0.6283 | 0
| 15:30 | 0.7089 | 0
| 16:30 | 1.0601 | 0
| 17:30 | 1.391 | 0
| 18:30 | 1.513 | 0
| 19:30 | 1.5828 | 0
| 20:30 | 1.7147 | 0
| 21:30 | 1.9424 | 0
| 22:30 | 2.1916 | 0
| 23:30 | 2.2003 | 0
Sun, 16/May | 0:30 | 2.2767 | 0
| 1:30 | 2.6437 | 0
| 2:30 | 2.8811 | 0
| 3:30 | 2.9971 | 0
| 4:30 | 3.2311 | 0
| 5:30 | 3.4635 | 0
| 6:30 | 3.3652 | 0
| 7:30 | 3.0619 | 0
| 8:30 | 2.6085 | 0
| 9:30 | 2.2304 | 0
| 10:30 | 2.207 | 0
| 11:30 | 2.1585 | 0
| 12:30 | 1.5326 | 0
| 13:30 | 1.4331 | 0
| 14:30 | 1.3469 | 0
| 15:30 | 0.8065 | 0
| 16:30 | 0.6513 | 0
| 17:30 | 0.4984 | 0
| 18:30 | 0.6073 | 0
| 19:30 | 0.9193 | 0
| 20:30 | 1.2548 | 0
| 21:30 | 1.4482 | 0
| 22:30 | 1.7376 | 0
| 23:30 | 2.1864 | 0
Mon, 17/May | 0:30 | 2.5202 | 0
| 1:30 | 2.8113 | 0
| 2:30 | 2.9404 | 0
| 3:30 | 3.0674 | 0
| 4:30 | 3.3179 | 0
| 5:30 | 3.4802 | 0
| 6:30 | 3.4026 | 0
| 7:30 | 3.3071 | 0
| 8:30 | 222.704 | 0
| 9:30 | 6.5656 | 0
| 10:30 | 2.2843 | 0
| 11:30 | 1.8228 | 0
| 12:30 | 2.2323 | 0
| 13:30 | 2.3244 | 0
| 14:30 | 1.2289 | 0
| 15:30 | 0.067 | 0
| 16:30 | 0 | 0
| 17:30 | 0.1481 | 0
| 18:30 | 0 | 0
| 19:30 | 0.1522 | 0
| 20:30 | 0.7833 | 0
| 21:30 | 1.1193 | 0
| 22:30 | 1.4888 | 0
| 23:30 | 1.865 | 0
Tue, 18/May | 0:30 | 2.0932 | 0
| 1:30 | 2.2494 | 0
| 2:30 | 2.3603 | 0
| 3:30 | 2.4426 | 0
| 4:30 | 2.6639 | 0
| 5:30 | 2.9206 | 0
| 6:30 | 2.8502 | 0
| 7:30 | 2.699 | 0
| 8:30 | 177.2395 | 0
| 9:30 | 5.3609 | 0
| 10:30 | 2.2686 | 0
| 11:30 | 0.7342 | 0
| 12:30 | 0.138 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0.232 | 0
| 17:30 | 3.3342 | 0
| 18:30 | 0.0074 | 0
| 19:30 | 0.0656 | 0
| 20:30 | 0.3026 | 0
| 21:30 | 0.723 | 0
| 22:30 | 1.3095 | 0
| 23:30 | 1.83 | 0
Wed, 19/May | 0:30 | 2.2506 | 0
| 1:30 | 2.7872 | 0
| 2:30 | 3.1166 | 0
| 3:30 | 3.2652 | 0
| 4:30 | 3.5379 | 0
| 5:30 | 3.7903 | 0
| 6:30 | 3.7537 | 0
| 7:30 | 3.3138 | 0
| 8:30 | 182.5881 | 0
| 9:30 | 5.2526 | 0
| 10:30 | 4.133 | 0
| 11:30 | 4.1102 | 0
| 12:30 | 2.3993 | 0
| 13:30 | 2.0531 | 0
| 14:30 | 2.5559 | 0
| 15:30 | 3.052 | 0
| 16:30 | 3.3881 | 0
| 17:30 | 3.9338 | 0
| 18:30 | 0.0177 | 0
| 19:30 | 0.265 | 0
| 20:30 | 0.8246 | 0
| 21:30 | 1.2316 | 0
| 22:30 | 1.656 | 0
| 23:30 | 1.8781 | 0
Thu, 20/May | 0:30 | 2.0905 | 0
| 1:30 | 2.3789 | 0
| 2:30 | 2.4477 | 0
| 3:30 | 2.3841 | 0
| 4:30 | 2.4984 | 0
| 5:30 | 2.6713 | 0
| 6:30 | 2.563 | 0
| 7:30 | 2.453 | 0
| 8:30 | 164.1091 | 0
| 9:30 | 6.8612 | 0
| 10:30 | 3.5898 | 0
| 11:30 | 1.3614 | 0
| 12:30 | 0.1212 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0195 | 0
| 22:30 | 0.332 | 0
| 23:30 | 0.79 | 0
Fri, 21/May | 0:30 | 1.0027 | 0
| 1:30 | 1.1819 | 0
| 2:30 | 1.4827 | 0
| 3:30 | 1.6062 | 0
| 4:30 | 1.7609 | 0
| 5:30 | 2.0047 | 0
| 6:30 | 1.9046 | 0
| 7:30 | 1.7782 | 0
| 8:30 | 129.0438 | 0
| 9:30 | 4.5669 | 0
| 10:30 | 2.576 | 0
| 11:30 | 2.3486 | 0
| 12:30 | 2.5727 | 0
| 13:30 | 2.0449 | 0
| 14:30 | 1.6829 | 0
| 15:30 | 2.3161 | 0
| 16:30 | 3.3845 | 0
| 17:30 | 3.6809 | 0
| 18:30 | 0 | 0
| 19:30 | 0.001 | 0
| 20:30 | 0.0415 | 0
| 21:30 | 0.1627 | 0
| 22:30 | 0.2968 | 0
| 23:30 | 0.5828 | 0
Sat, 22/May | 0:30 | 0.7086 | 0
| 1:30 | 0.9327 | 0
| 2:30 | 1.1719 | 0
| 3:30 | 1.1357 | 0
| 4:30 | 1.3433 | 0
| 5:30 | 1.5438 | 0
| 6:30 | 1.6067 | 0
| 7:30 | 1.5237 | 0
| 8:30 | 1.343 | 0
| 9:30 | 1.0836 | 0
| 10:30 | 0.8911 | 0
| 11:30 | 0.7146 | 0
| 12:30 | 0.5432 | 0
| 13:30 | 0.3265 | 0
| 14:30 | 0.5211 | 0
| 15:30 | 0.6571 | 0
| 16:30 | 0.3163 | 0
| 17:30 | 0.267 | 0
| 18:30 | 0.5234 | 0
| 19:30 | 0.7478 | 0
| 20:30 | 1.0694 | 0
| 21:30 | 1.6133 | 0
| 22:30 | 1.9326 | 0
| 23:30 | 2.105 | 0
Sun, 23/May | 0:30 | 2.2666 | 0
| 1:30 | 2.3536 | 0
| 2:30 | 2.3793 | 0
| 3:30 | 2.4341 | 0
| 4:30 | 2.6389 | 0
| 5:30 | 2.8392 | 0
| 6:30 | 2.7275 | 0
| 7:30 | 2.5835 | 0
| 8:30 | 2.5153 | 0
| 9:30 | 2.2638 | 0
| 10:30 | 2.0137 | 0
| 11:30 | 1.7518 | 0
| 12:30 | 1.3826 | 0
| 13:30 | 1.1711 | 0
| 14:30 | 0.9944 | 0
| 15:30 | 0.9599 | 0
| 16:30 | 1.1545 | 0
| 17:30 | 1.0432 | 0
| 18:30 | 0.8488 | 0
| 19:30 | 0.9807 | 0
| 20:30 | 1.2919 | 0
| 21:30 | 1.5472 | 0
| 22:30 | 1.839 | 0
| 23:30 | 2.1069 | 0
Mon, 24/May | 0:30 | 2.2218 | 0
| 1:30 | 2.4993 | 0
| 2:30 | 2.7505 | 0
| 3:30 | 2.8452 | 0
| 4:30 | 2.9222 | 0
| 5:30 | 3.0045 | 0
| 6:30 | 3.0452 | 0
| 7:30 | 2.8645 | 0
| 8:30 | 193.3036 | 0
| 9:30 | 5.1989 | 0
| 10:30 | 3.0358 | 0
| 11:30 | 1.3124 | 0
| 12:30 | 0.0171 | 0
| 13:30 | 0.0264 | 0
| 14:30 | 0.7312 | 0
| 15:30 | 0.5765 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0529 | 0
| 23:30 | 0.4925 | 0
Tue, 25/May | 0:30 | 0.7461 | 0
| 1:30 | 0.8101 | 0
| 2:30 | 1.034 | 0
| 3:30 | 1.1445 | 0
| 4:30 | 1.0967 | 0
| 5:30 | 1.2911 | 0
| 6:30 | 1.4721 | 0
| 7:30 | 1.6575 | 0
| 8:30 | 136.6877 | 0
| 9:30 | 4.6845 | 0
| 10:30 | 3.1816 | 0
| 11:30 | 1.7287 | 0
| 12:30 | 0.2816 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 1.545 | 0
| 18:30 | 0 | 0
| 19:30 | 0.0067 | 0
| 20:30 | 0.2147 | 0
| 21:30 | 0.5138 | 0
| 22:30 | 0.7926 | 0
| 23:30 | 1.0837 | 0
Wed, 26/May | 0:30 | 1.254 | 0
| 1:30 | 1.3984 | 0
| 2:30 | 1.643 | 0
| 3:30 | 1.9146 | 0
| 4:30 | 2.0205 | 0
| 5:30 | 2.0994 | 0
| 6:30 | 2.1447 | 0
| 7:30 | 1.99 | 0
| 8:30 | 130.3261 | 0
| 9:30 | 2.8652 | 0
| 10:30 | 0.9255 | 0
| 11:30 | 0.1249 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0764 | 0
| 23:30 | 0.7737 | 0
Thu, 27/May | 0:30 | 1.3089 | 0
| 1:30 | 1.719 | 0
| 2:30 | 2.2602 | 0
| 3:30 | 2.8102 | 0
| 4:30 | 3.1496 | 0
| 5:30 | 3.3468 | 0
| 6:30 | 3.4423 | 0
| 7:30 | 3.1083 | 0
| 8:30 | 159.502 | 0
| 9:30 | 4.4688 | 0
| 10:30 | 0.8352 | 0
| 11:30 | 0.0001 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0.3004 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0072 | 0
| 21:30 | 0.2635 | 0
| 22:30 | 0.7287 | 0
| 23:30 | 1.1795 | 0
Fri, 28/May | 0:30 | 1.5735 | 0
| 1:30 | 1.7224 | 0
| 2:30 | 1.917 | 0
| 3:30 | 2.0539 | 0
| 4:30 | 2.1579 | 0
| 5:30 | 2.2387 | 0
| 6:30 | 2.2889 | 0
| 7:30 | 2.1447 | 0
| 8:30 | 134.1526 | 0
| 9:30 | 4.4143 | 0
| 10:30 | 1.3856 | 0
| 11:30 | 0.0751 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0.0056 | 0
Sat, 29/May | 0:30 | 0.1029 | 0
| 1:30 | 0.418 | 0
| 2:30 | 0.7797 | 0
| 3:30 | 0.9321 | 0
| 4:30 | 1.0841 | 0
| 5:30 | 1.3364 | 0
| 6:30 | 1.2658 | 0
| 7:30 | 0.8688 | 0
| 8:30 | 0.5563 | 0
| 9:30 | 0.2492 | 0
| 10:30 | 0.0744 | 0
| 11:30 | 0.0139 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.003 | 0
| 23:30 | 0.2386 | 0
Sun, 30/May | 0:30 | 0.7978 | 0
| 1:30 | 1.1311 | 0
| 2:30 | 1.4796 | 0
| 3:30 | 1.7985 | 0
| 4:30 | 2.2282 | 0
| 5:30 | 2.3614 | 0
| 6:30 | 2.0313 | 0
| 7:30 | 1.3936 | 0
| 8:30 | 0.6164 | 0
| 9:30 | 0.1729 | 0
| 10:30 | 0.0583 | 0
| 11:30 | 0.0056 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0063 | 0
| 23:30 | 0.291 | 0
Mon, 31/May | 0:30 | 0.6006 | 0
| 1:30 | 0.8018 | 0
| 2:30 | 1.1518 | 0
| 3:30 | 1.3931 | 0
| 4:30 | 1.372 | 0
| 5:30 | 1.035 | 0
| 6:30 | 0.6694 | 0
| 7:30 | 0.5336 | 0
| 8:30 | 83.796 | 0
| 9:30 | 0.0168 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Tue, 01/Jun | 0:30 | 0.0076 | 0
| 1:30 | 0.0775 | 0
| 2:30 | 0.2183 | 0
| 3:30 | 0.4028 | 0
| 4:30 | 0.5382 | 0
| 5:30 | 0.6351 | 0
| 6:30 | 0.7115 | 0
| 7:30 | 0.7567 | 0
| 8:30 | 84.7291 | 0
| 9:30 | 0.5338 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Wed, 02/Jun | 0:30 | 0 | 0
| 1:30 | 0.019 | 0
| 2:30 | 0.1055 | 0
| 3:30 | 0.2263 | 0
| 4:30 | 0.3315 | 0
| 5:30 | 0.407 | 0
| 6:30 | 0.446 | 0
| 7:30 | 0.5077 | 0
| 8:30 | 75.3618 | 0
| 9:30 | 0.6156 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Thu, 03/Jun | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0.0233 | 0
| 3:30 | 0.131 | 0
| 4:30 | 0.2758 | 0
| 5:30 | 0.5013 | 0
| 6:30 | 0.6201 | 0
| 7:30 | 0.6716 | 0
| 8:30 | 80.9539 | 0
| 9:30 | 2.5959 | 0
| 10:30 | 1.2893 | 0
| 11:30 | 0.6325 | 0
| 12:30 | 0.0441 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0072 | 0
| 22:30 | 0.3074 | 0
| 23:30 | 0.9238 | 0
Fri, 04/Jun | 0:30 | 1.3997 | 0
| 1:30 | 1.9181 | 0
| 2:30 | 2.3615 | 0
| 3:30 | 2.7387 | 0
| 4:30 | 3.0332 | 0
| 5:30 | 3.1614 | 0
| 6:30 | 3.0711 | 0
| 7:30 | 2.763 | 0
| 8:30 | 148.5957 | 0
| 9:30 | 5.9506 | 0
| 10:30 | 3.404 | 0
| 11:30 | 1.703 | 0
| 12:30 | 1.0133 | 0
| 13:30 | 0.2833 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0.0277 | 0
| 17:30 | 1.3417 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0458 | 0
| 21:30 | 0.3535 | 0
| 22:30 | 0.8333 | 0
| 23:30 | 1.093 | 0
Sat, 05/Jun | 0:30 | 1.393 | 0
| 1:30 | 1.798 | 0
| 2:30 | 2.0849 | 0
| 3:30 | 2.5 | 0
| 4:30 | 2.979 | 0
| 5:30 | 3.2266 | 0
| 6:30 | 2.9848 | 0
| 7:30 | 2.5746 | 0
| 8:30 | 2.3038 | 0
| 9:30 | 2.0038 | 0
| 10:30 | 1.576 | 0
| 11:30 | 1.236 | 0
| 12:30 | 1.0523 | 0
| 13:30 | 0.7787 | 0
| 14:30 | 0.6197 | 0
| 15:30 | 0.5268 | 0
| 16:30 | 0.3907 | 0
| 17:30 | 0.5602 | 0
| 18:30 | 0.7976 | 0
| 19:30 | 1.0205 | 0
| 20:30 | 1.4315 | 0
| 21:30 | 1.8913 | 0
| 22:30 | 2.3721 | 0
| 23:30 | 2.6834 | 0
Sun, 06/Jun | 0:30 | 2.9065 | 0
| 1:30 | 3.3192 | 0
| 2:30 | 3.6638 | 0
| 3:30 | 3.9029 | 0
| 4:30 | 4.2068 | 0
| 5:30 | 4.393 | 0
| 6:30 | 4.3497 | 0
| 7:30 | 4.012 | 0
| 8:30 | 3.5611 | 0
| 9:30 | 2.9834 | 0
| 10:30 | 2.1725 | 0
| 11:30 | 1.4822 | 0
| 12:30 | 1.0471 | 0
| 13:30 | 0.7235 | 0
| 14:30 | 0.4719 | 0
| 15:30 | 0.3422 | 0
| 16:30 | 0.3881 | 0
| 17:30 | 0.5841 | 0
| 18:30 | 0.7996 | 0
| 19:30 | 1.055 | 0
| 20:30 | 1.2909 | 0
| 21:30 | 1.497 | 0
| 22:30 | 1.7419 | 0
| 23:30 | 1.9182 | 0
Mon, 07/Jun | 0:30 | 1.8144 | 0
| 1:30 | 1.7798 | 0
| 2:30 | 1.931 | 0
| 3:30 | 2.2839 | 0
| 4:30 | 2.6383 | 0
| 5:30 | 2.8999 | 0
| 6:30 | 3.027 | 0
| 7:30 | 2.8766 | 0
| 8:30 | 2.7216 | 0
| 9:30 | 2.4278 | 0
| 10:30 | 2.0998 | 0
| 11:30 | 1.8004 | 0
| 12:30 | 1.5153 | 0
| 13:30 | 1.4601 | 0
| 14:30 | 1.3984 | 0
| 15:30 | 1.3702 | 0
| 16:30 | 1.4064 | 0
| 17:30 | 1.4287 | 0
| 18:30 | 1.5204 | 0
| 19:30 | 1.6902 | 0
| 20:30 | 2.0085 | 0
| 21:30 | 2.4324 | 0
| 22:30 | 2.9369 | 0
| 23:30 | 3.4706 | 0
Tue, 08/Jun | 0:30 | 3.8636 | 0
| 1:30 | 4.1535 | 0
| 2:30 | 4.3926 | 0
| 3:30 | 4.5084 | 0
| 4:30 | 4.6096 | 0
| 5:30 | 4.7567 | 0
| 6:30 | 4.7171 | 0
| 7:30 | 4.343 | 0
| 8:30 | 271.1762 | 0
| 9:30 | 10.6442 | 0
| 10:30 | 5.1693 | 0
| 11:30 | 2.7836 | 0
| 12:30 | 1.1666 | 0
| 13:30 | 0.3747 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0.2309 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0968 | 0
| 21:30 | 0.6575 | 0
| 22:30 | 1.0264 | 0
| 23:30 | 1.2252 | 0
Wed, 09/Jun | 0:30 | 1.3141 | 0
| 1:30 | 1.3301 | 0
| 2:30 | 1.2995 | 0
| 3:30 | 1.1025 | 0
| 4:30 | 0.9498 | 0
| 5:30 | 0.9661 | 0
| 6:30 | 0.942 | 0
| 7:30 | 0.8654 | 0
| 8:30 | 116.6176 | 0
| 9:30 | 0.3726 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0389 | 0
| 22:30 | 0.4692 | 0
| 23:30 | 1.0576 | 0
Thu, 10/Jun | 0:30 | 1.3772 | 0
| 1:30 | 1.6469 | 0
| 2:30 | 1.9326 | 0
| 3:30 | 2.222 | 0
| 4:30 | 2.4089 | 0
| 5:30 | 2.4284 | 0
| 6:30 | 2.3826 | 0
| 7:30 | 2.3715 | 0
| 8:30 | 164.3622 | 0
| 9:30 | 8.8345 | 0
| 10:30 | 7.3513 | 0
| 11:30 | 6.5434 | 0
| 12:30 | 5.8816 | 0
| 13:30 | 5.6185 | 0
| 14:30 | 6.3458 | 0
| 15:30 | 5.5488 | 0
| 16:30 | 4.7909 | 0
| 17:30 | 4.6773 | 0
| 18:30 | 0.1776 | 0
| 19:30 | 0.5822 | 0
| 20:30 | 1.2273 | 0
| 21:30 | 1.7762 | 0
| 22:30 | 2.1957 | 0
| 23:30 | 2.6396 | 0
Fri, 11/Jun | 0:30 | 2.9413 | 0
| 1:30 | 3.1818 | 0
| 2:30 | 3.545 | 0
| 3:30 | 3.8821 | 0
| 4:30 | 4.1698 | 0
| 5:30 | 4.3834 | 0
| 6:30 | 4.2885 | 0
| 7:30 | 3.6197 | 0
| 8:30 | 183.8163 | 0
| 9:30 | 5.7168 | 0
| 10:30 | 2.0716 | 0
| 11:30 | 0.4859 | 0
| 12:30 | 0.0178 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0006 | 0
| 21:30 | 0.2033 | 0
| 22:30 | 0.6564 | 0
| 23:30 | 1.011 | 0
Sat, 12/Jun | 0:30 | 1.1893 | 0
| 1:30 | 1.2855 | 0
| 2:30 | 1.3918 | 0
| 3:30 | 1.4562 | 0
| 4:30 | 1.5414 | 0
| 5:30 | 1.6676 | 0
| 6:30 | 1.5442 | 0
| 7:30 | 1.4317 | 0
| 8:30 | 1.295 | 0
| 9:30 | 1.0601 | 0
| 10:30 | 0.6709 | 0
| 11:30 | 0.1786 | 0
| 12:30 | 0.0259 | 0
| 13:30 | 0.017 | 0
| 14:30 | 0.0058 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0119 | 0
| 21:30 | 0.0654 | 0
| 22:30 | 0.226 | 0
| 23:30 | 0.4507 | 0
Sun, 13/Jun | 0:30 | 0.4881 | 0
| 1:30 | 0.5471 | 0
| 2:30 | 0.6235 | 0
| 3:30 | 0.6361 | 0
| 4:30 | 0.5686 | 0
| 5:30 | 0.5722 | 0
| 6:30 | 0.6627 | 0
| 7:30 | 0.5254 | 0
| 8:30 | 0.4221 | 0
| 9:30 | 0.3476 | 0
| 10:30 | 0.197 | 0
| 11:30 | 0.0618 | 0
| 12:30 | 0.0018 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Mon, 14/Jun | 0:30 | 0.006 | 0
| 1:30 | 0.1156 | 0
| 2:30 | 0.3948 | 0
| 3:30 | 0.5161 | 0
| 4:30 | 0.6017 | 0
| 5:30 | 0.6632 | 0
| 6:30 | 0.6322 | 0
| 7:30 | 0.5251 | 0
| 8:30 | 81.0669 | 0
| 9:30 | 0.0094 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Tue, 15/Jun | 0:30 | 0.0009 | 0
| 1:30 | 0.0628 | 0
| 2:30 | 0.2434 | 0
| 3:30 | 0.464 | 0
| 4:30 | 0.6989 | 0
| 5:30 | 0.9163 | 0
| 6:30 | 0.944 | 0
| 7:30 | 0.7597 | 0
| 8:30 | 73.0087 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Wed, 16/Jun | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0.0118 | 0
| 4:30 | 0.0406 | 0
| 5:30 | 0.0868 | 0
| 6:30 | 0.103 | 0
| 7:30 | 0.0789 | 0
| 8:30 | 48.6344 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Thu, 17/Jun | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0.0013 | 0
| 4:30 | 0.0352 | 0
| 5:30 | 0.1385 | 0
| 6:30 | 0.2162 | 0
| 7:30 | 0.2524 | 0
| 8:30 | 63.7537 | 0
| 9:30 | 1.7882 | 0
| 10:30 | 1.3495 | 0
| 11:30 | 0.3184 | 0
| 12:30 | 0 | 0
| 13:30 | 0.0251 | 0
| 14:30 | 0.3797 | 0
| 15:30 | 0.3701 | 0
| 16:30 | 0.7421 | 0
| 17:30 | 1.0477 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0502 | 0
| 23:30 | 0.3881 | 0
Fri, 18/Jun | 0:30 | 0.8678 | 0
| 1:30 | 1.2409 | 0
| 2:30 | 1.7014 | 0
| 3:30 | 2.0055 | 0
| 4:30 | 2.3678 | 0
| 5:30 | 2.5672 | 0
| 6:30 | 2.3955 | 0
| 7:30 | 1.8628 | 0
| 8:30 | 109.5625 | 0
| 9:30 | 0.5038 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0.0587 | 0
Sat, 19/Jun | 0:30 | 0.2806 | 0
| 1:30 | 0.6996 | 0
| 2:30 | 1.0215 | 0
| 3:30 | 1.2369 | 0
| 4:30 | 1.4895 | 0
| 5:30 | 1.6236 | 0
| 6:30 | 1.4802 | 0
| 7:30 | 1.0092 | 0
| 8:30 | 0.4853 | 0
| 9:30 | 0.2357 | 0
| 10:30 | 0.1594 | 0
| 11:30 | 0.0525 | 0
| 12:30 | 0.0069 | 0
| 13:30 | 0.0028 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0177 | 0
| 22:30 | 0.1085 | 0
| 23:30 | 0.2441 | 0
Sun, 20/Jun | 0:30 | 0.3539 | 0
| 1:30 | 0.502 | 0
| 2:30 | 0.6931 | 0
| 3:30 | 0.8658 | 0
| 4:30 | 1.0478 | 0
| 5:30 | 1.2433 | 0
| 6:30 | 1.2881 | 0
| 7:30 | 1.2314 | 0
| 8:30 | 1.1953 | 0
| 9:30 | 1.199 | 0
| 10:30 | 1.2494 | 0
| 11:30 | 1.1648 | 0
| 12:30 | 0.8634 | 0
| 13:30 | 0.6087 | 0
| 14:30 | 0.4331 | 0
| 15:30 | 0.3331 | 0
| 16:30 | 0.3899 | 0
| 17:30 | 0.4556 | 0
| 18:30 | 0.4866 | 0
| 19:30 | 0.618 | 0
| 20:30 | 0.7839 | 0
| 21:30 | 0.8862 | 0
| 22:30 | 1.0578 | 0
| 23:30 | 1.3172 | 0
Mon, 21/Jun | 0:30 | 1.4793 | 0
| 1:30 | 1.6116 | 0
| 2:30 | 1.805 | 0
| 3:30 | 1.9533 | 0
| 4:30 | 2.0634 | 0
| 5:30 | 2.2061 | 0
| 6:30 | 2.2242 | 0
| 7:30 | 2.062 | 0
| 8:30 | 141.8624 | 0
| 9:30 | 2.905 | 0
| 10:30 | 0.7338 | 0
| 11:30 | 0.383 | 0
| 12:30 | 0.022 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0089 | 0
| 23:30 | 0.253 | 0
Tue, 22/Jun | 0:30 | 0.6381 | 0
| 1:30 | 0.8947 | 0
| 2:30 | 1.2038 | 0
| 3:30 | 1.5067 | 0
| 4:30 | 1.575 | 0
| 5:30 | 1.5553 | 0
| 6:30 | 1.4275 | 0
| 7:30 | 1.3648 | 0
| 8:30 | 112.2735 | 0
| 9:30 | 2.1686 | 0
| 10:30 | 0.1723 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0014 | 0
| 22:30 | 0.0956 | 0
| 23:30 | 0.3983 | 0
Wed, 23/Jun | 0:30 | 0.6162 | 0
| 1:30 | 0.8098 | 0
| 2:30 | 1.0061 | 0
| 3:30 | 1.1415 | 0
| 4:30 | 1.3209 | 0
| 5:30 | 1.4149 | 0
| 6:30 | 1.3164 | 0
| 7:30 | 1.1729 | 0
| 8:30 | 94.3252 | 0
| 9:30 | 0.4369 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0266 | 0
| 23:30 | 0.2014 | 0
Thu, 24/Jun | 0:30 | 0.5209 | 0
| 1:30 | 0.8487 | 0
| 2:30 | 1.0741 | 0
| 3:30 | 1.2209 | 0
| 4:30 | 1.3542 | 0
| 5:30 | 1.4432 | 0
| 6:30 | 1.4142 | 0
| 7:30 | 1.3811 | 0
| 8:30 | 107.9269 | 0
| 9:30 | 2.0932 | 0
| 10:30 | 0.0187 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0.4139 | 0
| 15:30 | 1.1908 | 0
| 16:30 | 1.1284 | 0
| 17:30 | 1.6099 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0117 | 0
| 23:30 | 0.0632 | 0
Fri, 25/Jun | 0:30 | 0.1126 | 0
| 1:30 | 0.1614 | 0
| 2:30 | 0.1968 | 0
| 3:30 | 0.1917 | 0
| 4:30 | 0.2419 | 0
| 5:30 | 0.3324 | 0
| 6:30 | 0.3566 | 0
| 7:30 | 0.2367 | 0
| 8:30 | 54.9233 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sat, 26/Jun | 0:30 | 0.0046 | 0
| 1:30 | 0.0535 | 0
| 2:30 | 0.1819 | 0
| 3:30 | 0.3087 | 0
| 4:30 | 0.4511 | 0
| 5:30 | 0.5459 | 0
| 6:30 | 0.4903 | 0
| 7:30 | 0.2947 | 0
| 8:30 | 0.0755 | 0
| 9:30 | 0.0024 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sun, 27/Jun | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0.01 | 0
| 5:30 | 0.0939 | 0
| 6:30 | 0.1331 | 0
| 7:30 | 0.1013 | 0
| 8:30 | 0.0876 | 0
| 9:30 | 0.0862 | 0
| 10:30 | 0.1171 | 0
| 11:30 | 0.0608 | 0
| 12:30 | 0.001 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Mon, 28/Jun | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0.0038 | 0
| 3:30 | 0.0125 | 0
| 4:30 | 0.0543 | 0
| 5:30 | 0.1293 | 0
| 6:30 | 0.1437 | 0
| 7:30 | 0.0343 | 0
| 8:30 | 41.039 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Tue, 29/Jun | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0.009 | 0
| 8:30 | 47.9907 | 0
| 9:30 | 0.2941 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Wed, 30/Jun | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0.0058 | 0
| 6:30 | 0.0165 | 0
| 7:30 | 0.017 | 0
| 8:30 | 43.7138 | 0
| 9:30 | 0.1273 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Thu, 01/Jul | 0:30 | 0 | 0
| 1:30 | 0.0061 | 0
| 2:30 | 0.0902 | 0
| 3:30 | 0.2871 | 0
| 4:30 | 0.6012 | 0
| 5:30 | 0.8007 | 0
| 6:30 | 0.931 | 0
| 7:30 | 0.7299 | 0
| 8:30 | 70.6201 | 0
| 9:30 | 0.4806 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0.0043 | 0
Fri, 02/Jul | 0:30 | 0.0994 | 0
| 1:30 | 0.4236 | 0
| 2:30 | 0.9679 | 0
| 3:30 | 1.2756 | 0
| 4:30 | 1.5558 | 0
| 5:30 | 1.6519 | 0
| 6:30 | 1.4214 | 0
| 7:30 | 1.0293 | 0
| 8:30 | 81.2245 | 0
| 9:30 | 0.012 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sat, 03/Jul | 0:30 | 0.0034 | 0
| 1:30 | 0.0405 | 0
| 2:30 | 0.1751 | 0
| 3:30 | 0.3904 | 0
| 4:30 | 0.7278 | 0
| 5:30 | 0.975 | 0
| 6:30 | 0.872 | 0
| 7:30 | 0.5769 | 0
| 8:30 | 0.2617 | 0
| 9:30 | 0.0319 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sun, 04/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0.0046 | 0
| 5:30 | 0.0252 | 0
| 6:30 | 0.0587 | 0
| 7:30 | 0.0314 | 0
| 8:30 | 0.0025 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Mon, 05/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0.0002 | 0
| 7:30 | 0 | 0
| 8:30 | 26.4204 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Tue, 06/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0 | 0
| 8:30 | 21.3749 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Wed, 07/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0.0031 | 0
| 6:30 | 0.0288 | 0
| 7:30 | 0.0288 | 0
| 8:30 | 40.5427 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Thu, 08/Jul | 0:30 | 0 | 0
| 1:30 | 0.0138 | 0
| 2:30 | 0.0533 | 0
| 3:30 | 0.1613 | 0
| 4:30 | 0.2363 | 0
| 5:30 | 0.3392 | 0
| 6:30 | 0.4193 | 0
| 7:30 | 0.2566 | 0
| 8:30 | 57.2615 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Fri, 09/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0.0009 | 0
| 5:30 | 0.0136 | 0
| 6:30 | 0.0216 | 0
| 7:30 | 0.021 | 0
| 8:30 | 47.6633 | 0
| 9:30 | 0.8582 | 0
| 10:30 | 0.3153 | 0
| 11:30 | 0.0031 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sat, 10/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0 | 0
| 8:30 | 0 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sun, 11/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0 | 0
| 8:30 | 0 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Mon, 12/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0.0004 | 0
| 4:30 | 0.015 | 0
| 5:30 | 0.0255 | 0
| 6:30 | 0.0532 | 0
| 7:30 | 0.0698 | 0
| 8:30 | 44.3458 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Tue, 13/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0 | 0
| 8:30 | 29.1863 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Wed, 14/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0.0031 | 0
| 6:30 | 0.0127 | 0
| 7:30 | 0.0035 | 0
| 8:30 | 38.1997 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Thu, 15/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0 | 0
| 8:30 | 36.3665 | 0
| 9:30 | 0.1356 | 0
| 10:30 | 0.0213 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Fri, 16/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0.0029 | 0
| 5:30 | 0.0245 | 0
| 6:30 | 0.0603 | 0
| 7:30 | 0.0653 | 0
| 8:30 | 45.5354 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sat, 17/Jul | 0:30 | 0 | 0
| 1:30 | 0.0091 | 0
| 2:30 | 0.0327 | 0
| 3:30 | 0.1018 | 0
| 4:30 | 0.1736 | 0
| 5:30 | 0.2488 | 0
| 6:30 | 0.2846 | 0
| 7:30 | 0.1952 | 0
| 8:30 | 0.098 | 0
| 9:30 | 0.0331 | 0
| 10:30 | 0.0041 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0056 | 0
| 23:30 | 0.1785 | 0
Sun, 18/Jul | 0:30 | 0.5844 | 0
| 1:30 | 0.926 | 0
| 2:30 | 1.2328 | 0
| 3:30 | 1.5157 | 0
| 4:30 | 1.6835 | 0
| 5:30 | 1.7771 | 0
| 6:30 | 1.7953 | 0
| 7:30 | 1.6651 | 0
| 8:30 | 1.4441 | 0
| 9:30 | 1.0165 | 0
| 10:30 | 0.7171 | 0
| 11:30 | 0.5897 | 0
| 12:30 | 0.4244 | 0
| 13:30 | 0.3522 | 0
| 14:30 | 0.396 | 0
| 15:30 | 0.4143 | 0
| 16:30 | 0.4257 | 0
| 17:30 | 0.4298 | 0
| 18:30 | 0.3889 | 0
| 19:30 | 0.4031 | 0
| 20:30 | 0.4534 | 0
| 21:30 | 0.4833 | 0
| 22:30 | 0.5275 | 0
| 23:30 | 0.6344 | 0
Mon, 19/Jul | 0:30 | 0.6997 | 0
| 1:30 | 0.7882 | 0
| 2:30 | 0.9782 | 0
| 3:30 | 1.1133 | 0
| 4:30 | 1.1933 | 0
| 5:30 | 1.311 | 0
| 6:30 | 1.264 | 0
| 7:30 | 1.1304 | 0
| 8:30 | 116.2896 | 0
| 9:30 | 3.1926 | 0
| 10:30 | 2.2691 | 0
| 11:30 | 1.9014 | 0
| 12:30 | 1.4458 | 0
| 13:30 | 0.4625 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0.0036 | 0
Tue, 20/Jul | 0:30 | 0.1312 | 0
| 1:30 | 0.4607 | 0
| 2:30 | 0.7662 | 0
| 3:30 | 1.0112 | 0
| 4:30 | 1.2759 | 0
| 5:30 | 1.4788 | 0
| 6:30 | 1.4662 | 0
| 7:30 | 1.0543 | 0
| 8:30 | 90.4362 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Wed, 21/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0.0033 | 0
| 3:30 | 0.1213 | 0
| 4:30 | 0.4575 | 0
| 5:30 | 0.7012 | 0
| 6:30 | 0.787 | 0
| 7:30 | 0.7321 | 0
| 8:30 | 84.1153 | 0
| 9:30 | 0.8169 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Thu, 22/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0.0065 | 0
| 5:30 | 0.0266 | 0
| 6:30 | 0.0586 | 0
| 7:30 | 0.0711 | 0
| 8:30 | 52.6976 | 0
| 9:30 | 0.0146 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Fri, 23/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0.0252 | 0
| 5:30 | 0.1306 | 0
| 6:30 | 0.2315 | 0
| 7:30 | 0.1788 | 0
| 8:30 | 56.5831 | 0
| 9:30 | 0.1508 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sat, 24/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0.0009 | 0
| 4:30 | 0.0102 | 0
| 5:30 | 0.0121 | 0
| 6:30 | 0.0122 | 0
| 7:30 | 0.0137 | 0
| 8:30 | 0.0093 | 0
| 9:30 | 0.0003 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0.0165 | 0
Sun, 25/Jul | 0:30 | 0.0786 | 0
| 1:30 | 0.22 | 0
| 2:30 | 0.5552 | 0
| 3:30 | 0.9213 | 0
| 4:30 | 1.1574 | 0
| 5:30 | 1.3627 | 0
| 6:30 | 1.433 | 0
| 7:30 | 1.2141 | 0
| 8:30 | 0.8971 | 0
| 9:30 | 0.5917 | 0
| 10:30 | 0.256 | 0
| 11:30 | 0.0579 | 0
| 12:30 | 0.0041 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0146 | 0
| 22:30 | 0.1512 | 0
| 23:30 | 0.4308 | 0
Mon, 26/Jul | 0:30 | 0.6727 | 0
| 1:30 | 0.8591 | 0
| 2:30 | 0.9902 | 0
| 3:30 | 1.0872 | 0
| 4:30 | 1.203 | 0
| 5:30 | 1.2918 | 0
| 6:30 | 1.2902 | 0
| 7:30 | 1.2388 | 0
| 8:30 | 109.5722 | 0
| 9:30 | 2.7535 | 0
| 10:30 | 1.7822 | 0
| 11:30 | 0.9278 | 0
| 12:30 | 0.0187 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Tue, 27/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0.0073 | 0
| 7:30 | 0.0166 | 0
| 8:30 | 54.4178 | 0
| 9:30 | 0.1692 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Wed, 28/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0 | 0
| 8:30 | 45.247 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Thu, 29/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0.0083 | 0
| 8:30 | 48.0322 | 0
| 9:30 | 0.0376 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Fri, 30/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0.0026 | 0
| 5:30 | 0.0242 | 0
| 6:30 | 0.0355 | 0
| 7:30 | 0.0548 | 0
| 8:30 | 56.9839 | 0
| 9:30 | 1.1403 | 0
| 10:30 | 0.6857 | 0
| 11:30 | 0.297 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sat, 31/Jul | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0 | 0
| 8:30 | 0 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sun, 01/Aug | 0:30 | 0 | 0
| 1:30 | 0.0191 | 0
| 2:30 | 0.1705 | 0
| 3:30 | 0.526 | 0
| 4:30 | 0.8103 | 0
| 5:30 | 0.9062 | 0
| 6:30 | 0.8946 | 0
| 7:30 | 0.3485 | 0
| 8:30 | 0.0032 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Mon, 02/Aug | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0.0059 | 0
| 3:30 | 0.011 | 0
| 4:30 | 0.0106 | 0
| 5:30 | 0.0179 | 0
| 6:30 | 0.0222 | 0
| 7:30 | 0.0205 | 0
| 8:30 | 0.0161 | 0
| 9:30 | 0.0089 | 0
| 10:30 | 0.0026 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Tue, 03/Aug | 0:30 | 0.0072 | 0
| 1:30 | 0.029 | 0
| 2:30 | 0.0821 | 0
| 3:30 | 0.0947 | 0
| 4:30 | 0.1002 | 0
| 5:30 | 0.1396 | 0
| 6:30 | 0.1581 | 0
| 7:30 | 0.1495 | 0
| 8:30 | 62.0126 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Wed, 04/Aug | 0:30 | 0 | 0
| 1:30 | 0.011 | 0
| 2:30 | 0.1009 | 0
| 3:30 | 0.2112 | 0
| 4:30 | 0.2366 | 0
| 5:30 | 0.2899 | 0
| 6:30 | 0.2639 | 0
| 7:30 | 0.0708 | 0
| 8:30 | 51.3976 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Thu, 05/Aug | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0 | 0
| 8:30 | 41.8634 | 0
| 9:30 | 0.0146 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Fri, 06/Aug | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0 | 0
| 8:30 | 36.8956 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sat, 07/Aug | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0 | 0
| 8:30 | 0 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sun, 08/Aug | 0:30 | 0.0032 | 0
| 1:30 | 0.0135 | 0
| 2:30 | 0.0075 | 0
| 3:30 | 0.0126 | 0
| 4:30 | 0.0186 | 0
| 5:30 | 0.0224 | 0
| 6:30 | 0.0542 | 0
| 7:30 | 0.1055 | 0
| 8:30 | 0.1373 | 0
| 9:30 | 0.143 | 0
| 10:30 | 0.1426 | 0
| 11:30 | 0.0972 | 0
| 12:30 | 0.0446 | 0
| 13:30 | 0.0627 | 0
| 14:30 | 0.0927 | 0
| 15:30 | 0.1096 | 0
| 16:30 | 0.1305 | 0
| 17:30 | 0.1563 | 0
| 18:30 | 0.1592 | 0
| 19:30 | 0.1647 | 0
| 20:30 | 0.2154 | 0
| 21:30 | 0.294 | 0
| 22:30 | 0.4033 | 0
| 23:30 | 0.5391 | 0
Mon, 09/Aug | 0:30 | 0.6462 | 0
| 1:30 | 0.6802 | 0
| 2:30 | 0.743 | 0
| 3:30 | 0.8366 | 0
| 4:30 | 0.9062 | 0
| 5:30 | 0.9879 | 0
| 6:30 | 1.0666 | 0
| 7:30 | 1.1172 | 0
| 8:30 | 115.5083 | 0
| 9:30 | 3.1229 | 0
| 10:30 | 2.0247 | 0
| 11:30 | 1.3889 | 0
| 12:30 | 1.2677 | 0
| 13:30 | 1.2247 | 0
| 14:30 | 1.1158 | 0
| 15:30 | 0.8633 | 0
| 16:30 | 0.797 | 0
| 17:30 | 1.2417 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0018 | 0
| 22:30 | 0.0561 | 0
| 23:30 | 0.2342 | 0
Tue, 10/Aug | 0:30 | 0.4389 | 0
| 1:30 | 0.5875 | 0
| 2:30 | 0.8455 | 0
| 3:30 | 1.2467 | 0
| 4:30 | 1.8095 | 0
| 5:30 | 2.243 | 0
| 6:30 | 2.1624 | 0
| 7:30 | 1.7664 | 0
| 8:30 | 123.5816 | 0
| 9:30 | 1.6494 | 0
| 10:30 | 0.1758 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0076 | 0
| 22:30 | 0.394 | 0
| 23:30 | 0.8858 | 0
Wed, 11/Aug | 0:30 | 0.9076 | 0
| 1:30 | 0.9727 | 0
| 2:30 | 1.2316 | 0
| 3:30 | 1.3645 | 0
| 4:30 | 1.337 | 0
| 5:30 | 1.2297 | 0
| 6:30 | 1.1363 | 0
| 7:30 | 1.0063 | 0
| 8:30 | 96.4828 | 0
| 9:30 | 1.2043 | 0
| 10:30 | 0.1658 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0058 | 0
| 23:30 | 0.0838 | 0
Thu, 12/Aug | 0:30 | 0.2843 | 0
| 1:30 | 0.73 | 0
| 2:30 | 1.0724 | 0
| 3:30 | 1.1817 | 0
| 4:30 | 1.1496 | 0
| 5:30 | 1.1757 | 0
| 6:30 | 1.0587 | 0
| 7:30 | 0.6662 | 0
| 8:30 | 82.5499 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Fri, 13/Aug | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0 | 0
| 8:30 | 44.0754 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sat, 14/Aug | 0:30 | 0 | 0
| 1:30 | 0.0101 | 0
| 2:30 | 0.0395 | 0
| 3:30 | 0.1197 | 0
| 4:30 | 0.212 | 0
| 5:30 | 0.3107 | 0
| 6:30 | 0.3809 | 0
| 7:30 | 0.3955 | 0
| 8:30 | 0.2804 | 0
| 9:30 | 0.0974 | 0
| 10:30 | 0.0829 | 0
| 11:30 | 0.1433 | 0
| 12:30 | 0.0314 | 0
| 13:30 | 0 | 0
| 14:30 | 0.0002 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0617 | 0
| 22:30 | 0.3896 | 0
| 23:30 | 0.7367 | 0
Sun, 15/Aug | 0:30 | 0.9232 | 0
| 1:30 | 1.1023 | 0
| 2:30 | 1.3238 | 0
| 3:30 | 1.5551 | 0
| 4:30 | 1.7061 | 0
| 5:30 | 1.9454 | 0
| 6:30 | 2.0365 | 0
| 7:30 | 1.7675 | 0
| 8:30 | 1.3293 | 0
| 9:30 | 0.7822 | 0
| 10:30 | 0.415 | 0
| 11:30 | 0.1645 | 0
| 12:30 | 0.0619 | 0
| 13:30 | 0.0346 | 0
| 14:30 | 0.0131 | 0
| 15:30 | 0.0034 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0.0109 | 0
| 20:30 | 0.2865 | 0
| 21:30 | 0.9836 | 0
| 22:30 | 1.3659 | 0
| 23:30 | 1.7355 | 0
Mon, 16/Aug | 0:30 | 2.1363 | 0
| 1:30 | 2.4766 | 0
| 2:30 | 2.5726 | 0
| 3:30 | 2.5105 | 0
| 4:30 | 2.4725 | 0
| 5:30 | 2.4152 | 0
| 6:30 | 2.5075 | 0
| 7:30 | 2.3695 | 0
| 8:30 | 160.7406 | 0
| 9:30 | 3.0158 | 0
| 10:30 | 0.2838 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.1933 | 0
| 22:30 | 0.7839 | 0
| 23:30 | 1.2395 | 0
Tue, 17/Aug | 0:30 | 1.6091 | 0
| 1:30 | 1.7308 | 0
| 2:30 | 1.7355 | 0
| 3:30 | 1.6664 | 0
| 4:30 | 1.6893 | 0
| 5:30 | 1.8854 | 0
| 6:30 | 1.8761 | 0
| 7:30 | 1.6295 | 0
| 8:30 | 131.2676 | 0
| 9:30 | 4.3605 | 0
| 10:30 | 2.6103 | 0
| 11:30 | 1.238 | 0
| 12:30 | 0.0816 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0026 | 0
| 23:30 | 0.1083 | 0
Wed, 18/Aug | 0:30 | 0.513 | 0
| 1:30 | 0.9398 | 0
| 2:30 | 1.241 | 0
| 3:30 | 1.4226 | 0
| 4:30 | 1.4545 | 0
| 5:30 | 1.4342 | 0
| 6:30 | 1.3564 | 0
| 7:30 | 1.1456 | 0
| 8:30 | 103.8899 | 0
| 9:30 | 1.0333 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0.0156 | 0
Thu, 19/Aug | 0:30 | 0.1884 | 0
| 1:30 | 0.6049 | 0
| 2:30 | 0.9174 | 0
| 3:30 | 1.1672 | 0
| 4:30 | 1.3435 | 0
| 5:30 | 1.5741 | 0
| 6:30 | 1.8041 | 0
| 7:30 | 1.5315 | 0
| 8:30 | 111.3658 | 0
| 9:30 | 0.9419 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0037 | 0
| 22:30 | 0.0872 | 0
| 23:30 | 0.2208 | 0
Fri, 20/Aug | 0:30 | 0.3807 | 0
| 1:30 | 0.6331 | 0
| 2:30 | 0.9565 | 0
| 3:30 | 1.2874 | 0
| 4:30 | 1.5951 | 0
| 5:30 | 1.9906 | 0
| 6:30 | 2.1776 | 0
| 7:30 | 1.8176 | 0
| 8:30 | 120.1619 | 0
| 9:30 | 0.7749 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0334 | 0
| 23:30 | 0.3427 | 0
Sat, 21/Aug | 0:30 | 0.7775 | 0
| 1:30 | 1.008 | 0
| 2:30 | 1.2542 | 0
| 3:30 | 1.5436 | 0
| 4:30 | 1.7242 | 0
| 5:30 | 2.0774 | 0
| 6:30 | 2.1519 | 0
| 7:30 | 1.4028 | 0
| 8:30 | 0.6732 | 0
| 9:30 | 0.3466 | 0
| 10:30 | 0.1451 | 0
| 11:30 | 0.0573 | 0
| 12:30 | 0.0673 | 0
| 13:30 | 0.0591 | 0
| 14:30 | 0.0197 | 0
| 15:30 | 0.0127 | 0
| 16:30 | 0.0411 | 0
| 17:30 | 0.1061 | 0
| 18:30 | 0.1734 | 0
| 19:30 | 0.35 | 0
| 20:30 | 0.652 | 0
| 21:30 | 0.9298 | 0
| 22:30 | 1.05 | 0
| 23:30 | 1.0935 | 0
Sun, 22/Aug | 0:30 | 1.1647 | 0
| 1:30 | 1.2613 | 0
| 2:30 | 1.4039 | 0
| 3:30 | 1.6294 | 0
| 4:30 | 1.8999 | 0
| 5:30 | 1.9442 | 0
| 6:30 | 1.7205 | 0
| 7:30 | 1.3018 | 0
| 8:30 | 0.9955 | 0
| 9:30 | 0.823 | 0
| 10:30 | 0.6127 | 0
| 11:30 | 0.4689 | 0
| 12:30 | 0.3003 | 0
| 13:30 | 0.221 | 0
| 14:30 | 0.2218 | 0
| 15:30 | 0.2007 | 0
| 16:30 | 0.2317 | 0
| 17:30 | 0.2625 | 0
| 18:30 | 0.3509 | 0
| 19:30 | 0.4706 | 0
| 20:30 | 0.5755 | 0
| 21:30 | 0.6327 | 0
| 22:30 | 0.6368 | 0
| 23:30 | 0.6853 | 0
Mon, 23/Aug | 0:30 | 0.7872 | 0
| 1:30 | 0.8396 | 0
| 2:30 | 0.8203 | 0
| 3:30 | 0.8308 | 0
| 4:30 | 0.9799 | 0
| 5:30 | 1.1903 | 0
| 6:30 | 1.3647 | 0
| 7:30 | 1.3792 | 0
| 8:30 | 135.2255 | 0
| 9:30 | 2.4432 | 0
| 10:30 | 1.2721 | 0
| 11:30 | 0.6042 | 0
| 12:30 | 0.0237 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0.1226 | 0
| 17:30 | 0.6921 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0.0147 | 0
Tue, 24/Aug | 0:30 | 0.0303 | 0
| 1:30 | 0.0797 | 0
| 2:30 | 0.132 | 0
| 3:30 | 0.1743 | 0
| 4:30 | 0.1573 | 0
| 5:30 | 0.2084 | 0
| 6:30 | 0.3777 | 0
| 7:30 | 0.4713 | 0
| 8:30 | 85.5204 | 0
| 9:30 | 1.6583 | 0
| 10:30 | 1.0728 | 0
| 11:30 | 0.3984 | 0
| 12:30 | 0.0137 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0.0967 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Wed, 25/Aug | 0:30 | 0.0041 | 0
| 1:30 | 0.0244 | 0
| 2:30 | 0.0833 | 0
| 3:30 | 0.1375 | 0
| 4:30 | 0.1932 | 0
| 5:30 | 0.2138 | 0
| 6:30 | 0.2003 | 0
| 7:30 | 0.1938 | 0
| 8:30 | 71.1256 | 0
| 9:30 | 1.117 | 0
| 10:30 | 0.2743 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Thu, 26/Aug | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0.0013 | 0
| 6:30 | 0.0131 | 0
| 7:30 | 0.0142 | 0
| 8:30 | 52.1609 | 0
| 9:30 | 0 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Fri, 27/Aug | 0:30 | 0.0032 | 0
| 1:30 | 0.0375 | 0
| 2:30 | 0.1462 | 0
| 3:30 | 0.2758 | 0
| 4:30 | 0.5728 | 0
| 5:30 | 0.7411 | 0
| 6:30 | 0.6748 | 0
| 7:30 | 0.4551 | 0
| 8:30 | 76.45 | 0
| 9:30 | 0.1675 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sat, 28/Aug | 0:30 | 0 | 0
| 1:30 | 0.0367 | 0
| 2:30 | 0.1616 | 0
| 3:30 | 0.2458 | 0
| 4:30 | 0.3425 | 0
| 5:30 | 0.4845 | 0
| 6:30 | 0.5839 | 0
| 7:30 | 0.489 | 0
| 8:30 | 0.2331 | 0
| 9:30 | 0.0636 | 0
| 10:30 | 0.0057 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Sun, 29/Aug | 0:30 | 0 | 0
| 1:30 | 0.0145 | 0
| 2:30 | 0.094 | 0
| 3:30 | 0.1488 | 0
| 4:30 | 0.1683 | 0
| 5:30 | 0.3002 | 0
| 6:30 | 0.2847 | 0
| 7:30 | 0.1272 | 0
| 8:30 | 0.05 | 0
| 9:30 | 0.0086 | 0
| 10:30 | 0.0003 | 0
| 11:30 | 0 | 0
| 12:30 | 0.0124 | 0
| 13:30 | 0.1566 | 0
| 14:30 | 0.0682 | 0
| 15:30 | 0.0061 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0.0057 | 0
| 20:30 | 0.1761 | 0
| 21:30 | 0.7571 | 0
| 22:30 | 1.1483 | 0
| 23:30 | 1.3678 | 0
Mon, 30/Aug | 0:30 | 1.6518 | 0
| 1:30 | 1.6748 | 0
| 2:30 | 1.6956 | 0
| 3:30 | 1.8648 | 0
| 4:30 | 1.9172 | 0
| 5:30 | 1.9012 | 0
| 6:30 | 1.8348 | 0
| 7:30 | 1.6914 | 0
| 8:30 | 135.9635 | 0
| 9:30 | 2.1607 | 0
| 10:30 | 0.7257 | 0
| 11:30 | 0.0681 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0.0125 | 0
Tue, 31/Aug | 0:30 | 0.1239 | 0
| 1:30 | 0.3081 | 0
| 2:30 | 0.4594 | 0
| 3:30 | 0.5497 | 0
| 4:30 | 0.6236 | 0
| 5:30 | 0.6589 | 0
| 6:30 | 0.6582 | 0
| 7:30 | 0.6205 | 0
| 8:30 | 89.9009 | 0
| 9:30 | 1.5323 | 0
| 10:30 | 0.2931 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Wed, 01/Sep | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0.0017 | 0
| 4:30 | 0.027 | 0
| 5:30 | 0.1244 | 0
| 6:30 | 0.2474 | 0
| 7:30 | 0.4247 | 0
| 8:30 | 75.4902 | 0
| 9:30 | 1.2151 | 0
| 10:30 | 0.0948 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Thu, 02/Sep | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0 | 0
| 6:30 | 0 | 0
| 7:30 | 0 | 0
| 8:30 | 42.2347 | 0
| 9:30 | 0.0604 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Fri, 03/Sep | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0 | 0
| 5:30 | 0.0165 | 0
| 6:30 | 0.0614 | 0
| 7:30 | 0.1527 | 0
| 8:30 | 65.6644 | 0
| 9:30 | 2.1814 | 0
| 10:30 | 0.9174 | 0
| 11:30 | 0.0225 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0.079 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0114 | 0
| 23:30 | 0.0908 | 0
Sat, 04/Sep | 0:30 | 0.2173 | 0
| 1:30 | 0.3412 | 0
| 2:30 | 0.4988 | 0
| 3:30 | 0.5776 | 0
| 4:30 | 0.5509 | 0
| 5:30 | 0.4201 | 0
| 6:30 | 0.2893 | 0
| 7:30 | 0.1521 | 0
| 8:30 | 0.0359 | 0
| 9:30 | 0.0006 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0027 | 0
| 21:30 | 0.0661 | 0
| 22:30 | 0.2324 | 0
| 23:30 | 0.4448 | 0
Sun, 05/Sep | 0:30 | 0.7016 | 0
| 1:30 | 0.9262 | 0
| 2:30 | 1.1043 | 0
| 3:30 | 1.2914 | 0
| 4:30 | 1.4882 | 0
| 5:30 | 1.6955 | 0
| 6:30 | 1.9172 | 0
| 7:30 | 2.002 | 0
| 8:30 | 1.7227 | 0
| 9:30 | 1.2326 | 0
| 10:30 | 0.8208 | 0
| 11:30 | 0.5175 | 0
| 12:30 | 0.2903 | 0
| 13:30 | 0.1466 | 0
| 14:30 | 0.0279 | 0
| 15:30 | 0.0001 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0.1572 | 0
| 20:30 | 0.7744 | 0
| 21:30 | 1.0731 | 0
| 22:30 | 1.4453 | 0
| 23:30 | 1.9105 | 0
Mon, 06/Sep | 0:30 | 2.2285 | 0
| 1:30 | 2.4214 | 0
| 2:30 | 2.5667 | 0
| 3:30 | 2.6558 | 0
| 4:30 | 2.8742 | 0
| 5:30 | 3.1317 | 0
| 6:30 | 3.189 | 0
| 7:30 | 3.1082 | 0
| 8:30 | 207.8209 | 0
| 9:30 | 7.4106 | 0
| 10:30 | 2.3903 | 0
| 11:30 | 0.4374 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0934 | 0
| 23:30 | 0.491 | 0
Tue, 07/Sep | 0:30 | 0.7531 | 0
| 1:30 | 0.9284 | 0
| 2:30 | 0.9813 | 0
| 3:30 | 1.1884 | 0
| 4:30 | 1.3491 | 0
| 5:30 | 1.1978 | 0
| 6:30 | 1.1129 | 0
| 7:30 | 1.0933 | 0
| 8:30 | 115.0772 | 0
| 9:30 | 1.2792 | 0
| 10:30 | 0.0633 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Wed, 08/Sep | 0:30 | 0 | 0
| 1:30 | 0.0156 | 0
| 2:30 | 0.0516 | 0
| 3:30 | 0.0932 | 0
| 4:30 | 0.1244 | 0
| 5:30 | 0.177 | 0
| 6:30 | 0.1968 | 0
| 7:30 | 0.1982 | 0
| 8:30 | 74.5178 | 0
| 9:30 | 1.4779 | 0
| 10:30 | 0.7872 | 0
| 11:30 | 0.204 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0.0183 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0141 | 0
| 23:30 | 0.1183 | 0
Thu, 09/Sep | 0:30 | 0.2214 | 0
| 1:30 | 0.4563 | 0
| 2:30 | 0.8435 | 0
| 3:30 | 1.1339 | 0
| 4:30 | 1.4326 | 0
| 5:30 | 1.5583 | 0
| 6:30 | 1.5603 | 0
| 7:30 | 1.5684 | 0
| 8:30 | 121.7213 | 0
| 9:30 | 3.7442 | 0
| 10:30 | 1.2193 | 0
| 11:30 | 0.0076 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0.433 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.001 | 0
| 21:30 | 0.0912 | 0
| 22:30 | 0.3068 | 0
| 23:30 | 0.5836 | 0
Fri, 10/Sep | 0:30 | 0.8415 | 0
| 1:30 | 1.1726 | 0
| 2:30 | 1.5371 | 0
| 3:30 | 1.7259 | 0
| 4:30 | 2.0109 | 0
| 5:30 | 2.3569 | 0
| 6:30 | 2.3427 | 0
| 7:30 | 2.0137 | 0
| 8:30 | 141.7903 | 0
| 9:30 | 6.4639 | 0
| 10:30 | 4.4183 | 0
| 11:30 | 3.6224 | 0
| 12:30 | 3.037 | 0
| 13:30 | 2.983 | 0
| 14:30 | 3.0465 | 0
| 15:30 | 2.9002 | 0
| 16:30 | 3.5442 | 0
| 17:30 | 4.0725 | 0
| 18:30 | 0.0029 | 0
| 19:30 | 0.101 | 0
| 20:30 | 0.5067 | 0
| 21:30 | 0.9895 | 0
| 22:30 | 1.3153 | 0
| 23:30 | 1.5474 | 0
Sat, 11/Sep | 0:30 | 1.6456 | 0
| 1:30 | 1.8153 | 0
| 2:30 | 1.9498 | 0
| 3:30 | 1.9488 | 0
| 4:30 | 1.9415 | 0
| 5:30 | 1.9611 | 0
| 6:30 | 1.9744 | 0
| 7:30 | 1.954 | 0
| 8:30 | 1.7401 | 0
| 9:30 | 1.4496 | 0
| 10:30 | 1.2366 | 0
| 11:30 | 0.9944 | 0
| 12:30 | 0.7321 | 0
| 13:30 | 0.4673 | 0
| 14:30 | 0.3294 | 0
| 15:30 | 0.3192 | 0
| 16:30 | 0.4337 | 0
| 17:30 | 0.6889 | 0
| 18:30 | 0.851 | 0
| 19:30 | 1.109 | 0
| 20:30 | 1.5333 | 0
| 21:30 | 1.881 | 0
| 22:30 | 2.084 | 0
| 23:30 | 2.1276 | 0
Sun, 12/Sep | 0:30 | 2.2529 | 0
| 1:30 | 2.3945 | 0
| 2:30 | 2.5628 | 0
| 3:30 | 2.7604 | 0
| 4:30 | 2.8354 | 0
| 5:30 | 2.8445 | 0
| 6:30 | 2.8901 | 0
| 7:30 | 2.9086 | 0
| 8:30 | 2.8436 | 0
| 9:30 | 2.7103 | 0
| 10:30 | 2.5381 | 0
| 11:30 | 2.3814 | 0
| 12:30 | 2.2498 | 0
| 13:30 | 2.1775 | 0
| 14:30 | 2.1474 | 0
| 15:30 | 1.9622 | 0
| 16:30 | 1.8184 | 0
| 17:30 | 1.8705 | 0
| 18:30 | 1.8909 | 0
| 19:30 | 2.081 | 0
| 20:30 | 2.3687 | 0
| 21:30 | 2.479 | 0
| 22:30 | 2.6312 | 0
| 23:30 | 2.8373 | 0
Mon, 13/Sep | 0:30 | 3.0236 | 0
| 1:30 | 3.1494 | 0
| 2:30 | 3.4199 | 0
| 3:30 | 3.6697 | 0
| 4:30 | 3.5802 | 0
| 5:30 | 3.4842 | 0
| 6:30 | 3.3546 | 0
| 7:30 | 3.3601 | 0
| 8:30 | 264.9733 | 0
| 9:30 | 19.4032 | 0
| 10:30 | 9.0735 | 0
| 11:30 | 5.9221 | 0
| 12:30 | 3.9806 | 0
| 13:30 | 2.3492 | 0
| 14:30 | 1.1581 | 0
| 15:30 | 0.2266 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0802 | 0
| 22:30 | 0.4429 | 0
| 23:30 | 0.9018 | 0
Tue, 14/Sep | 0:30 | 1.2159 | 0
| 1:30 | 1.5359 | 0
| 2:30 | 1.7493 | 0
| 3:30 | 1.7419 | 0
| 4:30 | 1.8651 | 0
| 5:30 | 2.0536 | 0
| 6:30 | 2.1517 | 0
| 7:30 | 2.1533 | 0
| 8:30 | 171.8715 | 0
| 9:30 | 5.1361 | 0
| 10:30 | 2.0278 | 0
| 11:30 | 0.7561 | 0
| 12:30 | 0.0711 | 0
| 13:30 | 0 | 0
| 14:30 | 0.6624 | 0
| 15:30 | 2.2887 | 0
| 16:30 | 2.8332 | 0
| 17:30 | 2.9683 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0125 | 0
| 21:30 | 0.1337 | 0
| 22:30 | 0.4259 | 0
| 23:30 | 0.6731 | 0
Wed, 15/Sep | 0:30 | 0.7937 | 0
| 1:30 | 0.8751 | 0
| 2:30 | 1.0194 | 0
| 3:30 | 1.2426 | 0
| 4:30 | 1.4121 | 0
| 5:30 | 1.5061 | 0
| 6:30 | 1.5178 | 0
| 7:30 | 1.5331 | 0
| 8:30 | 136.0507 | 0
| 9:30 | 6.1345 | 0
| 10:30 | 4.3221 | 0
| 11:30 | 2.3262 | 0
| 12:30 | 0.4102 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 1.8867 | 0
| 18:30 | 0 | 0
| 19:30 | 0.0005 | 0
| 20:30 | 0.1432 | 0
| 21:30 | 0.6164 | 0
| 22:30 | 0.8703 | 0
| 23:30 | 1.052 | 0
Thu, 16/Sep | 0:30 | 1.2353 | 0
| 1:30 | 1.379 | 0
| 2:30 | 1.4589 | 0
| 3:30 | 1.4509 | 0
| 4:30 | 1.502 | 0
| 5:30 | 1.6075 | 0
| 6:30 | 1.6577 | 0
| 7:30 | 1.7003 | 0
| 8:30 | 136.1666 | 0
| 9:30 | 5.6071 | 0
| 10:30 | 3.2712 | 0
| 11:30 | 1.7381 | 0
| 12:30 | 0.8092 | 0
| 13:30 | 0.2417 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 1.1505 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0122 | 0
| 21:30 | 0.1869 | 0
| 22:30 | 0.5719 | 0
| 23:30 | 0.8509 | 0
Fri, 17/Sep | 0:30 | 1.1034 | 0
| 1:30 | 1.3055 | 0
| 2:30 | 1.3846 | 0
| 3:30 | 1.4725 | 0
| 4:30 | 1.7133 | 0
| 5:30 | 2.1165 | 0
| 6:30 | 2.192 | 0
| 7:30 | 2.2661 | 0
| 8:30 | 153.0372 | 0
| 9:30 | 6.306 | 0
| 10:30 | 3.0032 | 0
| 11:30 | 1.6204 | 0
| 12:30 | 0.6729 | 0
| 13:30 | 0.0279 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0.047 | 0
| 17:30 | 1.4068 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0028 | 0
| 21:30 | 0.0536 | 0
| 22:30 | 0.2277 | 0
| 23:30 | 0.2915 | 0
Sat, 18/Sep | 0:30 | 0.2514 | 0
| 1:30 | 0.53 | 0
| 2:30 | 0.95 | 0
| 3:30 | 1.2088 | 0
| 4:30 | 1.3981 | 0
| 5:30 | 1.6331 | 0
| 6:30 | 1.8557 | 0
| 7:30 | 1.9418 | 0
| 8:30 | 1.8079 | 0
| 9:30 | 1.4772 | 0
| 10:30 | 1.0839 | 0
| 11:30 | 0.6857 | 0
| 12:30 | 1.0669 | 0
| 13:30 | 1.0505 | 0
| 14:30 | 0.6793 | 0
| 15:30 | 0.9983 | 0
| 16:30 | 0.9503 | 0
| 17:30 | 0.7966 | 0
| 18:30 | 0.996 | 0
| 19:30 | 1.2127 | 0
| 20:30 | 1.38 | 0
| 21:30 | 1.5628 | 0
| 22:30 | 1.7135 | 0
| 23:30 | 1.812 | 0
Sun, 19/Sep | 0:30 | 1.8378 | 0
| 1:30 | 1.9313 | 0
| 2:30 | 2.049 | 0
| 3:30 | 2.0938 | 0
| 4:30 | 2.1664 | 0
| 5:30 | 2.2674 | 0
| 6:30 | 2.2746 | 0
| 7:30 | 2.3334 | 0
| 8:30 | 2.35 | 0
| 9:30 | 2.1398 | 0
| 10:30 | 1.7835 | 0
| 11:30 | 1.3886 | 0
| 12:30 | 1.1448 | 0
| 13:30 | 1.2339 | 0
| 14:30 | 1.1787 | 0
| 15:30 | 0.8502 | 0
| 16:30 | 0.8349 | 0
| 17:30 | 0.9468 | 0
| 18:30 | 1.1265 | 0
| 19:30 | 1.5496 | 0
| 20:30 | 1.9895 | 0
| 21:30 | 2.371 | 0
| 22:30 | 2.7289 | 0
| 23:30 | 2.986 | 0
Mon, 20/Sep | 0:30 | 3.1977 | 0
| 1:30 | 3.378 | 0
| 2:30 | 3.4971 | 0
| 3:30 | 3.5263 | 0
| 4:30 | 3.5228 | 0
| 5:30 | 3.4361 | 0
| 6:30 | 3.3738 | 0
| 7:30 | 3.3379 | 0
| 8:30 | 249.5256 | 0
| 9:30 | 14.465 | 0
| 10:30 | 7.5915 | 0
| 11:30 | 6.5133 | 0
| 12:30 | 5.5257 | 0
| 13:30 | 3.8201 | 0
| 14:30 | 2.7675 | 0
| 15:30 | 3.3204 | 0
| 16:30 | 4.2538 | 0
| 17:30 | 5.1379 | 0
| 18:30 | 0.2781 | 0
| 19:30 | 1.1803 | 0
| 20:30 | 1.741 | 0
| 21:30 | 2.158 | 0
| 22:30 | 2.4693 | 0
| 23:30 | 2.6989 | 0
Tue, 21/Sep | 0:30 | 2.9038 | 0
| 1:30 | 3.0693 | 0
| 2:30 | 3.2041 | 0
| 3:30 | 3.3078 | 0
| 4:30 | 3.5016 | 0
| 5:30 | 3.7062 | 0
| 6:30 | 3.7968 | 0
| 7:30 | 3.8815 | 0
| 8:30 | 254.561 | 0
| 9:30 | 23.8723 | 0
| 10:30 | 11.594 | 0
| 11:30 | 7.3186 | 0
| 12:30 | 4.2574 | 0
| 13:30 | 2.0888 | 0
| 14:30 | 1.5147 | 0
| 15:30 | 1.7505 | 0
| 16:30 | 1.8828 | 0
| 17:30 | 2.3775 | 0
| 18:30 | 0.005 | 0
| 19:30 | 0.3729 | 0
| 20:30 | 1.2466 | 0
| 21:30 | 1.8524 | 0
| 22:30 | 2.4248 | 0
| 23:30 | 2.9232 | 0
Wed, 22/Sep | 0:30 | 3.268 | 0
| 1:30 | 3.5406 | 0
| 2:30 | 3.6791 | 0
| 3:30 | 3.8349 | 0
| 4:30 | 4.0168 | 0
| 5:30 | 4.1969 | 0
| 6:30 | 4.3737 | 0
| 7:30 | 4.328 | 0
| 8:30 | 255.852 | 0
| 9:30 | 15.9405 | 0
| 10:30 | 6.7421 | 0
| 11:30 | 4.8904 | 0
| 12:30 | 4.0723 | 0
| 13:30 | 3.3111 | 0
| 14:30 | 3.3051 | 0
| 15:30 | 3.4882 | 0
| 16:30 | 4.0463 | 0
| 17:30 | 4.7166 | 0
| 18:30 | 0.015 | 0
| 19:30 | 0.2244 | 0
| 20:30 | 0.6813 | 0
| 21:30 | 0.8743 | 0
| 22:30 | 0.9222 | 0
| 23:30 | 0.9372 | 0
Thu, 23/Sep | 0:30 | 0.8834 | 0
| 1:30 | 0.8322 | 0
| 2:30 | 0.7983 | 0
| 3:30 | 0.7669 | 0
| 4:30 | 0.7144 | 0
| 5:30 | 0.6995 | 0
| 6:30 | 0.7078 | 0
| 7:30 | 0.7571 | 0
| 8:30 | 105.0234 | 0
| 9:30 | 1.7844 | 0
| 10:30 | 0.5976 | 0
| 11:30 | 0.0707 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0 | 0
Fri, 24/Sep | 0:30 | 0 | 0
| 1:30 | 0 | 0
| 2:30 | 0 | 0
| 3:30 | 0 | 0
| 4:30 | 0.0114 | 0
| 5:30 | 0.0211 | 0
| 6:30 | 0.0355 | 0
| 7:30 | 0.0609 | 0
| 8:30 | 64.7605 | 0
| 9:30 | 0.2985 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0.0487 | 0
| 17:30 | 1.2583 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0337 | 0
| 22:30 | 0.2451 | 0
| 23:30 | 0.5231 | 0
Sat, 25/Sep | 0:30 | 0.611 | 0
| 1:30 | 0.7212 | 0
| 2:30 | 0.7826 | 0
| 3:30 | 0.8011 | 0
| 4:30 | 0.9256 | 0
| 5:30 | 1.0234 | 0
| 6:30 | 0.9319 | 0
| 7:30 | 0.874 | 0
| 8:30 | 0.7382 | 0
| 9:30 | 0.3769 | 0
| 10:30 | 0.1123 | 0
| 11:30 | 0.0172 | 0
| 12:30 | 0.0002 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0108 | 0
| 21:30 | 0.0946 | 0
| 22:30 | 0.2942 | 0
| 23:30 | 0.5872 | 0
Sun, 26/Sep | 0:30 | 0.8261 | 0
| 1:30 | 0.986 | 0
| 2:30 | 1.1205 | 0
| 3:30 | 1.2429 | 0
| 4:30 | 1.2867 | 0
| 5:30 | 1.2053 | 0
| 6:30 | 1.0511 | 0
| 7:30 | 1.0657 | 0
| 8:30 | 0.9687 | 0
| 9:30 | 0.7119 | 0
| 10:30 | 0.4507 | 0
| 11:30 | 0.1874 | 0
| 12:30 | 0.0676 | 0
| 13:30 | 0.0121 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0062 | 0
| 21:30 | 0.0119 | 0
| 22:30 | 0.0833 | 0
| 23:30 | 0.3884 | 0
Mon, 27/Sep | 0:30 | 0.6348 | 0
| 1:30 | 0.7439 | 0
| 2:30 | 0.7892 | 0
| 3:30 | 0.8338 | 0
| 4:30 | 0.8806 | 0
| 5:30 | 0.8161 | 0
| 6:30 | 0.7114 | 0
| 7:30 | 0.6773 | 0
| 8:30 | 111.6278 | 0
| 9:30 | 0.8307 | 0
| 10:30 | 0 | 0
| 11:30 | 0 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0016 | 0
| 23:30 | 0.047 | 0
Tue, 28/Sep | 0:30 | 0.1813 | 0
| 1:30 | 0.3833 | 0
| 2:30 | 0.5238 | 0
| 3:30 | 0.5953 | 0
| 4:30 | 0.6424 | 0
| 5:30 | 0.6385 | 0
| 6:30 | 0.62 | 0
| 7:30 | 0.7019 | 0
| 8:30 | 100.6389 | 0
| 9:30 | 1.7286 | 0
| 10:30 | 0.7181 | 0
| 11:30 | 0.0475 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0.0121 | 0
Wed, 29/Sep | 0:30 | 0.0398 | 0
| 1:30 | 0.0814 | 0
| 2:30 | 0.1269 | 0
| 3:30 | 0.1991 | 0
| 4:30 | 0.2936 | 0
| 5:30 | 0.4281 | 0
| 6:30 | 0.4318 | 0
| 7:30 | 0.4702 | 0
| 8:30 | 85.1557 | 0
| 9:30 | 2.421 | 0
| 10:30 | 1.936 | 0
| 11:30 | 1.4069 | 0
| 12:30 | 0.796 | 0
| 13:30 | 0.3331 | 0
| 14:30 | 0.0039 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0.3451 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0.0051 | 0
| 23:30 | 0.0652 | 0
Thu, 30/Sep | 0:30 | 0.1869 | 0
| 1:30 | 0.3082 | 0
| 2:30 | 0.4215 | 0
| 3:30 | 0.4779 | 0
| 4:30 | 0.6069 | 0
| 5:30 | 0.69 | 0
| 6:30 | 0.6966 | 0
| 7:30 | 0.6918 | 0
| 8:30 | 91.8242 | 0
| 9:30 | 3.1392 | 0
| 10:30 | 2.428 | 0
| 11:30 | 1.8702 | 0
| 12:30 | 1.6955 | 0
| 13:30 | 1.4687 | 0
| 14:30 | 1.4185 | 0
| 15:30 | 1.3577 | 0
| 16:30 | 1.3311 | 0
| 17:30 | 1.7175 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0.0149 | 0
Fri, 01/Oct | 0:30 | 0.1878 | 0
| 1:30 | 0.7202 | 0
| 2:30 | 1.3017 | 0
| 3:30 | 1.8795 | 0
| 4:30 | 2.3674 | 0
| 5:30 | 2.784 | 0
| 6:30 | 3.1293 | 0
| 7:30 | 3.283 | 0
| 8:30 | 192.3396 | 0
| 9:30 | 18.2774 | 0
| 10:30 | 10.7733 | 0
| 11:30 | 8.9376 | 0
| 12:30 | 6.5268 | 0
| 13:30 | 3.6488 | 0
| 14:30 | 1.3634 | 0
| 15:30 | 0.2479 | 0
| 16:30 | 1.1852 | 0
| 17:30 | 3.5327 | 0
| 18:30 | 0.0284 | 0
| 19:30 | 0.512 | 0
| 20:30 | 1.1392 | 0
| 21:30 | 1.4111 | 0
| 22:30 | 1.6341 | 0
| 23:30 | 1.734 | 0
Sat, 02/Oct | 0:30 | 2.1425 | 0
| 1:30 | 2.7098 | 0
| 2:30 | 2.9092 | 0
| 3:30 | 2.8609 | 0
| 4:30 | 2.983 | 0
| 5:30 | 3.2548 | 0
| 6:30 | 3.4747 | 0
| 7:30 | 3.7374 | 0
| 8:30 | 3.7166 | 0
| 9:30 | 3.3243 | 0
| 10:30 | 3.0524 | 0
| 11:30 | 2.6902 | 0
| 12:30 | 2.3762 | 0
| 13:30 | 2.1529 | 0
| 14:30 | 2.1061 | 0
| 15:30 | 2.1049 | 0
| 16:30 | 2.0589 | 0
| 17:30 | 2.297 | 0
| 18:30 | 2.6284 | 0
| 19:30 | 2.9762 | 0
| 20:30 | 3.2463 | 0
| 21:30 | 3.4588 | 0
| 22:30 | 3.7338 | 0
| 23:30 | 4.1443 | 0
Sun, 03/Oct | 0:30 | 4.399 | 0
| 1:30 | 4.6929 | 0
| 2:30 | 5.1179 | 0
| 3:30 | 5.4341 | 0
| 4:30 | 5.6137 | 0
| 5:30 | 5.7767 | 0
| 6:30 | 5.9604 | 0
| 7:30 | 6.0841 | 0
| 8:30 | 6.0341 | 0
| 9:30 | 5.6463 | 0
| 10:30 | 4.9739 | 0
| 11:30 | 4.2157 | 0
| 12:30 | 3.6515 | 0
| 13:30 | 3.336 | 0
| 14:30 | 3.189 | 0
| 15:30 | 3.0598 | 0
| 16:30 | 2.8833 | 0
| 17:30 | 2.8137 | 0
| 18:30 | 3.1353 | 0
| 19:30 | 3.7808 | 0
| 20:30 | 4.47 | 0
| 21:30 | 4.9883 | 0
| 22:30 | 5.3798 | 0
| 23:30 | 5.7438 | 0
Mon, 04/Oct | 0:30 | 5.9391 | 0
| 1:30 | 6.0518 | 0
| 2:30 | 6.2939 | 0
| 3:30 | 6.607 | 0
| 4:30 | 6.7628 | 0
| 5:30 | 6.9012 | 0
| 6:30 | 6.995 | 0
| 7:30 | 6.9765 | 0
| 8:30 | 444.1393 | 0
| 9:30 | 59.5988 | 0
| 10:30 | 23.0105 | 0
| 11:30 | 12.3332 | 0
| 12:30 | 9.1927 | 0
| 13:30 | 7.1963 | 0
| 14:30 | 6.5458 | 0
| 15:30 | 6.7605 | 0
| 16:30 | 7.3193 | 0
| 17:30 | 8.6525 | 0
| 18:30 | 0.893 | 0
| 19:30 | 1.8071 | 0
| 20:30 | 2.6107 | 0
| 21:30 | 3.1837 | 0
| 22:30 | 3.6297 | 0
| 23:30 | 4.2543 | 0
Tue, 05/Oct | 0:30 | 4.7924 | 0
| 1:30 | 5.263 | 0
| 2:30 | 5.8059 | 0
| 3:30 | 6.0874 | 0
| 4:30 | 6.1842 | 0
| 5:30 | 6.3449 | 0
| 6:30 | 6.524 | 0
| 7:30 | 6.6251 | 0
| 8:30 | 398.8916 | 0
| 9:30 | 52.3095 | 0
| 10:30 | 23.4547 | 0
| 11:30 | 10.5513 | 0
| 12:30 | 5.9328 | 0
| 13:30 | 3.9857 | 0
| 14:30 | 3.2836 | 0
| 15:30 | 2.5515 | 0
| 16:30 | 2.2963 | 0
| 17:30 | 4.6617 | 0
| 18:30 | 0.3715 | 0
| 19:30 | 1.486 | 0
| 20:30 | 2.33 | 0
| 21:30 | 2.9715 | 0
| 22:30 | 3.5099 | 0
| 23:30 | 4.0389 | 0
Wed, 06/Oct | 0:30 | 4.412 | 0
| 1:30 | 4.7509 | 0
| 2:30 | 5.0864 | 0
| 3:30 | 5.2245 | 0
| 4:30 | 5.5327 | 0
| 5:30 | 5.7735 | 0
| 6:30 | 5.7253 | 0
| 7:30 | 5.8839 | 0
| 8:30 | 361.7182 | 0
| 9:30 | 52.9155 | 0
| 10:30 | 24.4829 | 0
| 11:30 | 10.6816 | 0
| 12:30 | 6.7957 | 0
| 13:30 | 4.9659 | 0
| 14:30 | 3.4645 | 0
| 15:30 | 2.1068 | 0
| 16:30 | 3.0326 | 0
| 17:30 | 5.5044 | 0
| 18:30 | 0.2726 | 0
| 19:30 | 0.994 | 0
| 20:30 | 1.5375 | 0
| 21:30 | 2.0196 | 0
| 22:30 | 2.3561 | 0
| 23:30 | 2.5057 | 0
Thu, 07/Oct | 0:30 | 2.4615 | 0
| 1:30 | 2.4957 | 0
| 2:30 | 2.6655 | 0
| 3:30 | 2.7681 | 0
| 4:30 | 2.9463 | 0
| 5:30 | 3.2654 | 0
| 6:30 | 3.516 | 0
| 7:30 | 3.7203 | 0
| 8:30 | 240.637 | 0
| 9:30 | 20.9 | 0
| 10:30 | 8.9038 | 0
| 11:30 | 5.748 | 0
| 12:30 | 4.4224 | 0
| 13:30 | 3.3351 | 0
| 14:30 | 2.633 | 0
| 15:30 | 2.7079 | 0
| 16:30 | 3.6377 | 0
| 17:30 | 4.4753 | 0
| 18:30 | 0.0143 | 0
| 19:30 | 0.2138 | 0
| 20:30 | 0.7874 | 0
| 21:30 | 1.1645 | 0
| 22:30 | 1.3241 | 0
| 23:30 | 1.2757 | 0
Fri, 08/Oct | 0:30 | 1.1228 | 0
| 1:30 | 1.0646 | 0
| 2:30 | 1.0086 | 0
| 3:30 | 0.8894 | 0
| 4:30 | 0.8134 | 0
| 5:30 | 0.7022 | 0
| 6:30 | 0.5694 | 0
| 7:30 | 0.5157 | 0
| 8:30 | 99.036 | 0
| 9:30 | 1.293 | 0
| 10:30 | 0.798 | 0
| 11:30 | 0.7558 | 0
| 12:30 | 0.4836 | 0
| 13:30 | 0.3315 | 0
| 14:30 | 0.5572 | 0
| 15:30 | 1.4948 | 0
| 16:30 | 2.6811 | 0
| 17:30 | 3.2936 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0.0071 | 0
| 21:30 | 0.1018 | 0
| 22:30 | 0.4209 | 0
| 23:30 | 0.8305 | 0
Sat, 09/Oct | 0:30 | 1.095 | 0
| 1:30 | 1.4367 | 0
| 2:30 | 1.7293 | 0
| 3:30 | 2.0218 | 0
| 4:30 | 2.2311 | 0
| 5:30 | 2.4078 | 0
| 6:30 | 2.5084 | 0
| 7:30 | 2.5047 | 0
| 8:30 | 2.5147 | 0
| 9:30 | 2.3928 | 0
| 10:30 | 2.1086 | 0
| 11:30 | 1.8205 | 0
| 12:30 | 1.4801 | 0
| 13:30 | 1.1926 | 0
| 14:30 | 0.9945 | 0
| 15:30 | 0.7887 | 0
| 16:30 | 0.7609 | 0
| 17:30 | 0.9843 | 0
| 18:30 | 1.2542 | 0
| 19:30 | 1.6283 | 0
| 20:30 | 2.2726 | 0
| 21:30 | 2.7956 | 0
| 22:30 | 3.1273 | 0
| 23:30 | 3.2459 | 0
Sun, 10/Oct | 0:30 | 3.2446 | 0
| 1:30 | 3.4057 | 0
| 2:30 | 3.6397 | 0
| 3:30 | 3.6988 | 0
| 4:30 | 3.6478 | 0
| 5:30 | 3.6508 | 0
| 6:30 | 3.6432 | 0
| 7:30 | 3.6502 | 0
| 8:30 | 3.4745 | 0
| 9:30 | 3.095 | 0
| 10:30 | 2.6791 | 0
| 11:30 | 2.2296 | 0
| 12:30 | 1.7728 | 0
| 13:30 | 1.3861 | 0
| 14:30 | 1.119 | 0
| 15:30 | 0.942 | 0
| 16:30 | 0.9401 | 0
| 17:30 | 1.1056 | 0
| 18:30 | 1.3233 | 0
| 19:30 | 1.8071 | 0
| 20:30 | 2.294 | 0
| 21:30 | 2.4774 | 0
| 22:30 | 2.6223 | 0
| 23:30 | 2.6844 | 0
Mon, 11/Oct | 0:30 | 2.6606 | 0
| 1:30 | 2.8654 | 0
| 2:30 | 3.0856 | 0
| 3:30 | 3.1999 | 0
| 4:30 | 3.4661 | 0
| 5:30 | 3.7664 | 0
| 6:30 | 3.9478 | 0
| 7:30 | 4.0203 | 0
| 8:30 | 284.1477 | 0
| 9:30 | 20.9725 | 0
| 10:30 | 8.7074 | 0
| 11:30 | 5.5458 | 0
| 12:30 | 3.6961 | 0
| 13:30 | 2.4726 | 0
| 14:30 | 1.7006 | 0
| 15:30 | 1.2093 | 0
| 16:30 | 1.7126 | 0
| 17:30 | 2.8301 | 0
| 18:30 | 0 | 0
| 19:30 | 0.0299 | 0
| 20:30 | 0.5324 | 0
| 21:30 | 1.0783 | 0
| 22:30 | 1.3477 | 0
| 23:30 | 1.6794 | 0
Tue, 12/Oct | 0:30 | 1.9218 | 0
| 1:30 | 2.1367 | 0
| 2:30 | 2.3677 | 0
| 3:30 | 2.3815 | 0
| 4:30 | 2.4078 | 0
| 5:30 | 2.4216 | 0
| 6:30 | 2.3776 | 0
| 7:30 | 2.4693 | 0
| 8:30 | 197.126 | 0
| 9:30 | 8.2873 | 0
| 10:30 | 3.4126 | 0
| 11:30 | 0.9946 | 0
| 12:30 | 0.6633 | 0
| 13:30 | 1.472 | 0
| 14:30 | 1.9246 | 0
| 15:30 | 2.0569 | 0
| 16:30 | 2.4492 | 0
| 17:30 | 3.0811 | 0
| 18:30 | 0 | 0
| 19:30 | 0.0002 | 0
| 20:30 | 0.0517 | 0
| 21:30 | 0.1859 | 0
| 22:30 | 0.3146 | 0
| 23:30 | 0.4626 | 0
Wed, 13/Oct | 0:30 | 0.5407 | 0
| 1:30 | 0.5786 | 0
| 2:30 | 0.6311 | 0
| 3:30 | 0.6961 | 0
| 4:30 | 0.7542 | 0
| 5:30 | 0.8098 | 0
| 6:30 | 0.8249 | 0
| 7:30 | 0.8616 | 0
| 8:30 | 114.586 | 0
| 9:30 | 2.8825 | 0
| 10:30 | 1.6531 | 0
| 11:30 | 0.473 | 0
| 12:30 | 0.0071 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0.032 | 0
| 17:30 | 0.7988 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0.0111 | 0
Thu, 14/Oct | 0:30 | 0.0277 | 0
| 1:30 | 0.075 | 0
| 2:30 | 0.1253 | 0
| 3:30 | 0.173 | 0
| 4:30 | 0.205 | 0
| 5:30 | 0.244 | 0
| 6:30 | 0.2648 | 0
| 7:30 | 0.307 | 0
| 8:30 | 84.378 | 0
| 9:30 | 1.8955 | 0
| 10:30 | 1.0594 | 0
| 11:30 | 0.204 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0.0851 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0 | 0
| 22:30 | 0 | 0
| 23:30 | 0.0173 | 0
Fri, 15/Oct | 0:30 | 0.0902 | 0
| 1:30 | 0.2315 | 0
| 2:30 | 0.4912 | 0
| 3:30 | 0.7583 | 0
| 4:30 | 0.9431 | 0
| 5:30 | 1.1246 | 0
| 6:30 | 1.3998 | 0
| 7:30 | 1.7021 | 0
| 8:30 | 136.4963 | 0
| 9:30 | 6.3516 | 0
| 10:30 | 2.6327 | 0
| 11:30 | 0.2334 | 0
| 12:30 | 0 | 0
| 13:30 | 0 | 0
| 14:30 | 0 | 0
| 15:30 | 0 | 0
| 16:30 | 0 | 0
| 17:30 | 0.9032 | 0
| 18:30 | 0 | 0
| 19:30 | 0 | 0
| 20:30 | 0 | 0
| 21:30 | 0.0639 | 0
| 22:30 | 0.3992 | 0
| 23:30 | 0.6893 | 0
Sat, 16/Oct | 0:30 | 0.6703 | 0
| 1:30 | 1.2141 | 0
| 2:30 | 1.8481 | 0
| 3:30 | 1.8703 | 0
| 4:30 | 1.9775 | 0
| 5:30 | 2.2925 | 0
| 6:30 | 2.2054 | 0
| 7:30 | 1.8784 | 0
| 8:30 | 1.7936 | 0
| 9:30 | 1.5095 | 0
| 10:30 | 1.1239 | 0
| 11:30 | 0.9319 | 0
| 12:30 | 0.7909 | 0
| 13:30 | 0.7134 | 0
| 14:30 | 0.6593 | 0
| 15:30 | 0.5929 | 0
| 16:30 | 0.5489 | 0
| 17:30 | 0.6315 | 0
| 18:30 | 0.7676 | 0
| 19:30 | 0.8961 | 0
| 20:30 | 0.9829 | 0
| 21:30 | 0.9582 | 0
| 22:30 | 1.0113 | 0
| 23:30 | 1.1665 | 0
Sun, 17/Oct | 0:30 | 1.2991 | 0
| 1:30 | 1.4799 | 0
| 2:30 | 1.6686 | 0
| 3:30 | 1.7549 | 0
| 4:30 | 1.9063 | 0
| 5:30 | 2.0971 | 0
| 6:30 | 2.167 | 0
| 7:30 | 2.2805 | 0
| 8:30 | 2.4744 | 0
| 9:30 | 2.5485 | 0
| 10:30 | 2.4812 | 0
| 11:30 | 2.2108 | 0
| 12:30 | 1.5808 | 0
| 13:30 | 1.2805 | 0
| 14:30 | 1.2292 | 0
| 15:30 | 1.1397 | 0
| 16:30 | 1.2109 | 0
| 17:30 | 1.3823 | 0
| 18:30 | 1.6033 | 0
| 19:30 | 1.8459 | 0
| 20:30 | 2.0027 | 0
| 21:30 | 2.0269 | 0
| 22:30 | 1.9967 | 0
| 23:30 | 2.0858 | 0
Mon, 18/Oct | 0:30 | 2.2487 | 0
| 1:30 | 2.3602 | 0
| 2:30 | 2.2697 | 0
| 3:30 | 2.0578 | 0
| 4:30 | 2.4895 | 0
| 5:30 | 3.2857 | 0
| 6:30 | 3.6803 | 0
| 7:30 | 3.7035 | 0
| 8:30 | 263.3539 | 0
| 9:30 | 24.3696 | 0
| 10:30 | 11.6095 | 0
| 11:30 | 7.4091 | 0
| 12:30 | 4.682 | 0
| 13:30 | 5.8693 | 0
| 14:30 | 6.3168 | 0
| 15:30 | 4.3005 | 0
| 16:30 | 3.8894 | 0
| 17:30 | 5.6813 | 0
| 18:30 | 0.6042 | 0
| 19:30 | 1.2557 | 0
| 20:30 | 1.6188 | 0
| 21:30 | 1.9146 | 0
| 22:30 | 2.1055 | 0
| 23:30 | 2.262 | 0
Tue, 19/Oct | 0:30 | 2.2452 | 0
| 1:30 | 2.2271 | 0
| 2:30 | 2.3109 | 0
| 3:30 | 2.432 | 0
| 4:30 | 2.6807 | 0
| 5:30 | 2.8281 | 0
| 6:30 | 2.8994 | 0
| 7:30 | 3.1955 | 0
| 8:30 | 223.6768 | 0
| 9:30 | 21.3247 | 0
| 10:30 | 9.606 | 0
| 11:30 | 5.9735 | 0
| 12:30 | 4.3341 | 0
| 13:30 | 3.6555 | 0
| 14:30 | 3.9559 | 0
| 15:30 | 4.8072 | 0
| 16:30 | 5.9325 | 0
| 17:30 | 7.1473 | 0
| 18:30 | 0.4359 | 0
| 19:30 | 1.1775 | 0
| 20:30 | 1.6716 | 0
| 21:30 | 2.114 | 0
| 22:30 | 2.5978 | 0
| 23:30 | 2.9756 | 0
Wed, 20/Oct | 0:30 | 3.1905 | 0
| 1:30 | 3.2797 | 0
| 2:30 | 3.4475 | 0
| 3:30 | 3.661 | 0
| 4:30 | 3.8406 | 0
| 5:30 | 4.0794 | 0
| 6:30 | 4.3265 | 0
| 7:30 | 4.5081 | 0
| 8:30 | 273.2206 | 0
| 9:30 | 35.4997 | 0
| 10:30 | 19.9368 | 0
| 11:30 | 12.1294 | 0
| 12:30 | 8.447 | 0
| 13:30 | 6.6052 | 0
| 14:30 | 6.2508 | 0
| 15:30 | 5.3031 | 0
| 16:30 | 5.8057 | 0
| 17:30 | 8.5351 | 0
| 18:30 | 1.4155 | 0
| 19:30 | 2.2168 | 0
| 20:30 | 2.9791 | 0
| 21:30 | 3.4837 | 0
| 22:30 | 3.8768 | 0
| 23:30 | 4.2271 | 0
Thu, 21/Oct | 0:30 | 4.4934 | 0
| 1:30 | 4.8297 | 0
| 2:30 | 5.0386 | 0
| 3:30 | 5.0989 | 0
| 4:30 | 5.1269 | 0
| 5:30 | 5.2576 | 0
| 6:30 | 5.1764 | 0
| 7:30 | 5.0789 | 0
| 8:30 | 304.8205 | 0
| 9:30 | 37.7079 | 0
| 10:30 | 16.1322 | 0
| 11:30 | 8.8932 | 0
| 12:30 | 5.4732 | 0
| 13:30 | 4.1315 | 0
| 14:30 | 4.5148 | 0
| 15:30 | 4.9077 | 0
| 16:30 | 4.8248 | 0
| 17:30 | 4.3747 | 0
| 18:30 | 0.0078 | 0
| 19:30 | 0.1189 | 0
| 20:30 | 0.3043 | 0
| 21:30 | 0.4622 | 0
| 22:30 | 0.6374 | 0
| 23:30 | 0.6934 | 0
Fri, 22/Oct | 0:30 | 0.6529 | 0
| 1:30 | 0.6469 | 0
| 2:30 | 0.6262 | 0
| 3:30 | 0.5742 | 0
| 4:30 | 0.6112 | 0
| 5:30 | 0.6929 | 0
| 6:30 | 0.6969 | 0
| 7:30 | 0.7317 | 0
| 8:30 | 102.256 | 0
| 9:30 | 2.9639 | 0
| 10:30 | 2.35 | 0
| 11:30 | 1.9445 | 0
| 12:30 | 1.5891 | 0
| 13:30 | 1.3496 | 0
| 14:30 | 0.6209 | 0
| 15:30 | 0 | 0
| 16:30 | 0.5627 | 0
| 17:30 | 2.8238 | 0
| 18:30 | 0 | 0
| 19:30 | 0.0217 | 0
| 20:30 | 0.6545 | 0
| 21:30 | 1.2248 | 0
| 22:30 | 1.6581 | 0
| 23:30 | 2.0729 | 0
Sat, 23/Oct | 0:30 | 2.3443 | 0
| 1:30 | 2.5578 | 0
| 2:30 | 2.7621 | 0
| 3:30 | 2.9763 | 0
| 4:30 | 3.1922 | 0
| 5:30 | 3.4504 | 0
| 6:30 | 3.707 | 0
| 7:30 | 3.9322 | 0
| 8:30 | 4.0416 | 0
| 9:30 | 3.8325 | 0
| 10:30 | 3.3914 | 0
| 11:30 | 2.7762 | 0
| 12:30 | 2.3846 | 0
| 13:30 | 2.2964 | 0
| 14:30 | 2.1069 | 0
| 15:30 | 1.9523 | 0
| 16:30 | 2.1606 | 0
| 17:30 | 2.4501 | 0
| 18:30 | 2.6832 | 0
| 19:30 | 3.0207 | 0
| 20:30 | 3.2776 | 0
| 21:30 | 3.3432 | 0
| 22:30 | 3.3444 | 0
| 23:30 | 3.3939 | 0
Sun, 24/Oct | 0:30 | 3.3795 | 0
| 1:30 | 3.351 | 0
| 2:30 | 3.3923 | 0
| 3:30 | 3.384 | 0
| 4:30 | 3.2776 | 0
| 5:30 | 3.2964 | 0
| 6:30 | 3.3962 | 0
| 7:30 | 3.403 | 0
| 8:30 | 3.338 | 0
| 9:30 | 3.2131 | 0
| 10:30 | 2.9421 | 0
| 11:30 | 2.6939 | 0
| 12:30 | 2.4133 | 0
| 13:30 | 2.0781 | 0
| 14:30 | 2.0352 | 0
| 15:30 | 1.9747 | 0
| 16:30 | 1.9892 | 0
| 17:30 | 2.1836 | 0
| 18:30 | 2.2864 | 0
| 19:30 | 2.4272 | 0
| 20:30 | 2.6921 | 0
| 21:30 | 2.9485 | 0
| 22:30 | 3.169 | 0
| 23:30 | 3.4411 | 0
Mon, 25/Oct | 0:30 | 3.6815 | 0
| 1:30 | 3.9684 | 0
| 2:30 | 4.1963 | 0
| 3:30 | 4.236 | 0
| 4:30 | 4.3477 | 0
| 5:30 | 4.6271 | 0
| 6:30 | 4.9137 | 0
| 7:30 | 5.2046 | 0
| 8:30 | 5.4438 | 0
| 9:30 | 5.454 | 0
| 10:30 | 5.3793 | 0
| 11:30 | 5.1975 | 0
| 12:30 | 4.6894 | 0
| 13:30 | 4.3817 | 0
| 14:30 | 4.3479 | 0
| 15:30 | 4.1492 | 0
| 16:30 | 4.2962 | 0
| 17:30 | 4.7415 | 0
| 18:30 | 5.0169 | 0
| 19:30 | 5.4179 | 0
| 20:30 | 5.9608 | 0
| 21:30 | 6.4533 | 0
| 22:30 | 6.8953 | 0
| 23:30 | 7.2136 | 0
Tue, 26/Oct | 0:30 | 7.4485 | 0
| 1:30 | 7.6117 | 0
| 2:30 | 7.7099 | 0
| 3:30 | 7.8945 | 0
| 4:30 | 8.2382 | 0
| 5:30 | 8.5963 | 0
| 6:30 | 8.8826 | 0
| 7:30 | 9.1161 | 0
| 8:30 | 563.0961 | 0
| 9:30 | 106.1395 | 0
| 10:30 | 62.5202 | 0
| 11:30 | 40.7143 | 0
| 12:30 | 27.0678 | 0
| 13:30 | 16.4547 | 0
| 14:30 | 10.276 | 0
| 15:30 | 8.1532 | 0
| 16:30 | 8.785 | 0
| 17:30 | 13.9577 | 0
| 18:30 | 2.2678 | 0
| 19:30 | 3.1801 | 0
| 20:30 | 4.0251 | 0
| 21:30 | 4.6734 | 0
| 22:30 | 4.9991 | 0
| 23:30 | 5.5596 | 0
Wed, 27/Oct | 0:30 | 6.0905 | 0
| 1:30 | 6.3561 | 0
| 2:30 | 6.4576 | 0
| 3:30 | 6.6835 | 0
| 4:30 | 6.7102 | 0
| 5:30 | 6.6252 | 0
| 6:30 | 6.8561 | 0
| 7:30 | 6.7595 | 0
| 8:30 | 407.415 | 0
| 9:30 | 48.3755 | 0
| 10:30 | 25.018 | 0
| 11:30 | 12.7029 | 0
| 12:30 | 7.0252 | 0
| 13:30 | 5.0342 | 0
| 14:30 | 4.9261 | 0
| 15:30 | 5.2442 | 0
| 16:30 | 6.5285 | 0
| 17:30 | 8.5999 | 0
| 18:30 | 0.5838 | 0
| 19:30 | 1.2831 | 0
| 20:30 | 1.6657 | 0
| 21:30 | 2.1384 | 0
| 22:30 | 2.5416 | 0
| 23:30 | 2.6763 | 0
Thu, 28/Oct | 0:30 | 2.6901 | 0
| 1:30 | 2.7055 | 0
| 2:30 | 2.4553 | 0
| 3:30 | 2.2941 | 0
| 4:30 | 2.4656 | 0
| 5:30 | 2.678 | 0
| 6:30 | 2.8043 | 0
| 7:30 | 2.7821 | 0
| 8:30 | 220.4481 | 0
| 9:30 | 11.1868 | 0
| 10:30 | 9.2756 | 0
| 11:30 | 7.8745 | 0
| 12:30 | 4.1108 | 0
| 13:30 | 3.1054 | 0
| 14:30 | 2.8469 | 0
| 15:30 | 3.1862 | 0
| 16:30 | 3.7729 | 0
| 17:30 | 4.3298 | 0
| 18:30 | 0.0242 | 0
| 19:30 | 0.3918 | 0
| 20:30 | 1.0821 | 0
| 21:30 | 1.5658 | 0
| 22:30 | 2.0467 | 0
| 23:30 | 2.3518 | 0
Fri, 29/Oct | 0:30 | 2.3168 | 0
| 1:30 | 2.3201 | 0
| 2:30 | 2.3493 | 0
| 3:30 | 2.2681 | 0
| 4:30 | 2.1339 | 0
| 5:30 | 1.9128 | 0
| 6:30 | 1.781 | 0
| 7:30 | 1.638 | 0
| 8:30 | 150.8221 | 0
| 9:30 | 2.4442 | 0
| 10:30 | 1.8419 | 0
| 11:30 | 1.4547 | 0
| 12:30 | 1.1936 | 0
| 13:30 | 1.3653 | 0
| 14:30 | 1.5879 | 0
| 15:30 | 2.2119 | 0
| 16:30 | 3.345 | 0
| 17:30 | 4.1571 | 0
| 18:30 | 0 | 0
| 19:30 | 0.0154 | 0
| 20:30 | 0.1775 | 0
| 21:30 | 0.5006 | 0
| 22:30 | 0.7445 | 0
| 23:30 | 0.994 | 0
Sat, 30/Oct | 0:30 | 1.2265 | 0
| 1:30 | 1.4048 | 0
| 2:30 | 1.6359 | 0
| 3:30 | 1.8085 | 0
| 4:30 | 1.8981 | 0
| 5:30 | 1.9811 | 0
| 6:30 | 2.1046 | 0
| 7:30 | 2.202 | 0
| 8:30 | 2.2029 | 0
| 9:30 | 2.2744 | 0
| 10:30 | 2.1227 | 0
| 11:30 | 1.7306 | 0
| 12:30 | 1.3803 | 0
| 13:30 | 1.2104 | 0
| 14:30 | 1.1555 | 0
| 15:30 | 1.0949 | 0
| 16:30 | 1.5058 | 0
| 17:30 | 1.9713 | 0
| 18:30 | 2.0479 | 0
| 19:30 | 2.3285 | 0
| 20:30 | 2.7217 | 0
| 21:30 | 2.9544 | 0
| 22:30 | 3.136 | 0
| 23:30 | 3.3841 | 0
Sun, 31/Oct | 0:30 | 3.6094 | 0
| 1:30 | 3.7727 | 0
| 2:30 | 3.8627 | 0
| 3:30 | 3.8226 | 0
| 4:30 | 3.9466 | 0
| 5:30 | 4.196 | 0
| 6:30 | 4.1865 | 0
| 7:30 | 4.206 | 0
| 8:30 | 4.2616 | 0
| 9:30 | 4.0389 | 0
| 10:30 | 3.5062 | 0
| 11:30 | 2.7568 | 0
| 12:30 | 2.1947 | 0
| 13:30 | 1.8055 | 0
| 14:30 | 1.5271 | 0
| 15:30 | 1.5364 | 0
| 16:30 | 1.7102 | 0
| 17:30 | 1.8659 | 0
| 18:30 | 1.8962 | 0
| 19:30 | 1.8571 | 0
| 20:30 | 1.8729 | 0
| 21:30 | 1.9659 | 0
| 22:30 | 2.1098 | 0
| 23:30 | 2.4204 | 0
Mon, 01/Nov | 0:30 | 3.2988 | 0
| 1:30 | 4.3811 | 0
| 2:30 | 5.1723 | 0
| 3:30 | 5.8607 | 0
| 4:30 | 6.3914 | 0
| 5:30 | 6.8173 | 0
| 6:30 | 6.9109 | 0
| 7:30 | 6.7137 | 0
| 8:30 | 407.8712 | 0
| 9:30 | 50.8892 | 0
| 10:30 | 29.0336 | 0
| 11:30 | 16.2908 | 0
| 12:30 | 10.2211 | 0
| 13:30 | 8.4739 | 0
| 14:30 | 7.4856 | 0
| 15:30 | 7.9 | 0
| 16:30 | 9.3487 | 0
| 17:30 | 10.2448 | 0
| 18:30 | 1.1514 | 0
| 19:30 | 1.7802 | 0
| 20:30 | 2.2256 | 0
| 21:30 | 2.539 | 0
| 22:30 | 2.8024 | 0
| 23:30 | 3.1065 | 0
Tue, 02/Nov | 0:30 | 3.426 | 0
| 1:30 | 3.7086 | 0
| 2:30 | 3.7557 | 0
| 3:30 | 3.7712 | 0
| 4:30 | 3.8215 | 0
| 5:30 | 3.8706 | 0
| 6:30 | 3.9536 | 0
| 7:30 | 4.0216 | 0
| 8:30 | 277.1187 | 0
| 9:30 | 24.9468 | 0
| 10:30 | 11.4608 | 0
| 11:30 | 7.3406 | 0
| 12:30 | 4.621 | 0
| 13:30 | 3.7838 | 0
| 14:30 | 5.1508 | 0
| 15:30 | 7.1688 | 0
| 16:30 | 8.6607 | 0
| 17:30 | 9.1983 | 0
| 18:30 | 0.8411 | 0
| 19:30 | 1.5131 | 0
| 20:30 | 1.8604 | 0
| 21:30 | 2.1312 | 0
| 22:30 | 2.3353 | 0
| 23:30 | 2.4532 | 0
Wed, 03/Nov | 0:30 | 2.638 | 0
| 1:30 | 2.7986 | 0
| 2:30 | 2.8892 | 0
| 3:30 | 2.9488 | 0
| 4:30 | 3.0425 | 0
| 5:30 | 3.114 | 0
| 6:30 | 3.1322 | 0
| 7:30 | 3.1343 | 0
| 8:30 | 220.9393 | 0
| 9:30 | 14.7201 | 0
| 10:30 | 8.7598 | 0
| 11:30 | 6.8381 | 0
| 12:30 | 5.2005 | 0
| 13:30 | 4.2925 | 0
| 14:30 | 4.0402 | 0
| 15:30 | 5.0214 | 0
| 16:30 | 7.0803 | 0
| 17:30 | 8.9221 | 0
| 18:30 | 0.7283 | 0
| 19:30 | 1.4851 | 0
| 20:30 | 1.846 | 0
| 21:30 | 1.9891 | 0
| 22:30 | 2.2303 | 0
| 23:30 | 2.373 | 0
Thu, 04/Nov | 0:30 | 2.4916 | 0
| 1:30 | 2.5961 | 0
| 2:30 | 2.8219 | 0
| 3:30 | 3.196 | 0
| 4:30 | 3.4219 | 0
| 5:30 | 3.4127 | 0
| 6:30 | 3.3281 | 0
| 7:30 | 3.3266 | 0
| 8:30 | 220.5612 | 0
| 9:30 | 15.3072 | 0
| 10:30 | 7.7062 | 0
| 11:30 | 5.2989 | 0
| 12:30 | 4.7222 | 0
| 13:30 | 4.9564 | 0
| 14:30 | 5.1646 | 0
| 15:30 | 6.2632 | 0
| 16:30 | 8.6049 | 0
| 17:30 | 11.8483 | 0
| 18:30 | 1.3567 | 0
| 19:30 | 2.0184 | 0
| 20:30 | 2.5602 | 0
| 21:30 | 3.0888 | 0
| 22:30 | 3.3064 | 0
| 23:30 | 3.4427 | 0
Fri, 05/Nov | 0:30 | 3.6387 | 0
| 1:30 | 3.7747 | 0
| 2:30 | 3.7844 | 0
| 3:30 | 3.9071 | 0
| 4:30 | 3.9507 | 0
| 5:30 | 4 | 0
| 6:30 | 4.0543 | 0
| 7:30 | 4.09 | 0
| 8:30 | 253.1807 | 0
| 9:30 | 24.8011 | 0
| 10:30 | 13.4905 | 0
| 11:30 | 9.6313 | 0
| 12:30 | 8.4802 | 0
| 13:30 | 8.1613 | 0
| 14:30 | 8.2621 | 0
| 15:30 | 9.1638 | 0
| 16:30 | 10.4449 | 0
| 17:30 | 11.7057 | 0
| 18:30 | 1.5363 | 0
| 19:30 | 2.3448 | 0
| 20:30 | 3.1164 | 0
| 21:30 | 3.7575 | 0
| 22:30 | 4.2622 | 0
| 23:30 | 4.5946 | 0
Sat, 06/Nov | 0:30 | 5.0603 | 0
| 1:30 | 5.3864 | 0
| 2:30 | 5.4407 | 0
| 3:30 | 5.6076 | 0
| 4:30 | 5.6964 | 0
| 5:30 | 5.472 | 0
| 6:30 | 5.219 | 0
| 7:30 | 5.1994 | 0
| 8:30 | 5.165 | 0
| 9:30 | 4.8588 | 0
| 10:30 | 4.5385 | 0
| 11:30 | 3.9276 | 0
| 12:30 | 3.2422 | 0
| 13:30 | 3.0413 | 0
| 14:30 | 3.094 | 0
| 15:30 | 3.2349 | 0
| 16:30 | 3.6689 | 0
| 17:30 | 3.9113 | 0
| 18:30 | 4.0272 | 0
| 19:30 | 4.2562 | 0
| 20:30 | 4.4311 | 0
| 21:30 | 4.5583 | 0
| 22:30 | 4.6784 | 0
| 23:30 | 4.7858 | 0
Sun, 07/Nov | 0:30 | 4.9757 | 0
| 1:30 | 5.1991 | 0
| 2:30 | 5.391 | 0
| 3:30 | 5.5773 | 0
| 4:30 | 5.7463 | 0
| 5:30 | 5.9627 | 0
| 6:30 | 6.154 | 0
| 7:30 | 6.1863 | 0
| 8:30 | 6.1005 | 0
| 9:30 | 5.9161 | 0
| 10:30 | 5.5436 | 0
| 11:30 | 5.1487 | 0
| 12:30 | 4.7939 | 0
| 13:30 | 4.5182 | 0
| 14:30 | 4.433 | 0
| 15:30 | 4.6004 | 0
| 16:30 | 4.8047 | 0
| 17:30 | 5.1897 | 0
| 18:30 | 5.7212 | 0
| 19:30 | 5.9572 | 0
| 20:30 | 6.0733 | 0
| 21:30 | 6.2028 | 0
| 22:30 | 6.2908 | 0
| 23:30 | 6.2398 | 0
Mon, 08/Nov | 0:30 | 6.2255 | 0
| 1:30 | 6.3528 | 0
| 2:30 | 6.4965 | 0
| 3:30 | 6.6852 | 0
| 4:30 | 6.7913 | 0
| 5:30 | 6.7399 | 0
| 6:30 | 6.7357 | 0
| 7:30 | 6.7766 | 0
| 8:30 | 447.8687 | 0
| 9:30 | 59.9187 | 0
| 10:30 | 35.6813 | 0
| 11:30 | 23.6042 | 0
| 12:30 | 18.1135 | 0
| 13:30 | 17.1261 | 0
| 14:30 | 18.0315 | 0
| 15:30 | 22.7774 | 0
| 16:30 | 26.7188 | 0
| 17:30 | 27.5276 | 0
| 18:30 | 2.4063 | 0
| 19:30 | 2.9661 | 0
| 20:30 | 3.3223 | 0
| 21:30 | 3.583 | 0
| 22:30 | 3.723 | 0
| 23:30 | 3.79 | 0
Tue, 09/Nov | 0:30 | 3.9111 | 0
| 1:30 | 4.1307 | 0
| 2:30 | 4.3707 | 0
| 3:30 | 4.608 | 0
| 4:30 | 4.7994 | 0
| 5:30 | 4.9134 | 0
| 6:30 | 5.016 | 0
| 7:30 | 5.1013 | 0
| 8:30 | 337.564 | 0
| 9:30 | 41.1644 | 0
| 10:30 | 24.8982 | 0
| 11:30 | 17.1353 | 0
| 12:30 | 14.2533 | 0
| 13:30 | 13.1269 | 0
| 14:30 | 12.7772 | 0
| 15:30 | 13.5807 | 0
| 16:30 | 14.6303 | 0
| 17:30 | 13.9702 | 0
| 18:30 | 1.7388 | 0
| 19:30 | 2.2741 | 0
| 20:30 | 2.7424 | 0
| 21:30 | 3.052 | 0
| 22:30 | 3.3317 | 0
| 23:30 | 3.4228 | 0
Wed, 10/Nov | 0:30 | 3.4759 | 0
| 1:30 | 3.5351 | 0
| 2:30 | 3.6391 | 0
| 3:30 | 3.7547 | 0
| 4:30 | 3.8505 | 0
| 5:30 | 3.8544 | 0
| 6:30 | 4.0235 | 0
| 7:30 | 4.2753 | 0
| 8:30 | 282.3715 | 0
| 9:30 | 34.5301 | 0
| 10:30 | 21.5819 | 0
| 11:30 | 14.9194 | 0
| 12:30 | 10.8049 | 0
| 13:30 | 8.8122 | 0
| 14:30 | 8.2786 | 0
| 15:30 | 9.3821 | 0
| 16:30 | 10.962 | 0
| 17:30 | 12.4638 | 0
| 18:30 | 1.8447 | 0
| 19:30 | 2.5755 | 0
| 20:30 | 3.0627 | 0
| 21:30 | 3.3821 | 0
| 22:30 | 3.7318 | 0
| 23:30 | 4.1256 | 0
Thu, 11/Nov | 0:30 | 4.4946 | 0
| 1:30 | 4.9202 | 0
| 2:30 | 5.3458 | 0
| 3:30 | 5.5105 | 0
| 4:30 | 5.4725 | 0
| 5:30 | 5.3186 | 0
| 6:30 | 5.1279 | 0
| 7:30 | 4.974 | 0
| 8:30 | 293.1973 | 0
| 9:30 | 32.6729 | 0
| 10:30 | 16.4599 | 0
| 11:30 | 10.348 | 0
| 12:30 | 8.1952 | 0
| 13:30 | 7.1113 | 0
| 14:30 | 8.2692 | 0
| 15:30 | 9.5854 | 0
| 16:30 | 16.294 | 0
| 17:30 | 27.0971 | 0
| 18:30 | 2.6004 | 0
| 19:30 | 3.1324 | 0
| 20:30 | 3.6578 | 0
| 21:30 | 3.9653 | 0
| 22:30 | 4.2928 | 0
| 23:30 | 4.8155 | 0
Fri, 12/Nov | 0:30 | 5.31 | 0
| 1:30 | 5.5618 | 0
| 2:30 | 5.67 | 0
| 3:30 | 5.7969 | 0
| 4:30 | 5.8743 | 0
| 5:30 | 6.0515 | 0
| 6:30 | 6.2134 | 0
| 7:30 | 6.1473 | 0
| 8:30 | 346.6853 | 0
| 9:30 | 57.4419 | 0
| 10:30 | 38.2343 | 0
| 11:30 | 27.8492 | 0
| 12:30 | 22.333 | 0
| 13:30 | 18.9965 | 0
| 14:30 | 18.5242 | 0
| 15:30 | 19.8123 | 0
| 16:30 | 21.7798 | 0
| 17:30 | 23.251 | 0
| 18:30 | 2.6525 | 0
| 19:30 | 3.397 | 0
| 20:30 | 3.8197 | 0
| 21:30 | 4.1317 | 0
| 22:30 | 4.4786 | 0
| 23:30 | 4.7064 | 0
Sat, 13/Nov | 0:30 | 4.958 | 0
| 1:30 | 5.1215 | 0
| 2:30 | 5.2484 | 0
| 3:30 | 5.4789 | 0
| 4:30 | 5.7192 | 0
| 5:30 | 5.9716 | 0
| 6:30 | 6.1787 | 0
| 7:30 | 6.3997 | 0
| 8:30 | 6.5238 | 0
| 9:30 | 6.2871 | 0
| 10:30 | 5.7687 | 0
| 11:30 | 5.2459 | 0
| 12:30 | 4.8669 | 0
| 13:30 | 4.7027 | 0
| 14:30 | 4.7414 | 0
| 15:30 | 5.0273 | 0
| 16:30 | 5.5038 | 0
| 17:30 | 5.8981 | 0
| 18:30 | 6.3126 | 0
| 19:30 | 6.7243 | 0
| 20:30 | 7.0021 | 0
| 21:30 | 7.3365 | 0
| 22:30 | 7.6787 | 0
| 23:30 | 7.8883 | 0
Sun, 14/Nov | 0:30 | 8.0352 | 0
| 1:30 | 8.1579 | 0
| 2:30 | 8.2726 | 0
| 3:30 | 8.4714 | 0
| 4:30 | 8.7364 | 0
| 5:30 | 8.9881 | 0
| 6:30 | 9.0865 | 0
| 7:30 | 9.1201 | 0
| 8:30 | 9.1282 | 0
| 9:30 | 8.8087 | 0
| 10:30 | 8.2972 | 0
| 11:30 | 7.8006 | 0
| 12:30 | 7.321 | 0
| 13:30 | 6.9151 | 0
| 14:30 | 6.7955 | 0
| 15:30 | 6.9582 | 0
| 16:30 | 7.2132 | 0
| 17:30 | 7.5272 | 0
| 18:30 | 7.8212 | 0
| 19:30 | 7.8668 | 0
| 20:30 | 7.784 | 0
| 21:30 | 7.7924 | 0
| 22:30 | 7.9349 | 0
| 23:30 | 8.1282 | 0
Mon, 15/Nov | 0:30 | 8.2521 | 0
| 1:30 | 8.2801 | 0
| 2:30 | 8.1228 | 0
| 3:30 | 7.8229 | 0
| 4:30 | 7.3251 | 0
| 5:30 | 6.8759 | 0
| 6:30 | 6.6978 | 0
| 7:30 | 6.6507 | 0
| 8:30 | 462.2529 | 0
| 9:30 | 57.4013 | 0
| 10:30 | 32.0282 | 0
| 11:30 | 19.9168 | 0
| 12:30 | 14.7016 | 0
| 13:30 | 12.7568 | 0
| 14:30 | 11.2093 | 0
| 15:30 | 10.9761 | 0
| 16:30 | 13.2635 | 0
| 17:30 | 15.4614 | 0
| 18:30 | 1.218 | 0
| 19:30 | 1.8823 | 0
| 20:30 | 2.3744 | 0
| 21:30 | 2.9298 | 0
| 22:30 | 3.3198 | 0
| 23:30 | 3.5389 | 0
Tue, 16/Nov | 0:30 | 3.8221 | 0
| 1:30 | 4.0758 | 0
| 2:30 | 4.3324 | 0
| 3:30 | 4.5972 | 0
| 4:30 | 4.7961 | 0
| 5:30 | 4.9073 | 0
| 6:30 | 5.0337 | 0
| 7:30 | 5.2177 | 0
| 8:30 | 349.4732 | 0
| 9:30 | 43.8832 | 0
| 10:30 | 28.7106 | 0
| 11:30 | 20.0928 | 0
| 12:30 | 16.582 | 0
| 13:30 | 14.4354 | 0
| 14:30 | 12.4954 | 0
| 15:30 | 13.2632 | 0
| 16:30 | 16.038 | 0
| 17:30 | 17.903 | 0
| 18:30 | 2.0044 | 0
| 19:30 | 2.5725 | 0
| 20:30 | 3.112 | 0
| 21:30 | 3.4632 | 0
| 22:30 | 3.7628 | 0
| 23:30 | 3.9302 | 0
Wed, 17/Nov | 0:30 | 3.9559 | 0
| 1:30 | 4.1415 | 0
| 2:30 | 4.3756 | 0
| 3:30 | 4.4441 | 0
| 4:30 | 4.6334 | 0
| 5:30 | 4.87 | 0
| 6:30 | 4.9661 | 0
| 7:30 | 4.9246 | 0
| 8:30 | 311.9534 | 0
| 9:30 | 31.6516 | 0
| 10:30 | 15.832 | 0
| 11:30 | 10.4845 | 0
| 12:30 | 7.8558 | 0
| 13:30 | 6.5342 | 0
| 14:30 | 6.1528 | 0
| 15:30 | 6.2638 | 0
| 16:30 | 6.8139 | 0
| 17:30 | 7.06 | 0
| 18:30 | 0.3381 | 0
| 19:30 | 0.957 | 0
| 20:30 | 1.2549 | 0
| 21:30 | 1.4772 | 0
| 22:30 | 1.6169 | 0
| 23:30 | 1.7709 | 0
Thu, 18/Nov | 0:30 | 2.0709 | 0
| 1:30 | 2.2824 | 0
| 2:30 | 2.1435 | 0
| 3:30 | 1.9952 | 0
| 4:30 | 2.0279 | 0
| 5:30 | 2.109 | 0
| 6:30 | 2.0701 | 0
| 7:30 | 1.9026 | 0
| 8:30 | 167.9317 | 0
| 9:30 | 6.7721 | 0
| 10:30 | 4.8675 | 0
| 11:30 | 3.9899 | 0
| 12:30 | 3.8504 | 0
| 13:30 | 4.0156 | 0
| 14:30 | 4.2295 | 0
| 15:30 | 4.6434 | 0
| 16:30 | 5.1137 | 0
| 17:30 | 5.0137 | 0
| 18:30 | 0.0297 | 0
| 19:30 | 0.2358 | 0
| 20:30 | 0.5912 | 0
| 21:30 | 0.869 | 0
| 22:30 | 1.0996 | 0
| 23:30 | 1.328 | 0
Fri, 19/Nov | 0:30 | 1.5541 | 0
| 1:30 | 1.8149 | 0
| 2:30 | 1.9768 | 0
| 3:30 | 2.1394 | 0
| 4:30 | 2.3737 | 0
| 5:30 | 2.5259 | 0
| 6:30 | 2.6376 | 0
| 7:30 | 2.7852 | 0
| 8:30 | 192.7751 | 0
| 9:30 | 17.8737 | 0
| 10:30 | 12.4763 | 0
| 11:30 | 10.7242 | 0
| 12:30 | 10.0134 | 0
| 13:30 | 9.8694 | 0
| 14:30 | 9.6587 | 0
| 15:30 | 9.9672 | 0
| 16:30 | 13.2046 | 0
| 17:30 | 16.8714 | 0
| 18:30 | 2.2353 | 0
| 19:30 | 2.9462 | 0
| 20:30 | 3.4538 | 0
| 21:30 | 3.7914 | 0
| 22:30 | 4.079 | 0
| 23:30 | 4.2777 | 0
Sat, 20/Nov | 0:30 | 4.3926 | 0
| 1:30 | 4.3994 | 0
| 2:30 | 4.3866 | 0
| 3:30 | 4.3123 | 0
| 4:30 | 4.2484 | 0
| 5:30 | 4.2017 | 0
| 6:30 | 4.1672 | 0
| 7:30 | 4.2247 | 0
| 8:30 | 4.2621 | 0
| 9:30 | 4.2777 | 0
| 10:30 | 4.1633 | 0
| 11:30 | 3.9943 | 0
| 12:30 | 3.886 | 0
| 13:30 | 3.8386 | 0
| 14:30 | 3.8447 | 0
| 15:30 | 3.9809 | 0
| 16:30 | 4.2978 | 0
| 17:30 | 4.5732 | 0
| 18:30 | 4.8451 | 0
| 19:30 | 5.1475 | 0
| 20:30 | 5.4012 | 0
| 21:30 | 5.6439 | 0
| 22:30 | 5.7949 | 0
| 23:30 | 5.8129 | 0
Sun, 21/Nov | 0:30 | 5.8308 | 0
| 1:30 | 5.8727 | 0
| 2:30 | 5.8756 | 0
| 3:30 | 5.8699 | 0
| 4:30 | 5.9037 | 0
| 5:30 | 5.9261 | 0
| 6:30 | 5.9337 | 0
| 7:30 | 5.9674 | 0
| 8:30 | 5.991 | 0
| 9:30 | 5.9236 | 0
| 10:30 | 5.7962 | 0
| 11:30 | 5.4859 | 0
| 12:30 | 5.266 | 0
| 13:30 | 5.2163 | 0
| 14:30 | 5.1587 | 0
| 15:30 | 5.3031 | 0
| 16:30 | 5.5421 | 0
| 17:30 | 5.7376 | 0
| 18:30 | 5.8853 | 0
| 19:30 | 6.0426 | 0
| 20:30 | 6.191 | 0
| 21:30 | 6.3836 | 0
| 22:30 | 6.5116 | 0
| 23:30 | 6.5321 | 0
Mon, 22/Nov | 0:30 | 6.5573 | 0
| 1:30 | 6.5839 | 0
| 2:30 | 6.6356 | 0
| 3:30 | 6.6621 | 0
| 4:30 | 6.7027 | 0
| 5:30 | 6.8998 | 0
| 6:30 | 7.2235 | 0
| 7:30 | 7.4931 | 0
| 8:30 | 492.212 | 0
| 9:30 | 86.6865 | 0
| 10:30 | 61.3664 | 0
| 11:30 | 47.9003 | 0
| 12:30 | 40.8641 | 0
| 13:30 | 38.3295 | 0
| 14:30 | 42.3477 | 0
| 15:30 | 46.1953 | 0
| 16:30 | 48.7345 | 0
| 17:30 | 53.6688 | 0
| 18:30 | 4.2566 | 0
| 19:30 | 4.8929 | 0
| 20:30 | 5.4377 | 0
| 21:30 | 5.897 | 0
| 22:30 | 6.2672 | 0
| 23:30 | 6.6943 | 0
Tue, 23/Nov | 0:30 | 7.1199 | 0
| 1:30 | 7.4781 | 0
| 2:30 | 7.7462 | 0
| 3:30 | 7.9849 | 0
| 4:30 | 8.2388 | 0
| 5:30 | 8.4192 | 0
| 6:30 | 8.3642 | 0
| 7:30 | 8.1481 | 0
| 8:30 | 476.8061 | 0
| 9:30 | 78.221 | 0
| 10:30 | 48.8089 | 0
| 11:30 | 37.0208 | 0
| 12:30 | 29.3108 | 0
| 13:30 | 22.415 | 0
| 14:30 | 20.1296 | 0
| 15:30 | 23.1951 | 0
| 16:30 | 29.1153 | 0
| 17:30 | 31.9038 | 0
| 18:30 | 3.1254 | 0
| 19:30 | 3.8639 | 0
| 20:30 | 4.233 | 0
| 21:30 | 4.6272 | 0
| 22:30 | 4.9422 | 0
| 23:30 | 5.2195 | 0
Wed, 24/Nov | 0:30 | 5.4039 | 0
| 1:30 | 5.5539 | 0
| 2:30 | 5.7637 | 0
| 3:30 | 6.0172 | 0
| 4:30 | 6.2746 | 0
| 5:30 | 6.4613 | 0
| 6:30 | 6.7338 | 0
| 7:30 | 7.0388 | 0
| 8:30 | 405.7068 | 0
| 9:30 | 68.7861 | 0
| 10:30 | 49.2193 | 0
| 11:30 | 35.3207 | 0
| 12:30 | 31.1431 | 0
| 13:30 | 31.0725 | 0
| 14:30 | 30.0162 | 0
| 15:30 | 31.4165 | 0
| 16:30 | 34.1903 | 0
| 17:30 | 35.1745 | 0
| 18:30 | 3.6544 | 0
| 19:30 | 4.5578 | 0
| 20:30 | 5.1393 | 0
| 21:30 | 5.7659 | 0
| 22:30 | 6.289 | 0
| 23:30 | 6.4799 | 0
Thu, 25/Nov | 0:30 | 6.5119 | 0
| 1:30 | 6.7485 | 0
| 2:30 | 7.054 | 0
| 3:30 | 7.5459 | 0
| 4:30 | 7.9991 | 0
| 5:30 | 8.2434 | 0
| 6:30 | 8.4981 | 0
| 7:30 | 8.7359 | 0
| 8:30 | 483.1129 | 0
| 9:30 | 104.6024 | 0
| 10:30 | 70.5326 | 0
| 11:30 | 51.0056 | 0
| 12:30 | 40.6158 | 0
| 13:30 | 36.0391 | 0
| 14:30 | 34.1806 | 0
| 15:30 | 36.1421 | 0
| 16:30 | 38.2579 | 0
| 17:30 | 38.0601 | 0
| 18:30 | 3.9113 | 0
| 19:30 | 4.6467 | 0
| 20:30 | 5.1636 | 0
| 21:30 | 5.8051 | 0
| 22:30 | 6.3498 | 0
| 23:30 | 6.922 | 0
Fri, 26/Nov | 0:30 | 7.4172 | 0
| 1:30 | 7.861 | 0
| 2:30 | 8.0963 | 0
| 3:30 | 8.2271 | 0
| 4:30 | 8.3906 | 0
| 5:30 | 8.4509 | 0
| 6:30 | 8.5198 | 0
| 7:30 | 8.542 | 0
| 8:30 | 467.2562 | 0
| 9:30 | 95.3964 | 0
| 10:30 | 66.6825 | 0
| 11:30 | 49.8548 | 0
| 12:30 | 42.1482 | 0
| 13:30 | 39.8646 | 0
| 14:30 | 39.7825 | 0
| 15:30 | 42.398 | 0
| 16:30 | 45.8483 | 0
| 17:30 | 47.3222 | 0
| 18:30 | 4.5364 | 0
| 19:30 | 5.1056 | 0
| 20:30 | 5.528 | 0
| 21:30 | 6.135 | 0
| 22:30 | 6.5931 | 0
| 23:30 | 6.9065 | 0
Sat, 27/Nov | 0:30 | 7.1603 | 0
| 1:30 | 7.5371 | 0
| 2:30 | 7.8474 | 0
| 3:30 | 8.0401 | 0
| 4:30 | 8.1611 | 0
| 5:30 | 8.226 | 0
| 6:30 | 8.2532 | 0
| 7:30 | 8.3211 | 0
| 8:30 | 8.3446 | 0
| 9:30 | 8.3783 | 0
| 10:30 | 8.3087 | 0
| 11:30 | 8.0188 | 0
| 12:30 | 7.7765 | 0
| 13:30 | 7.679 | 0
| 14:30 | 7.6269 | 0
| 15:30 | 7.6672 | 0
| 16:30 | 7.7695 | 0
| 17:30 | 7.8867 | 0
| 18:30 | 8.0594 | 0
| 19:30 | 8.2742 | 0
| 20:30 | 8.509 | 0
| 21:30 | 8.7509 | 0
| 22:30 | 8.919 | 0
| 23:30 | 9.0154 | 0
Sun, 28/Nov | 0:30 | 9.1406 | 0
| 1:30 | 9.2737 | 0
| 2:30 | 9.4119 | 0
| 3:30 | 9.6093 | 0
| 4:30 | 10.023 | 0
| 5:30 | 10.4666 | 0
| 6:30 | 10.4822 | 0
| 7:30 | 10.4605 | 0
| 8:30 | 10.5312 | 0
| 9:30 | 10.3848 | 0
| 10:30 | 9.9278 | 0
| 11:30 | 9.2512 | 0
| 12:30 | 8.5846 | 0
| 13:30 | 8.1409 | 0
| 14:30 | 8.0258 | 0
| 15:30 | 8.1571 | 0
| 16:30 | 8.3842 | 0
| 17:30 | 8.5204 | 0
| 18:30 | 8.6238 | 0
| 19:30 | 8.7557 | 0
| 20:30 | 8.9017 | 0
| 21:30 | 9.0023 | 0
| 22:30 | 9.0526 | 0
| 23:30 | 9.0706 | 0
Mon, 29/Nov | 0:30 | 9.0867 | 0
| 1:30 | 9.0442 | 0
| 2:30 | 8.9093 | 0
| 3:30 | 8.8126 | 0
| 4:30 | 8.7869 | 0
| 5:30 | 8.7879 | 0
| 6:30 | 9.0894 | 0
| 7:30 | 9.5266 | 0
| 8:30 | 639.0981 | 0
| 9:30 | 121.4946 | 0
| 10:30 | 81.643 | 0
| 11:30 | 61.0101 | 0
| 12:30 | 48.2122 | 0
| 13:30 | 39.2625 | 0
| 14:30 | 35.7332 | 0
| 15:30 | 41.1728 | 0
| 16:30 | 57.0246 | 0
| 17:30 | 65.9258 | 0
| 18:30 | 4.5433 | 0
| 19:30 | 5.334 | 0
| 20:30 | 6.0769 | 0
| 21:30 | 6.8946 | 0
| 22:30 | 7.7823 | 0
| 23:30 | 8.3226 | 0
Tue, 30/Nov | 0:30 | 8.7543 | 0
| 1:30 | 9.224 | 0
| 2:30 | 9.6503 | 0
| 3:30 | 9.9311 | 0
| 4:30 | 10.2569 | 0
| 5:30 | 10.5563 | 0
| 6:30 | 10.9457 | 0
| 7:30 | 11.2461 | 0
| 8:30 | 647.6375 | 0
| 9:30 | 133.7207 | 0
| 10:30 | 81.099 | 0
| 11:30 | 54.7826 | 0
| 12:30 | 41.245 | 0
| 13:30 | 32.0201 | 0
| 14:30 | 27.8391 | 0
| 15:30 | 33.1287 | 0
| 16:30 | 42.8172 | 0
| 17:30 | 44.6894 | 0
| 18:30 | 3.7229 | 0
| 19:30 | 4.2406 | 0
| 20:30 | 4.583 | 0
| 21:30 | 4.929 | 0
| 22:30 | 5.2637 | 0
| 23:30 | 5.6852 | 0
Wed, 01/Dec | 0:30 | 6.246 | 0
| 1:30 | 6.7445 | 0
| 2:30 | 7.2115 | 0
| 3:30 | 7.5822 | 0
| 4:30 | 7.8208 | 0
| 5:30 | 7.9709 | 0
| 6:30 | 8.093 | 0
| 7:30 | 8.3022 | 0
| 8:30 | 479.7034 | 0
| 9:30 | 98.7352 | 0
| 10:30 | 72.0774 | 0
| 11:30 | 52.9204 | 0
| 12:30 | 45.3144 | 0
| 13:30 | 44.5443 | 0
| 14:30 | 46.2435 | 0
| 15:30 | 49.282 | 0
| 16:30 | 50.869 | 0
| 17:30 | 49.9778 | 0
| 18:30 | 4.4732 | 0
| 19:30 | 5.12 | 0
| 20:30 | 5.8206 | 0
| 21:30 | 6.5626 | 0
| 22:30 | 7.1503 | 0
| 23:30 | 7.6073 | 0
Thu, 02/Dec | 0:30 | 8.1781 | 0
| 1:30 | 8.7493 | 0
| 2:30 | 9.1316 | 0
| 3:30 | 9.513 | 0
| 4:30 | 9.8894 | 0
| 5:30 | 10.1931 | 0
| 6:30 | 10.5124 | 0
| 7:30 | 10.7704 | 0
| 8:30 | 582.852 | 0
| 9:30 | 138.1418 | 0
| 10:30 | 92.1093 | 0
| 11:30 | 69.0906 | 0
| 12:30 | 52.1381 | 0
| 13:30 | 39.3921 | 0
| 14:30 | 36.8113 | 0
| 15:30 | 43.1177 | 0
| 16:30 | 53.7572 | 0
| 17:30 | 57.4127 | 0
| 18:30 | 4.9422 | 0
| 19:30 | 5.2348 | 0
| 20:30 | 5.439 | 0
| 21:30 | 5.6597 | 0
| 22:30 | 5.6522 | 0
| 23:30 | 5.7123 | 0
Fri, 03/Dec | 0:30 | 5.7817 | 0
| 1:30 | 5.8478 | 0
| 2:30 | 5.7616 | 0
| 3:30 | 5.6714 | 0
| 4:30 | 5.613 | 0
| 5:30 | 5.4486 | 0
| 6:30 | 5.299 | 0
| 7:30 | 5.2168 | 0
| 8:30 | 323.4319 | 0
| 9:30 | 42.3085 | 0
| 10:30 | 23.1209 | 0
| 11:30 | 15.2531 | 0
| 12:30 | 13.3714 | 0
| 13:30 | 12.2949 | 0
| 14:30 | 10.6509 | 0
| 15:30 | 11.5646 | 0
| 16:30 | 15.4721 | 0
| 17:30 | 16.764 | 0
| 18:30 | 2.0092 | 0
| 19:30 | 2.7531 | 0
| 20:30 | 3.1699 | 0
| 21:30 | 3.4964 | 0
| 22:30 | 4.0025 | 0
| 23:30 | 4.3428 | 0
Sat, 04/Dec | 0:30 | 4.5706 | 0
| 1:30 | 4.8499 | 0
| 2:30 | 5.0766 | 0
| 3:30 | 5.4175 | 0
| 4:30 | 5.8319 | 0
| 5:30 | 5.9576 | 0
| 6:30 | 5.9725 | 0
| 7:30 | 5.94 | 0
| 8:30 | 5.862 | 0
| 9:30 | 5.7137 | 0
| 10:30 | 5.4149 | 0
| 11:30 | 5.0985 | 0
| 12:30 | 4.8782 | 0
| 13:30 | 4.6896 | 0
| 14:30 | 4.4903 | 0
| 15:30 | 4.4389 | 0
| 16:30 | 4.4182 | 0
| 17:30 | 4.464 | 0
| 18:30 | 4.4742 | 0
| 19:30 | 4.4629 | 0
| 20:30 | 4.5058 | 0
| 21:30 | 4.4174 | 0
| 22:30 | 4.451 | 0
| 23:30 | 4.9217 | 0
Sun, 05/Dec | 0:30 | 5.4572 | 0
| 1:30 | 5.7551 | 0
| 2:30 | 5.9358 | 0
| 3:30 | 6.1043 | 0
| 4:30 | 6.2767 | 0
| 5:30 | 6.3389 | 0
| 6:30 | 6.4299 | 0
| 7:30 | 6.57 | 0
| 8:30 | 6.6399 | 0
| 9:30 | 6.6339 | 0
| 10:30 | 6.3311 | 0
| 11:30 | 5.7471 | 0
| 12:30 | 5.4589 | 0
| 13:30 | 5.4813 | 0
| 14:30 | 5.4102 | 0
| 15:30 | 5.5763 | 0
| 16:30 | 6.0558 | 0
| 17:30 | 6.4622 | 0
| 18:30 | 6.8423 | 0
| 19:30 | 7.351 | 0
| 20:30 | 7.8269 | 0
| 21:30 | 8.2994 | 0
| 22:30 | 8.8054 | 0
| 23:30 | 9.1026 | 0
Mon, 06/Dec | 0:30 | 9.2291 | 0
| 1:30 | 9.3814 | 0
| 2:30 | 9.5729 | 0
| 3:30 | 9.778 | 0
| 4:30 | 9.9027 | 0
| 5:30 | 9.9357 | 0
| 6:30 | 9.9435 | 0
| 7:30 | 10.0283 | 0
| 8:30 | 613.8956 | 0
| 9:30 | 115.7927 | 0
| 10:30 | 68.6719 | 0
| 11:30 | 50.303 | 0
| 12:30 | 43.0489 | 0
| 13:30 | 42.4402 | 0
| 14:30 | 41.7695 | 0
| 15:30 | 40.364 | 0
| 16:30 | 37.2018 | 0
| 17:30 | 32.1919 | 0
| 18:30 | 2.4772 | 0
| 19:30 | 2.8015 | 0
| 20:30 | 3.0565 | 0
| 21:30 | 3.3867 | 0
| 22:30 | 3.5479 | 0
| 23:30 | 3.7095 | 0
Tue, 07/Dec | 0:30 | 3.8632 | 0
| 1:30 | 4.0679 | 0
| 2:30 | 4.2383 | 0
| 3:30 | 4.3554 | 0
| 4:30 | 4.5318 | 0
| 5:30 | 4.6537 | 0
| 6:30 | 4.6565 | 0
| 7:30 | 4.6973 | 0
| 8:30 | 324.6576 | 0
| 9:30 | 32.7635 | 0
| 10:30 | 19.5223 | 0
| 11:30 | 13.3949 | 0
| 12:30 | 11.2981 | 0
| 13:30 | 10.4222 | 0
| 14:30 | 10.1527 | 0
| 15:30 | 10.6663 | 0
| 16:30 | 11.3998 | 0
| 17:30 | 11.4183 | 0
| 18:30 | 1.3224 | 0
| 19:30 | 1.9489 | 0
| 20:30 | 2.3825 | 0
| 21:30 | 2.7536 | 0
| 22:30 | 3.034 | 0
| 23:30 | 3.174 | 0
Wed, 08/Dec | 0:30 | 3.4548 | 0
| 1:30 | 3.834 | 0
| 2:30 | 4.1069 | 0
| 3:30 | 4.3179 | 0
| 4:30 | 4.6494 | 0
| 5:30 | 5.0586 | 0
| 6:30 | 5.5197 | 0
| 7:30 | 5.8379 | 0
| 8:30 | 349.7921 | 0
| 9:30 | 45.7853 | 0
| 10:30 | 20.7046 | 0
| 11:30 | 12.6077 | 0
| 12:30 | 11.6083 | 0
| 13:30 | 11.7417 | 0
| 14:30 | 14.7655 | 0
| 15:30 | 24.7603 | 0
| 16:30 | 31.6429 | 0
| 17:30 | 32.2309 | 0
| 18:30 | 3.3945 | 0
| 19:30 | 4.3622 | 0
| 20:30 | 4.8676 | 0
| 21:30 | 5.3831 | 0
| 22:30 | 5.9188 | 0
| 23:30 | 6.3388 | 0
Thu, 09/Dec | 0:30 | 6.7965 | 0
| 1:30 | 7.2745 | 0
| 2:30 | 7.6939 | 0
| 3:30 | 7.9852 | 0
| 4:30 | 8.1558 | 0
| 5:30 | 8.1498 | 0
| 6:30 | 8.1424 | 0
| 7:30 | 8.2533 | 0
| 8:30 | 465.4073 | 0
| 9:30 | 94.0129 | 0
| 10:30 | 60.6826 | 0
| 11:30 | 42.558 | 0
| 12:30 | 34.433 | 0
| 13:30 | 30.0147 | 0
| 14:30 | 27.0248 | 0
| 15:30 | 27.1336 | 0
| 16:30 | 28.2465 | 0
| 17:30 | 27.7192 | 0
| 18:30 | 2.9694 | 0
| 19:30 | 3.6073 | 0
| 20:30 | 3.9367 | 0
| 21:30 | 4.252 | 0
| 22:30 | 4.6453 | 0
| 23:30 | 4.7671 | 0
Fri, 10/Dec | 0:30 | 4.8815 | 0
| 1:30 | 5.0643 | 0
| 2:30 | 5.08 | 0
| 3:30 | 5.2308 | 0
| 4:30 | 5.4695 | 0
| 5:30 | 5.5719 | 0
| 6:30 | 5.5421 | 0
| 7:30 | 5.5264 | 0
| 8:30 | 334.6211 | 0
| 9:30 | 47.8917 | 0
| 10:30 | 29.4844 | 0
| 11:30 | 19.5663 | 0
| 12:30 | 15.7151 | 0
| 13:30 | 15.3891 | 0
| 14:30 | 15.1736 | 0
| 15:30 | 16.3166 | 0
| 16:30 | 18.7115 | 0
| 17:30 | 18.226 | 0
| 18:30 | 2.2327 | 0
| 19:30 | 2.9118 | 0
| 20:30 | 3.3021 | 0
| 21:30 | 3.5346 | 0
| 22:30 | 3.898 | 0
| 23:30 | 4.0997 | 0
Sat, 11/Dec | 0:30 | 4.3247 | 0
| 1:30 | 4.6039 | 0
| 2:30 | 4.8919 | 0
| 3:30 | 5.2847 | 0
| 4:30 | 5.6632 | 0
| 5:30 | 6.0031 | 0
| 6:30 | 6.0207 | 0
| 7:30 | 5.9207 | 0
| 8:30 | 5.8374 | 0
| 9:30 | 5.4956 | 0
| 10:30 | 5.1653 | 0
| 11:30 | 4.9612 | 0
| 12:30 | 4.8497 | 0
| 13:30 | 4.834 | 0
| 14:30 | 4.8541 | 0
| 15:30 | 4.9641 | 0
| 16:30 | 5.1214 | 0
| 17:30 | 5.1831 | 0
| 18:30 | 5.3002 | 0
| 19:30 | 5.5221 | 0
| 20:30 | 5.5588 | 0
| 21:30 | 5.6243 | 0
| 22:30 | 5.8164 | 0
| 23:30 | 5.8643 | 0
Sun, 12/Dec | 0:30 | 5.9277 | 0
| 1:30 | 6.0904 | 0
| 2:30 | 6.1746 | 0
| 3:30 | 6.2849 | 0
| 4:30 | 6.3307 | 0
| 5:30 | 6.2678 | 0
| 6:30 | 6.2654 | 0
| 7:30 | 6.2701 | 0
| 8:30 | 6.2847 | 0
| 9:30 | 6.2807 | 0
| 10:30 | 6.2193 | 0
| 11:30 | 6.1143 | 0
| 12:30 | 6.1693 | 0
| 13:30 | 6.3465 | 0
| 14:30 | 6.4079 | 0
| 15:30 | 6.4664 | 0
| 16:30 | 6.6202 | 0
| 17:30 | 6.7123 | 0
| 18:30 | 6.84 | 0
| 19:30 | 6.8636 | 0
| 20:30 | 6.7885 | 0
| 21:30 | 6.7118 | 0
| 22:30 | 6.6702 | 0
| 23:30 | 6.7854 | 0
Mon, 13/Dec | 0:30 | 6.8793 | 0
| 1:30 | 6.9547 | 0
| 2:30 | 6.9173 | 0
| 3:30 | 6.9213 | 0
| 4:30 | 6.966 | 0
| 5:30 | 6.955 | 0
| 6:30 | 7.065 | 0
| 7:30 | 7.1775 | 0
| 8:30 | 480.7175 | 0
| 9:30 | 74.4546 | 0
| 10:30 | 53.1866 | 0
| 11:30 | 42.6641 | 0
| 12:30 | 34.1418 | 0
| 13:30 | 27.0401 | 0
| 14:30 | 22.7444 | 0
| 15:30 | 23.132 | 0
| 16:30 | 24.3623 | 0
| 17:30 | 22.2867 | 0
| 18:30 | 2.0756 | 0
| 19:30 | 2.8309 | 0
| 20:30 | 3.4514 | 0
| 21:30 | 4.0316 | 0
| 22:30 | 4.4323 | 0
| 23:30 | 4.7568 | 0
Tue, 14/Dec | 0:30 | 5.0885 | 0
| 1:30 | 5.4608 | 0
| 2:30 | 5.6269 | 0
| 3:30 | 5.8569 | 0
| 4:30 | 6.2013 | 0
| 5:30 | 6.387 | 0
| 6:30 | 6.6823 | 0
| 7:30 | 7.1739 | 0
| 8:30 | 443.6234 | 0
| 9:30 | 86.4144 | 0
| 10:30 | 67.8384 | 0
| 11:30 | 60.2309 | 0
| 12:30 | 57.8268 | 0
| 13:30 | 60.212 | 0
| 14:30 | 62.9879 | 0
| 15:30 | 64.33 | 0
| 16:30 | 63.0833 | 0
| 17:30 | 59.8329 | 0
| 18:30 | 4.9601 | 0
| 19:30 | 5.54 | 0
| 20:30 | 6.02 | 0
| 21:30 | 6.455 | 0
| 22:30 | 6.7513 | 0
| 23:30 | 7.0015 | 0
Wed, 15/Dec | 0:30 | 7.2663 | 0
| 1:30 | 7.461 | 0
| 2:30 | 7.6207 | 0
| 3:30 | 7.72 | 0
| 4:30 | 7.7973 | 0
| 5:30 | 7.8253 | 0
| 6:30 | 7.9855 | 0
| 7:30 | 8.0699 | 0
| 8:30 | 462.2934 | 0
| 9:30 | 97.9359 | 0
| 10:30 | 76.3356 | 0
| 11:30 | 63.312 | 0
| 12:30 | 55.0622 | 0
| 13:30 | 50.622 | 0
| 14:30 | 47.7145 | 0
| 15:30 | 46.9966 | 0
| 16:30 | 46.3299 | 0
| 17:30 | 44.3886 | 0
| 18:30 | 4.2841 | 0
| 19:30 | 4.864 | 0
| 20:30 | 5.2485 | 0
| 21:30 | 5.7703 | 0
| 22:30 | 6.1414 | 0
| 23:30 | 6.3463 | 0
Thu, 16/Dec | 0:30 | 6.5655 | 0
| 1:30 | 6.8959 | 0
| 2:30 | 7.1426 | 0
| 3:30 | 7.2428 | 0
| 4:30 | 7.3545 | 0
| 5:30 | 7.4058 | 0
| 6:30 | 7.4444 | 0
| 7:30 | 7.5813 | 0
| 8:30 | 432.4347 | 0
| 9:30 | 84.4236 | 0
| 10:30 | 56.5621 | 0
| 11:30 | 41.8115 | 0
| 12:30 | 36.9735 | 0
| 13:30 | 35.602 | 0
| 14:30 | 33.8883 | 0
| 15:30 | 35.0399 | 0
| 16:30 | 37.7041 | 0
| 17:30 | 36.6427 | 0
| 18:30 | 3.8752 | 0
| 19:30 | 4.6632 | 0
| 20:30 | 4.8824 | 0
| 21:30 | 5.0211 | 0
| 22:30 | 5.1056 | 0
| 23:30 | 5.144 | 0
Fri, 17/Dec | 0:30 | 5.234 | 0
| 1:30 | 5.2441 | 0
| 2:30 | 5.2981 | 0
| 3:30 | 5.2564 | 0
| 4:30 | 5.2106 | 0
| 5:30 | 5.3475 | 0
| 6:30 | 5.7337 | 0
| 7:30 | 6.1903 | 0
| 8:30 | 366.2447 | 0
| 9:30 | 74.3172 | 0
| 10:30 | 58.838 | 0
| 11:30 | 48.5945 | 0
| 12:30 | 41.1496 | 0
| 13:30 | 38.5036 | 0
| 14:30 | 37.5853 | 0
| 15:30 | 42.2316 | 0
| 16:30 | 52.0266 | 0
| 17:30 | 57.5719 | 0
| 18:30 | 5.22 | 0
| 19:30 | 5.8476 | 0
| 20:30 | 6.2809 | 0
| 21:30 | 6.8205 | 0
| 22:30 | 7.2867 | 0
| 23:30 | 7.6481 | 0
Sat, 18/Dec | 0:30 | 7.9652 | 0
| 1:30 | 8.2386 | 0
| 2:30 | 8.434 | 0
| 3:30 | 8.4607 | 0
| 4:30 | 8.4121 | 0
| 5:30 | 8.417 | 0
| 6:30 | 8.4341 | 0
| 7:30 | 8.4139 | 0
| 8:30 | 8.3832 | 0
| 9:30 | 8.3367 | 0
| 10:30 | 8.2499 | 0
| 11:30 | 8.0401 | 0
| 12:30 | 7.7565 | 0
| 13:30 | 7.5637 | 0
| 14:30 | 7.4653 | 0
| 15:30 | 7.6438 | 0
| 16:30 | 7.8662 | 0
| 17:30 | 7.8699 | 0
| 18:30 | 7.7824 | 0
| 19:30 | 7.8479 | 0
| 20:30 | 7.9159 | 0
| 21:30 | 7.8276 | 0
| 22:30 | 7.7112 | 0
| 23:30 | 7.5716 | 0
Sun, 19/Dec | 0:30 | 7.4783 | 0
| 1:30 | 7.4488 | 0
| 2:30 | 7.3825 | 0
| 3:30 | 7.3177 | 0
| 4:30 | 7.3776 | 0
| 5:30 | 7.3821 | 0
| 6:30 | 7.4112 | 0
| 7:30 | 7.4368 | 0
| 8:30 | 7.333 | 0
| 9:30 | 7.2814 | 0
| 10:30 | 7.1167 | 0
| 11:30 | 6.8026 | 0
| 12:30 | 6.6772 | 0
| 13:30 | 6.611 | 0
| 14:30 | 6.4928 | 0
| 15:30 | 6.5471 | 0
| 16:30 | 6.6866 | 0
| 17:30 | 6.8074 | 0
| 18:30 | 6.9406 | 0
| 19:30 | 7.0919 | 0
| 20:30 | 7.1839 | 0
| 21:30 | 7.349 | 0
| 22:30 | 7.5995 | 0
| 23:30 | 7.6486 | 0
Mon, 20/Dec | 0:30 | 7.708 | 0
| 1:30 | 7.8317 | 0
| 2:30 | 7.8652 | 0
| 3:30 | 7.8707 | 0
| 4:30 | 7.9912 | 0
| 5:30 | 8.1248 | 0
| 6:30 | 8.2739 | 0
| 7:30 | 8.4441 | 0
| 8:30 | 557.6465 | 0
| 9:30 | 95.8666 | 0
| 10:30 | 62.9479 | 0
| 11:30 | 46.7426 | 0
| 12:30 | 37.7244 | 0
| 13:30 | 33.1811 | 0
| 14:30 | 31.8151 | 0
| 15:30 | 37.7991 | 0
| 16:30 | 46.874 | 0
| 17:30 | 46.2318 | 0
| 18:30 | 3.4329 | 0
| 19:30 | 4.3302 | 0
| 20:30 | 5.0349 | 0
| 21:30 | 5.6629 | 0
| 22:30 | 6.4467 | 0
| 23:30 | 7.2062 | 0
Tue, 21/Dec | 0:30 | 7.7856 | 0
| 1:30 | 8.2414 | 0
| 2:30 | 8.5737 | 0
| 3:30 | 8.9995 | 0
| 4:30 | 9.3041 | 0
| 5:30 | 9.3686 | 0
| 6:30 | 9.3587 | 0
| 7:30 | 9.3855 | 0
| 8:30 | 554.0182 | 0
| 9:30 | 111.7451 | 0
| 10:30 | 80.3341 | 0
| 11:30 | 63.4862 | 0
| 12:30 | 52.5352 | 0
| 13:30 | 44.0026 | 0
| 14:30 | 39.2769 | 0
| 15:30 | 39.3625 | 0
| 16:30 | 40.9778 | 0
| 17:30 | 40.2985 | 0
| 18:30 | 3.6363 | 0
| 19:30 | 4.1376 | 0
| 20:30 | 4.376 | 0
| 21:30 | 4.7441 | 0
| 22:30 | 5.0709 | 0
| 23:30 | 5.1557 | 0
Wed, 22/Dec | 0:30 | 5.1699 | 0
| 1:30 | 5.3114 | 0
| 2:30 | 5.3488 | 0
| 3:30 | 5.1948 | 0
| 4:30 | 4.9816 | 0
| 5:30 | 4.7761 | 0
| 6:30 | 4.7158 | 0
| 7:30 | 4.7905 | 0
| 8:30 | 320.7407 | 0
| 9:30 | 33.3777 | 0
| 10:30 | 17.1267 | 0
| 11:30 | 11.5142 | 0
| 12:30 | 9.9005 | 0
| 13:30 | 8.6829 | 0
| 14:30 | 8.1554 | 0
| 15:30 | 8.3004 | 0
| 16:30 | 8.5957 | 0
| 17:30 | 8.3878 | 0
| 18:30 | 0.728 | 0
| 19:30 | 1.473 | 0
| 20:30 | 1.8439 | 0
| 21:30 | 2.1073 | 0
| 22:30 | 2.0551 | 0
| 23:30 | 1.9297 | 0
Thu, 23/Dec | 0:30 | 2.0432 | 0
| 1:30 | 2.1994 | 0
| 2:30 | 2.2356 | 0
| 3:30 | 2.2303 | 0
| 4:30 | 2.2286 | 0
| 5:30 | 2.2187 | 0
| 6:30 | 2.3312 | 0
| 7:30 | 2.5752 | 0
| 8:30 | 203.7019 | 0
| 9:30 | 12.0291 | 0
| 10:30 | 7.1426 | 0
| 11:30 | 5.5 | 0
| 12:30 | 5.115 | 0
| 13:30 | 5.1818 | 0
| 14:30 | 5.657 | 0
| 15:30 | 6.5086 | 0
| 16:30 | 7.3214 | 0
| 17:30 | 7.4911 | 0
| 18:30 | 0.4508 | 0
| 19:30 | 1.1307 | 0
| 20:30 | 1.4198 | 0
| 21:30 | 1.968 | 0
| 22:30 | 2.049 | 0
| 23:30 | 2.561 | 0
Fri, 24/Dec | 0:30 | 3.9598 | 0
| 1:30 | 4.6765 | 0
| 2:30 | 5.0171 | 0
| 3:30 | 5.3852 | 0
| 4:30 | 5.5803 | 0
| 5:30 | 5.7025 | 0
| 6:30 | 6.1884 | 0
| 7:30 | 6.6794 | 0
| 8:30 | 383.9127 | 0
| 9:30 | 82.0429 | 0
| 10:30 | 56.9245 | 0
| 11:30 | 42.6742 | 0
| 12:30 | 33.5215 | 0
| 13:30 | 27.576 | 0
| 14:30 | 25.3211 | 0
| 15:30 | 28.4628 | 0
| 16:30 | 35.9836 | 0
| 17:30 | 39.1082 | 0
| 18:30 | 3.9843 | 0
| 19:30 | 4.5375 | 0
| 20:30 | 4.764 | 0
| 21:30 | 4.9153 | 0
| 22:30 | 5.3018 | 0
| 23:30 | 5.4604 | 0
Sat, 25/Dec | 0:30 | 5.4891 | 0
| 1:30 | 5.5939 | 0
| 2:30 | 5.4528 | 0
| 3:30 | 5.2717 | 0
| 4:30 | 5.2607 | 0
| 5:30 | 5.2059 | 0
| 6:30 | 4.9602 | 0
| 7:30 | 4.6647 | 0
| 8:30 | 4.525 | 0
| 9:30 | 4.692 | 0
| 10:30 | 4.8271 | 0
| 11:30 | 4.8455 | 0
| 12:30 | 5.2732 | 0
| 13:30 | 5.9745 | 0
| 14:30 | 6.5209 | 0
| 15:30 | 6.949 | 0
| 16:30 | 7.4393 | 0
| 17:30 | 7.7746 | 0
| 18:30 | 7.9888 | 0
| 19:30 | 8.2203 | 0
| 20:30 | 8.5364 | 0
| 21:30 | 8.8947 | 0
| 22:30 | 9.1968 | 0
| 23:30 | 9.3871 | 0
Sun, 26/Dec | 0:30 | 9.6163 | 0
| 1:30 | 9.8729 | 0
| 2:30 | 10.0023 | 0
| 3:30 | 10.0916 | 0
| 4:30 | 10.2661 | 0
| 5:30 | 10.489 | 0
| 6:30 | 10.6796 | 0
| 7:30 | 10.7126 | 0
| 8:30 | 10.578 | 0
| 9:30 | 10.3597 | 0
| 10:30 | 9.9865 | 0
| 11:30 | 9.6097 | 0
| 12:30 | 9.5075 | 0
| 13:30 | 9.5022 | 0
| 14:30 | 9.5098 | 0
| 15:30 | 9.7002 | 0
| 16:30 | 10.1318 | 0
| 17:30 | 10.5829 | 0
| 18:30 | 10.8203 | 0
| 19:30 | 11.0475 | 0
| 20:30 | 11.3286 | 0
| 21:30 | 11.6087 | 0
| 22:30 | 11.8208 | 0
| 23:30 | 12.1034 | 0
Mon, 27/Dec | 0:30 | 12.377 | 0
| 1:30 | 12.3966 | 0
| 2:30 | 12.11 | 0
| 3:30 | 12.0541 | 0
| 4:30 | 12.442 | 0
| 5:30 | 12.4685 | 0
| 6:30 | 12.2423 | 0
| 7:30 | 12.1327 | 0
| 8:30 | 12.4016 | 0
| 9:30 | 12.7608 | 0
| 10:30 | 12.7202 | 0
| 11:30 | 12.5131 | 0
| 12:30 | 12.2041 | 0
| 13:30 | 11.8754 | 0
| 14:30 | 11.4383 | 0
| 15:30 | 11.2069 | 0
| 16:30 | 11.2616 | 0
| 17:30 | 11.264 | 0
| 18:30 | 11.317 | 0
| 19:30 | 11.3882 | 0
| 20:30 | 11.4512 | 0
| 21:30 | 11.581 | 0
| 22:30 | 11.724 | 0
| 23:30 | 11.8304 | 0
Tue, 28/Dec | 0:30 | 11.8877 | 0
| 1:30 | 11.8235 | 0
| 2:30 | 11.7343 | 0
| 3:30 | 11.7348 | 0
| 4:30 | 11.8689 | 0
| 5:30 | 11.9503 | 0
| 6:30 | 11.8581 | 0
| 7:30 | 11.7868 | 0
| 8:30 | 11.6329 | 0
| 9:30 | 11.4194 | 0
| 10:30 | 11.1928 | 0
| 11:30 | 10.77 | 0
| 12:30 | 10.4119 | 0
| 13:30 | 10.1566 | 0
| 14:30 | 9.9036 | 0
| 15:30 | 9.879 | 0
| 16:30 | 9.9993 | 0
| 17:30 | 10.0615 | 0
| 18:30 | 10.0057 | 0
| 19:30 | 9.9992 | 0
| 20:30 | 10.0666 | 0
| 21:30 | 10.0838 | 0
| 22:30 | 10.0184 | 0
| 23:30 | 9.9197 | 0
Wed, 29/Dec | 0:30 | 10.0453 | 0
| 1:30 | 10.264 | 0
| 2:30 | 10.2993 | 0
| 3:30 | 10.3553 | 0
| 4:30 | 10.3708 | 0
| 5:30 | 10.1693 | 0
| 6:30 | 10.036 | 0
| 7:30 | 9.9515 | 0
| 8:30 | 773.8599 | 0
| 9:30 | 132.4837 | 0
| 10:30 | 93.0704 | 0
| 11:30 | 74.3489 | 0
| 12:30 | 58.7802 | 0
| 13:30 | 48.9681 | 0
| 14:30 | 43.7639 | 0
| 15:30 | 42.5083 | 0
| 16:30 | 42.9229 | 0
| 17:30 | 39.0624 | 0
| 18:30 | 1.9108 | 0
| 19:30 | 2.5183 | 0
| 20:30 | 3.3486 | 0
| 21:30 | 4.2208 | 0
| 22:30 | 5.253 | 0
| 23:30 | 5.8794 | 0
Thu, 30/Dec | 0:30 | 6.3813 | 0
| 1:30 | 6.8728 | 0
| 2:30 | 7.1596 | 0
| 3:30 | 7.3801 | 0
| 4:30 | 7.5459 | 0
| 5:30 | 7.6609 | 0
| 6:30 | 7.8171 | 0
| 7:30 | 7.9194 | 0
| 8:30 | 543.5721 | 0
| 9:30 | 81.5075 | 0
| 10:30 | 53.0766 | 0
| 11:30 | 39.876 | 0
| 12:30 | 33.4726 | 0
| 13:30 | 25.8401 | 0
| 14:30 | 18.2096 | 0
| 15:30 | 16.6928 | 0
| 16:30 | 17.5135 | 0
| 17:30 | 17.1117 | 0
| 18:30 | 1.686 | 0
| 19:30 | 2.2099 | 0
| 20:30 | 2.6365 | 0
| 21:30 | 3.0963 | 0
| 22:30 | 3.4832 | 0
| 23:30 | 3.7376 | 0
Fri, 31/Dec | 0:30 | 4.1755 | 0
| 1:30 | 4.6763 | 0
| 2:30 | 5.0339 | 0
| 3:30 | 5.3509 | 0
| 4:30 | 5.6389 | 0
| 5:30 | 5.8356 | 0
| 6:30 | 6.0718 | 0
| 7:30 | 6.5238 | 0
| 8:30 | 433.4269 | 0
| 9:30 | 77.9993 | 0
| 10:30 | 54.8715 | 0
| 11:30 | 42.1585 | 0
| 12:30 | 32.3102 | 0
| 13:30 | 26.4245 | 0
| 14:30 | 23.5141 | 0
| 15:30 | 28.1924 | 0
| 16:30 | 40.6673 | 0
| 17:30 | 46.3573 | 0
| 18:30 | 4.3349 | 0
| 19:30 | 5.1319 | 0
| 20:30 | 5.6162 | 0
| 21:30 | 6.1837 | 0
| 22:30 | 6.5957 | 0
| 23:30 | 6.943 | 0

## Thermal Profile (Sensible)
Below is the sum of the thermal gain / loss per hour for the area served by the AHU expressed as a positive number for heat gain or a negative number for heat loss. The number is in kW
Hour
Date | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
2021-01-01 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 24
2021-01-02 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 48
2021-01-03 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 72
2021-01-04 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 96
2021-01-05 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 120
2021-01-06 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 144
2021-01-07 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 168
2021-01-08 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 192
2021-01-09 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 216
2021-01-10 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 240
2021-01-11 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 264
2021-01-12 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 288
2021-01-13 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 312
2021-01-14 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 336
2021-01-15 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 360
2021-01-16 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 384
2021-01-17 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 408
2021-01-18 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 432
2021-01-19 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 456
2021-01-20 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 480
2021-01-21 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 504
2021-01-22 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 528
2021-01-23 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 552
2021-01-24 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 576
2021-01-25 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 600
2021-01-26 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 624
2021-01-27 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 648
2021-01-28 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 672
2021-01-29 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 696
2021-01-30 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 720
2021-01-31 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 744
2021-02-01 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 768
2021-02-02 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 792
2021-02-03 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 816
2021-02-04 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 840
2021-02-05 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 864
2021-02-06 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 888
2021-02-07 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 912
2021-02-08 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 936
2021-02-09 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 960
2021-02-10 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 984
2021-02-11 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1008
2021-02-12 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1032
2021-02-13 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1056
2021-02-14 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1080
2021-02-15 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1104
2021-02-16 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1128
2021-02-17 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1152
2021-02-18 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1176
2021-02-19 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1200
2021-02-20 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1224
2021-02-21 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1248
2021-02-22 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1272
2021-02-23 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1296
2021-02-24 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1320
2021-02-25 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1344
2021-02-26 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1368
2021-02-27 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1392
2021-02-28 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1416
2021-03-01 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1440
2021-03-02 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1464
2021-03-03 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1488
2021-03-04 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1512
2021-03-05 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1536
2021-03-06 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1560
2021-03-07 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1584
2021-03-08 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1608
2021-03-09 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1632
2021-03-10 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1656
2021-03-11 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1680
2021-03-12 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1704
2021-03-13 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1728
2021-03-14 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1752
2021-03-15 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1776
2021-03-16 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1800
2021-03-17 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1824
2021-03-18 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1848
2021-03-19 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1872
2021-03-20 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1896
2021-03-21 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1920
2021-03-22 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1944
2021-03-23 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1968
2021-03-24 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1992
2021-03-25 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2016
2021-03-26 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2040
2021-03-27 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2064
2021-03-28 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2088
2021-03-29 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2112
2021-03-30 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2136
2021-03-31 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2160
2021-04-01 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2184
2021-04-02 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2208
2021-04-03 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2232
2021-04-04 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2256
2021-04-05 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2280
2021-04-06 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2304
2021-04-07 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2328
2021-04-08 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2352
2021-04-09 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2376
2021-04-10 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2400
2021-04-11 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2424
2021-04-12 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2448
2021-04-13 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2472
2021-04-14 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2496
2021-04-15 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2520
2021-04-16 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2544
2021-04-17 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2568
2021-04-18 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2592
2021-04-19 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2616
2021-04-20 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2640
2021-04-21 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2664
2021-04-22 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2688
2021-04-23 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2712
2021-04-24 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2736
2021-04-25 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2760
2021-04-26 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2784
2021-04-27 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2808
2021-04-28 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2832
2021-04-29 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2856
2021-04-30 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2880
2021-05-01 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2904
2021-05-02 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2928
2021-05-03 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2952
2021-05-04 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 2976
2021-05-05 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3000
2021-05-06 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3024
2021-05-07 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3048
2021-05-08 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3072
2021-05-09 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3096
2021-05-10 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3120
2021-05-11 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3144
2021-05-12 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3168
2021-05-13 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3192
2021-05-14 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3216
2021-05-15 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3240
2021-05-16 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3264
2021-05-17 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3288
2021-05-18 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3312
2021-05-19 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3336
2021-05-20 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3360
2021-05-21 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3384
2021-05-22 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3408
2021-05-23 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3432
2021-05-24 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3456
2021-05-25 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3480
2021-05-26 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3504
2021-05-27 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3528
2021-05-28 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3552
2021-05-29 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3576
2021-05-30 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3600
2021-05-31 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3624
2021-06-01 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3648
2021-06-02 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3672
2021-06-03 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3696
2021-06-04 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3720
2021-06-05 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3744
2021-06-06 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3768
2021-06-07 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3792
2021-06-08 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3816
2021-06-09 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3840
2021-06-10 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3864
2021-06-11 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3888
2021-06-12 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3912
2021-06-13 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3936
2021-06-14 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3960
2021-06-15 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 3984
2021-06-16 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4008
2021-06-17 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4032
2021-06-18 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4056
2021-06-19 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4080
2021-06-20 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4104
2021-06-21 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4128
2021-06-22 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4152
2021-06-23 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4176
2021-06-24 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4200
2021-06-25 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4224
2021-06-26 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4248
2021-06-27 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4272
2021-06-28 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4296
2021-06-29 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4320
2021-06-30 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4344
2021-07-01 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4368
2021-07-02 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4392
2021-07-03 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4416
2021-07-04 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4440
2021-07-05 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4464
2021-07-06 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4488
2021-07-07 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4512
2021-07-08 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4536
2021-07-09 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4560
2021-07-10 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4584
2021-07-11 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4608
2021-07-12 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4632
2021-07-13 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4656
2021-07-14 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4680
2021-07-15 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4704
2021-07-16 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4728
2021-07-17 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4752
2021-07-18 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4776
2021-07-19 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4800
2021-07-20 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4824
2021-07-21 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4848
2021-07-22 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4872
2021-07-23 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4896
2021-07-24 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4920
2021-07-25 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4944
2021-07-26 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4968
2021-07-27 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 4992
2021-07-28 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5016
2021-07-29 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5040
2021-07-30 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5064
2021-07-31 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5088
2021-08-01 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5112
2021-08-02 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5136
2021-08-03 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5160
2021-08-04 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5184
2021-08-05 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5208
2021-08-06 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5232
2021-08-07 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5256
2021-08-08 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5280
2021-08-09 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5304
2021-08-10 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5328
2021-08-11 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5352
2021-08-12 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5376
2021-08-13 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5400
2021-08-14 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5424
2021-08-15 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5448
2021-08-16 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5472
2021-08-17 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5496
2021-08-18 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5520
2021-08-19 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5544
2021-08-20 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5568
2021-08-21 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5592
2021-08-22 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5616
2021-08-23 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5640
2021-08-24 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5664
2021-08-25 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5688
2021-08-26 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5712
2021-08-27 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5736
2021-08-28 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5760
2021-08-29 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5784
2021-08-30 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5808
2021-08-31 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5832
2021-09-01 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5856
2021-09-02 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5880
2021-09-03 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5904
2021-09-04 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5928
2021-09-05 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5952
2021-09-06 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 5976
2021-09-07 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6000
2021-09-08 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6024
2021-09-09 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6048
2021-09-10 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6072
2021-09-11 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6096
2021-09-12 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6120
2021-09-13 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6144
2021-09-14 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6168
2021-09-15 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6192
2021-09-16 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6216
2021-09-17 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6240
2021-09-18 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6264
2021-09-19 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6288
2021-09-20 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6312
2021-09-21 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6336
2021-09-22 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6360
2021-09-23 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6384
2021-09-24 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6408
2021-09-25 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6432
2021-09-26 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6456
2021-09-27 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6480
2021-09-28 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6504
2021-09-29 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6528
2021-09-30 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6552
2021-10-01 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6576
2021-10-02 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6600
2021-10-03 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6624
2021-10-04 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6648
2021-10-05 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6672
2021-10-06 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6696
2021-10-07 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6720
2021-10-08 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6744
2021-10-09 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6768
2021-10-10 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6792
2021-10-11 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6816
2021-10-12 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6840
2021-10-13 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6864
2021-10-14 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6888
2021-10-15 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6912
2021-10-16 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6936
2021-10-17 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6960
2021-10-18 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6984
2021-10-19 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7008
2021-10-20 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7032
2021-10-21 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7056
2021-10-22 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7080
2021-10-23 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7104
2021-10-24 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7128
2021-10-25 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7152
2021-10-26 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7176
2021-10-27 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7200
2021-10-28 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7224
2021-10-29 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7248
2021-10-30 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7272
2021-10-31 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7296
2021-11-01 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7320
2021-11-02 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7344
2021-11-03 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7368
2021-11-04 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7392
2021-11-05 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7416
2021-11-06 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7440
2021-11-07 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7464
2021-11-08 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7488
2021-11-09 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7512
2021-11-10 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7536
2021-11-11 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7560
2021-11-12 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7584
2021-11-13 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7608
2021-11-14 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7632
2021-11-15 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7656
2021-11-16 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7680
2021-11-17 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7704
2021-11-18 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7728
2021-11-19 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7752
2021-11-20 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7776
2021-11-21 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7800
2021-11-22 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7824
2021-11-23 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7848
2021-11-24 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7872
2021-11-25 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7896
2021-11-26 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7920
2021-11-27 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7944
2021-11-28 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7968
2021-11-29 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 7992
2021-11-30 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8016
2021-12-01 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8040
2021-12-02 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8064
2021-12-03 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8088
2021-12-04 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8112
2021-12-05 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8136
2021-12-06 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8160
2021-12-07 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8184
2021-12-08 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8208
2021-12-09 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8232
2021-12-10 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8256
2021-12-11 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8280
2021-12-12 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8304
2021-12-13 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8328
2021-12-14 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8352
2021-12-15 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8376
2021-12-16 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8400
2021-12-17 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8424
2021-12-18 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8448
2021-12-19 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8472
2021-12-20 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8496
2021-12-21 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8520
2021-12-22 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8544
2021-12-23 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8568
2021-12-24 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8592
2021-12-25 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8616
2021-12-26 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8640
2021-12-27 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8664
2021-12-28 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8688
2021-12-29 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8712
2021-12-30 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8736
2021-12-31 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 8760

## Thermal Profile (Latent)
Below is the sum of the thermal gain / loss per hour for the area served by the AHU expressed as a positive number for heat gain or a negative number for heat loss. The number is in kW
Hour
Date | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
2021-01-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24
2021-01-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48
2021-01-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72
2021-01-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96
2021-01-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120
2021-01-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144
2021-01-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168
2021-01-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192
2021-01-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216
2021-01-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240
2021-01-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264
2021-01-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 288
2021-01-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312
2021-01-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336
2021-01-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360
2021-01-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384
2021-01-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408
2021-01-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 432
2021-01-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 456
2021-01-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480
2021-01-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 504
2021-01-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 528
2021-01-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552
2021-01-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 576
2021-01-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600
2021-01-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 624
2021-01-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 648
2021-01-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 672
2021-01-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 696
2021-01-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720
2021-01-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 744
2021-02-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 768
2021-02-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 792
2021-02-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 816
2021-02-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840
2021-02-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 864
2021-02-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 888
2021-02-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 912
2021-02-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 936
2021-02-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960
2021-02-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 984
2021-02-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1008
2021-02-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1032
2021-02-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1056
2021-02-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1080
2021-02-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1104
2021-02-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1128
2021-02-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1152
2021-02-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1176
2021-02-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200
2021-02-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1224
2021-02-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1248
2021-02-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1272
2021-02-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1296
2021-02-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1320
2021-02-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1344
2021-02-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1368
2021-02-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1392
2021-02-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1416
2021-03-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1440
2021-03-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1464
2021-03-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1488
2021-03-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1512
2021-03-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1536
2021-03-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1560
2021-03-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1584
2021-03-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1608
2021-03-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1632
2021-03-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1656
2021-03-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1680
2021-03-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1704
2021-03-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1728
2021-03-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1752
2021-03-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1776
2021-03-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1800
2021-03-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1824
2021-03-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1848
2021-03-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1872
2021-03-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1896
2021-03-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1920
2021-03-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1944
2021-03-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1968
2021-03-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1992
2021-03-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016
2021-03-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2040
2021-03-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2064
2021-03-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2088
2021-03-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2112
2021-03-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2136
2021-03-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2160
2021-04-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2184
2021-04-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2208
2021-04-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2232
2021-04-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2256
2021-04-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2280
2021-04-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2304
2021-04-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2328
2021-04-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2352
2021-04-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2376
2021-04-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2400
2021-04-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2424
2021-04-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2448
2021-04-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2472
2021-04-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2496
2021-04-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2520
2021-04-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2544
2021-04-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2568
2021-04-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2592
2021-04-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2616
2021-04-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2640
2021-04-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2664
2021-04-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2688
2021-04-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2712
2021-04-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2736
2021-04-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2760
2021-04-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2784
2021-04-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2808
2021-04-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2832
2021-04-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2856
2021-04-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2880
2021-05-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2904
2021-05-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2928
2021-05-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2952
2021-05-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2976
2021-05-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3000
2021-05-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3024
2021-05-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3048
2021-05-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3072
2021-05-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3096
2021-05-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3120
2021-05-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3144
2021-05-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3168
2021-05-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3192
2021-05-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3216
2021-05-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3240
2021-05-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3264
2021-05-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3288
2021-05-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3312
2021-05-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3336
2021-05-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3360
2021-05-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3384
2021-05-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3408
2021-05-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3432
2021-05-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3456
2021-05-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3480
2021-05-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3504
2021-05-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3528
2021-05-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3552
2021-05-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3576
2021-05-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3600
2021-05-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3624
2021-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3648
2021-06-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3672
2021-06-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3696
2021-06-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3720
2021-06-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3744
2021-06-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3768
2021-06-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3792
2021-06-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3816
2021-06-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3840
2021-06-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3864
2021-06-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3888
2021-06-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3912
2021-06-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3936
2021-06-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3960
2021-06-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3984
2021-06-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4008
2021-06-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4032
2021-06-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4056
2021-06-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4080
2021-06-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4104
2021-06-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4128
2021-06-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4152
2021-06-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4176
2021-06-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4200
2021-06-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4224
2021-06-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4248
2021-06-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4272
2021-06-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4296
2021-06-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4320
2021-06-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4344
2021-07-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4368
2021-07-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4392
2021-07-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4416
2021-07-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4440
2021-07-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4464
2021-07-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4488
2021-07-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4512
2021-07-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4536
2021-07-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4560
2021-07-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4584
2021-07-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4608
2021-07-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4632
2021-07-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4656
2021-07-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4680
2021-07-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4704
2021-07-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4728
2021-07-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4752
2021-07-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4776
2021-07-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4800
2021-07-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4824
2021-07-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4848
2021-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4872
2021-07-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4896
2021-07-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4920
2021-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4944
2021-07-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4968
2021-07-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4992
2021-07-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5016
2021-07-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5040
2021-07-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5064
2021-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5088
2021-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5112
2021-08-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5136
2021-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5160
2021-08-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5184
2021-08-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5208
2021-08-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5232
2021-08-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5256
2021-08-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5280
2021-08-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5304
2021-08-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5328
2021-08-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5352
2021-08-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5376
2021-08-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5400
2021-08-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5424
2021-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5448
2021-08-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5472
2021-08-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5496
2021-08-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5520
2021-08-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5544
2021-08-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5568
2021-08-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5592
2021-08-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5616
2021-08-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5640
2021-08-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5664
2021-08-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5688
2021-08-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5712
2021-08-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5736
2021-08-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5760
2021-08-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5784
2021-08-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5808
2021-08-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832
2021-09-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5856
2021-09-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5880
2021-09-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5904
2021-09-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5928
2021-09-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5952
2021-09-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5976
2021-09-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6000
2021-09-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6024
2021-09-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6048
2021-09-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6072
2021-09-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6096
2021-09-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6120
2021-09-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6144
2021-09-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6168
2021-09-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6192
2021-09-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6216
2021-09-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6240
2021-09-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6264
2021-09-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6288
2021-09-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6312
2021-09-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6336
2021-09-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6360
2021-09-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6384
2021-09-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6408
2021-09-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6432
2021-09-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6456
2021-09-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6480
2021-09-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6504
2021-09-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6528
2021-09-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6552
2021-10-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6576
2021-10-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6600
2021-10-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6624
2021-10-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6648
2021-10-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6672
2021-10-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6696
2021-10-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6720
2021-10-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6744
2021-10-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6768
2021-10-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6792
2021-10-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6816
2021-10-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6840
2021-10-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6864
2021-10-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6888
2021-10-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6912
2021-10-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6936
2021-10-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6960
2021-10-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6984
2021-10-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7008
2021-10-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7032
2021-10-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7056
2021-10-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7080
2021-10-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7104
2021-10-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7128
2021-10-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7152
2021-10-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7176
2021-10-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7200
2021-10-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7224
2021-10-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7248
2021-10-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7272
2021-10-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7296
2021-11-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7320
2021-11-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7344
2021-11-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7368
2021-11-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7392
2021-11-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7416
2021-11-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7440
2021-11-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7464
2021-11-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7488
2021-11-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7512
2021-11-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7536
2021-11-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7560
2021-11-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7584
2021-11-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7608
2021-11-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7632
2021-11-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7656
2021-11-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7680
2021-11-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7704
2021-11-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7728
2021-11-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7752
2021-11-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7776
2021-11-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7800
2021-11-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7824
2021-11-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7848
2021-11-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7872
2021-11-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7896
2021-11-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7920
2021-11-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7944
2021-11-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7968
2021-11-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7992
2021-11-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8016
2021-12-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8040
2021-12-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8064
2021-12-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8088
2021-12-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8112
2021-12-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8136
2021-12-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8160
2021-12-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8184
2021-12-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8208
2021-12-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8232
2021-12-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8256
2021-12-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8280
2021-12-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8304
2021-12-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8328
2021-12-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8352
2021-12-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8376
2021-12-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8400
2021-12-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8424
2021-12-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8448
2021-12-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8472
2021-12-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8496
2021-12-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8520
2021-12-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8544
2021-12-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8568
2021-12-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8592
2021-12-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8616
2021-12-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8640
2021-12-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8664
2021-12-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8688
2021-12-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8712
2021-12-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8736
2021-12-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760

## Set Point Shedule
Set Point Profile Generator
Hour | -3 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00
Hour | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Setpoint Day 01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Setpoint Day 02 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Setpoint Day 03 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2
Setpoint Day 04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Setpoint Day 05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Setpoint Day 06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Setpoint Day 07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Setpoint Day 08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Setpoint Day 09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Setpoint Day 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Day | Mon |  | Tue |  | Wed |  | Thu |  | Fri |  | Sat |  | Sun
Day num | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7
Typical Week 01 | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01
Typical Week 02 | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01
Typical Week 03 | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01
Typical Week 04 | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01
Typical Week 05 | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01
Typical Week 06 | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01
Typical Week 07 | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01
Typical Week 08 | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01
Typical Week 09 | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01
Typical Week 10 | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01 |  | Setpoint Day 01
Year | 2021
Week No. | Month |  | Week profile
1 | January |  | Typical Week 01
2 | January |  | Typical Week 02
3 | January |  | Typical Week 03
4 | January |  | Typical Week 04
5 | February |  | Typical Week 05
6 | February |  | Typical Week 06
7 | February |  | Typical Week 07
8 | February |  | Typical Week 08
9 | March |  | Typical Week 09
10 | March |  | Typical Week 10
11 | March |  | Typical Week 01
12 | March |  | Typical Week 02
13 | March |  | Typical Week 03
14 | April |  | Typical Week 04
15 | April |  | Typical Week 05
16 | April |  | Typical Week 06
17 | April |  | Typical Week 07
18 | May |  | Typical Week 08
19 | May |  | Typical Week 09
20 | May |  | Typical Week 10
21 | May |  | Typical Week 01
22 | May |  | Typical Week 02
23 | June |  | Typical Week 03
24 | June |  | Typical Week 04
25 | June |  | Typical Week 05
26 | June |  | Typical Week 06
27 | July |  | Typical Week 07
28 | July |  | Typical Week 08
29 | July |  | Typical Week 09
30 | July |  | Typical Week 10
31 | August |  | Typical Week 01
32 | August |  | Typical Week 02
33 | August |  | Typical Week 03
34 | August |  | Typical Week 04
35 | August |  | Typical Week 05
36 | September |  | Typical Week 06
37 | September |  | Typical Week 07
38 | September |  | Typical Week 08
39 | September |  | Typical Week 09
40 | October |  | Typical Week 10
41 | October |  | Typical Week 01
42 | October |  | Typical Week 02
43 | October |  | Typical Week 03
44 | November |  | Typical Week 04
45 | November |  | Typical Week 05
46 | November |  | Typical Week 06
47 | November |  | Typical Week 07
48 | November |  | Typical Week 08
49 | December |  | Typical Week 09
50 | December |  | Typical Week 10
51 | December |  | Typical Week 01
52 | December |  | Typical Week 02
53 | January |  | Typical Week 03

## Set Point Profile
Hours
Date | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | Week no | Day | Week profile name | Day profile name
2021-01-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | Typical Week 01 | Setpoint Day 01
2021-01-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | Typical Week 01 | Setpoint Day 01
2021-01-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 7 | Typical Week 02 | Setpoint Day 01
2021-01-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | Typical Week 02 | Setpoint Day 01
2021-01-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | Typical Week 02 | Setpoint Day 01
2021-01-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | Typical Week 02 | Setpoint Day 01
2021-01-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 4 | Typical Week 02 | Setpoint Day 01
2021-01-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 5 | Typical Week 02 | Setpoint Day 01
2021-01-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 6 | Typical Week 02 | Setpoint Day 01
2021-01-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 7 | Typical Week 03 | Setpoint Day 01
2021-01-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | Typical Week 03 | Setpoint Day 01
2021-01-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2 | Typical Week 03 | Setpoint Day 01
2021-01-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | Typical Week 03 | Setpoint Day 01
2021-01-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 4 | Typical Week 03 | Setpoint Day 01
2021-01-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 5 | Typical Week 03 | Setpoint Day 01
2021-01-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 6 | Typical Week 03 | Setpoint Day 01
2021-01-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 7 | Typical Week 04 | Setpoint Day 01
2021-01-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 1 | Typical Week 04 | Setpoint Day 01
2021-01-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 2 | Typical Week 04 | Setpoint Day 01
2021-01-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 3 | Typical Week 04 | Setpoint Day 01
2021-01-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 4 | Typical Week 04 | Setpoint Day 01
2021-01-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 5 | Typical Week 04 | Setpoint Day 01
2021-01-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 6 | Typical Week 04 | Setpoint Day 01
2021-01-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 7 | Typical Week 05 | Setpoint Day 01
2021-01-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 1 | Typical Week 05 | Setpoint Day 01
2021-01-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 2 | Typical Week 05 | Setpoint Day 01
2021-01-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 3 | Typical Week 05 | Setpoint Day 01
2021-01-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 4 | Typical Week 05 | Setpoint Day 01
2021-01-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | Typical Week 05 | Setpoint Day 01
2021-01-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 6 | Typical Week 05 | Setpoint Day 01
2021-01-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 7 | Typical Week 06 | Setpoint Day 01
2021-02-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 1 | Typical Week 06 | Setpoint Day 01
2021-02-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 2 | Typical Week 06 | Setpoint Day 01
2021-02-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 3 | Typical Week 06 | Setpoint Day 01
2021-02-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 4 | Typical Week 06 | Setpoint Day 01
2021-02-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 5 | Typical Week 06 | Setpoint Day 01
2021-02-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 6 | Typical Week 06 | Setpoint Day 01
2021-02-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 7 | Typical Week 07 | Setpoint Day 01
2021-02-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 1 | Typical Week 07 | Setpoint Day 01
2021-02-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 2 | Typical Week 07 | Setpoint Day 01
2021-02-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 3 | Typical Week 07 | Setpoint Day 01
2021-02-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 4 | Typical Week 07 | Setpoint Day 01
2021-02-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 5 | Typical Week 07 | Setpoint Day 01
2021-02-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 7 | 6 | Typical Week 07 | Setpoint Day 01
2021-02-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 7 | Typical Week 08 | Setpoint Day 01
2021-02-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 1 | Typical Week 08 | Setpoint Day 01
2021-02-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 2 | Typical Week 08 | Setpoint Day 01
2021-02-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 3 | Typical Week 08 | Setpoint Day 01
2021-02-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 4 | Typical Week 08 | Setpoint Day 01
2021-02-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 5 | Typical Week 08 | Setpoint Day 01
2021-02-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 8 | 6 | Typical Week 08 | Setpoint Day 01
2021-02-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 7 | Typical Week 09 | Setpoint Day 01
2021-02-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 1 | Typical Week 09 | Setpoint Day 01
2021-02-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 2 | Typical Week 09 | Setpoint Day 01
2021-02-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 3 | Typical Week 09 | Setpoint Day 01
2021-02-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 4 | Typical Week 09 | Setpoint Day 01
2021-02-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 5 | Typical Week 09 | Setpoint Day 01
2021-02-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9 | 6 | Typical Week 09 | Setpoint Day 01
2021-02-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 7 | Typical Week 10 | Setpoint Day 01
2021-03-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 1 | Typical Week 10 | Setpoint Day 01
2021-03-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 2 | Typical Week 10 | Setpoint Day 01
2021-03-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 3 | Typical Week 10 | Setpoint Day 01
2021-03-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 4 | Typical Week 10 | Setpoint Day 01
2021-03-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 5 | Typical Week 10 | Setpoint Day 01
2021-03-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 10 | 6 | Typical Week 10 | Setpoint Day 01
2021-03-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 7 | Typical Week 01 | Setpoint Day 01
2021-03-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 1 | Typical Week 01 | Setpoint Day 01
2021-03-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 2 | Typical Week 01 | Setpoint Day 01
2021-03-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 3 | Typical Week 01 | Setpoint Day 01
2021-03-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 4 | Typical Week 01 | Setpoint Day 01
2021-03-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 5 | Typical Week 01 | Setpoint Day 01
2021-03-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 11 | 6 | Typical Week 01 | Setpoint Day 01
2021-03-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 7 | Typical Week 02 | Setpoint Day 01
2021-03-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 1 | Typical Week 02 | Setpoint Day 01
2021-03-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 2 | Typical Week 02 | Setpoint Day 01
2021-03-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 3 | Typical Week 02 | Setpoint Day 01
2021-03-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 4 | Typical Week 02 | Setpoint Day 01
2021-03-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 5 | Typical Week 02 | Setpoint Day 01
2021-03-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 12 | 6 | Typical Week 02 | Setpoint Day 01
2021-03-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 7 | Typical Week 03 | Setpoint Day 01
2021-03-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 1 | Typical Week 03 | Setpoint Day 01
2021-03-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 2 | Typical Week 03 | Setpoint Day 01
2021-03-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 3 | Typical Week 03 | Setpoint Day 01
2021-03-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 4 | Typical Week 03 | Setpoint Day 01
2021-03-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 5 | Typical Week 03 | Setpoint Day 01
2021-03-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 13 | 6 | Typical Week 03 | Setpoint Day 01
2021-03-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 7 | Typical Week 04 | Setpoint Day 01
2021-03-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 1 | Typical Week 04 | Setpoint Day 01
2021-03-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 2 | Typical Week 04 | Setpoint Day 01
2021-03-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 3 | Typical Week 04 | Setpoint Day 01
2021-04-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 4 | Typical Week 04 | Setpoint Day 01
2021-04-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 5 | Typical Week 04 | Setpoint Day 01
2021-04-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 14 | 6 | Typical Week 04 | Setpoint Day 01
2021-04-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 7 | Typical Week 05 | Setpoint Day 01
2021-04-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 1 | Typical Week 05 | Setpoint Day 01
2021-04-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 2 | Typical Week 05 | Setpoint Day 01
2021-04-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 3 | Typical Week 05 | Setpoint Day 01
2021-04-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 4 | Typical Week 05 | Setpoint Day 01
2021-04-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 5 | Typical Week 05 | Setpoint Day 01
2021-04-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15 | 6 | Typical Week 05 | Setpoint Day 01
2021-04-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 7 | Typical Week 06 | Setpoint Day 01
2021-04-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 1 | Typical Week 06 | Setpoint Day 01
2021-04-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 2 | Typical Week 06 | Setpoint Day 01
2021-04-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 3 | Typical Week 06 | Setpoint Day 01
2021-04-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 4 | Typical Week 06 | Setpoint Day 01
2021-04-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 5 | Typical Week 06 | Setpoint Day 01
2021-04-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 16 | 6 | Typical Week 06 | Setpoint Day 01
2021-04-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 7 | Typical Week 07 | Setpoint Day 01
2021-04-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 1 | Typical Week 07 | Setpoint Day 01
2021-04-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 2 | Typical Week 07 | Setpoint Day 01
2021-04-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 3 | Typical Week 07 | Setpoint Day 01
2021-04-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 4 | Typical Week 07 | Setpoint Day 01
2021-04-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 5 | Typical Week 07 | Setpoint Day 01
2021-04-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17 | 6 | Typical Week 07 | Setpoint Day 01
2021-04-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 7 | Typical Week 08 | Setpoint Day 01
2021-04-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 1 | Typical Week 08 | Setpoint Day 01
2021-04-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 2 | Typical Week 08 | Setpoint Day 01
2021-04-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 3 | Typical Week 08 | Setpoint Day 01
2021-04-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 4 | Typical Week 08 | Setpoint Day 01
2021-04-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 5 | Typical Week 08 | Setpoint Day 01
2021-05-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 18 | 6 | Typical Week 08 | Setpoint Day 01
2021-05-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 7 | Typical Week 09 | Setpoint Day 01
2021-05-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 1 | Typical Week 09 | Setpoint Day 01
2021-05-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 2 | Typical Week 09 | Setpoint Day 01
2021-05-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 3 | Typical Week 09 | Setpoint Day 01
2021-05-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 4 | Typical Week 09 | Setpoint Day 01
2021-05-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 5 | Typical Week 09 | Setpoint Day 01
2021-05-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19 | 6 | Typical Week 09 | Setpoint Day 01
2021-05-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 7 | Typical Week 10 | Setpoint Day 01
2021-05-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 1 | Typical Week 10 | Setpoint Day 01
2021-05-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 2 | Typical Week 10 | Setpoint Day 01
2021-05-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 3 | Typical Week 10 | Setpoint Day 01
2021-05-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 4 | Typical Week 10 | Setpoint Day 01
2021-05-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 5 | Typical Week 10 | Setpoint Day 01
2021-05-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 6 | Typical Week 10 | Setpoint Day 01
2021-05-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 7 | Typical Week 01 | Setpoint Day 01
2021-05-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 1 | Typical Week 01 | Setpoint Day 01
2021-05-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 2 | Typical Week 01 | Setpoint Day 01
2021-05-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 3 | Typical Week 01 | Setpoint Day 01
2021-05-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 4 | Typical Week 01 | Setpoint Day 01
2021-05-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 5 | Typical Week 01 | Setpoint Day 01
2021-05-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 21 | 6 | Typical Week 01 | Setpoint Day 01
2021-05-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 7 | Typical Week 02 | Setpoint Day 01
2021-05-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 1 | Typical Week 02 | Setpoint Day 01
2021-05-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 2 | Typical Week 02 | Setpoint Day 01
2021-05-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 3 | Typical Week 02 | Setpoint Day 01
2021-05-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 4 | Typical Week 02 | Setpoint Day 01
2021-05-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 5 | Typical Week 02 | Setpoint Day 01
2021-05-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 22 | 6 | Typical Week 02 | Setpoint Day 01
2021-05-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 7 | Typical Week 03 | Setpoint Day 01
2021-05-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 1 | Typical Week 03 | Setpoint Day 01
2021-06-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 2 | Typical Week 03 | Setpoint Day 01
2021-06-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 3 | Typical Week 03 | Setpoint Day 01
2021-06-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 4 | Typical Week 03 | Setpoint Day 01
2021-06-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 5 | Typical Week 03 | Setpoint Day 01
2021-06-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 23 | 6 | Typical Week 03 | Setpoint Day 01
2021-06-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 7 | Typical Week 04 | Setpoint Day 01
2021-06-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 1 | Typical Week 04 | Setpoint Day 01
2021-06-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 2 | Typical Week 04 | Setpoint Day 01
2021-06-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 3 | Typical Week 04 | Setpoint Day 01
2021-06-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 4 | Typical Week 04 | Setpoint Day 01
2021-06-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 5 | Typical Week 04 | Setpoint Day 01
2021-06-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 24 | 6 | Typical Week 04 | Setpoint Day 01
2021-06-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 7 | Typical Week 05 | Setpoint Day 01
2021-06-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 1 | Typical Week 05 | Setpoint Day 01
2021-06-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 2 | Typical Week 05 | Setpoint Day 01
2021-06-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 3 | Typical Week 05 | Setpoint Day 01
2021-06-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 4 | Typical Week 05 | Setpoint Day 01
2021-06-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 5 | Typical Week 05 | Setpoint Day 01
2021-06-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 25 | 6 | Typical Week 05 | Setpoint Day 01
2021-06-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 7 | Typical Week 06 | Setpoint Day 01
2021-06-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 1 | Typical Week 06 | Setpoint Day 01
2021-06-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 2 | Typical Week 06 | Setpoint Day 01
2021-06-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 3 | Typical Week 06 | Setpoint Day 01
2021-06-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 4 | Typical Week 06 | Setpoint Day 01
2021-06-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 5 | Typical Week 06 | Setpoint Day 01
2021-06-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 26 | 6 | Typical Week 06 | Setpoint Day 01
2021-06-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 7 | Typical Week 07 | Setpoint Day 01
2021-06-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 1 | Typical Week 07 | Setpoint Day 01
2021-06-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 2 | Typical Week 07 | Setpoint Day 01
2021-06-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 3 | Typical Week 07 | Setpoint Day 01
2021-07-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 4 | Typical Week 07 | Setpoint Day 01
2021-07-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 5 | Typical Week 07 | Setpoint Day 01
2021-07-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 27 | 6 | Typical Week 07 | Setpoint Day 01
2021-07-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 7 | Typical Week 08 | Setpoint Day 01
2021-07-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 1 | Typical Week 08 | Setpoint Day 01
2021-07-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 2 | Typical Week 08 | Setpoint Day 01
2021-07-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 3 | Typical Week 08 | Setpoint Day 01
2021-07-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 4 | Typical Week 08 | Setpoint Day 01
2021-07-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 5 | Typical Week 08 | Setpoint Day 01
2021-07-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 28 | 6 | Typical Week 08 | Setpoint Day 01
2021-07-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 7 | Typical Week 09 | Setpoint Day 01
2021-07-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 1 | Typical Week 09 | Setpoint Day 01
2021-07-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 2 | Typical Week 09 | Setpoint Day 01
2021-07-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 3 | Typical Week 09 | Setpoint Day 01
2021-07-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 4 | Typical Week 09 | Setpoint Day 01
2021-07-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 5 | Typical Week 09 | Setpoint Day 01
2021-07-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 29 | 6 | Typical Week 09 | Setpoint Day 01
2021-07-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 7 | Typical Week 10 | Setpoint Day 01
2021-07-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 1 | Typical Week 10 | Setpoint Day 01
2021-07-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 2 | Typical Week 10 | Setpoint Day 01
2021-07-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 3 | Typical Week 10 | Setpoint Day 01
2021-07-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 4 | Typical Week 10 | Setpoint Day 01
2021-07-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 5 | Typical Week 10 | Setpoint Day 01
2021-07-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 30 | 6 | Typical Week 10 | Setpoint Day 01
2021-07-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 7 | Typical Week 01 | Setpoint Day 01
2021-07-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 1 | Typical Week 01 | Setpoint Day 01
2021-07-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 2 | Typical Week 01 | Setpoint Day 01
2021-07-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 3 | Typical Week 01 | Setpoint Day 01
2021-07-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 4 | Typical Week 01 | Setpoint Day 01
2021-07-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 5 | Typical Week 01 | Setpoint Day 01
2021-07-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 31 | 6 | Typical Week 01 | Setpoint Day 01
2021-08-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 7 | Typical Week 02 | Setpoint Day 01
2021-08-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 1 | Typical Week 02 | Setpoint Day 01
2021-08-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 2 | Typical Week 02 | Setpoint Day 01
2021-08-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 3 | Typical Week 02 | Setpoint Day 01
2021-08-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 4 | Typical Week 02 | Setpoint Day 01
2021-08-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 5 | Typical Week 02 | Setpoint Day 01
2021-08-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 32 | 6 | Typical Week 02 | Setpoint Day 01
2021-08-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 7 | Typical Week 03 | Setpoint Day 01
2021-08-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 1 | Typical Week 03 | Setpoint Day 01
2021-08-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 2 | Typical Week 03 | Setpoint Day 01
2021-08-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 3 | Typical Week 03 | Setpoint Day 01
2021-08-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 4 | Typical Week 03 | Setpoint Day 01
2021-08-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 5 | Typical Week 03 | Setpoint Day 01
2021-08-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 33 | 6 | Typical Week 03 | Setpoint Day 01
2021-08-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 7 | Typical Week 04 | Setpoint Day 01
2021-08-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 1 | Typical Week 04 | Setpoint Day 01
2021-08-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 2 | Typical Week 04 | Setpoint Day 01
2021-08-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 3 | Typical Week 04 | Setpoint Day 01
2021-08-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 4 | Typical Week 04 | Setpoint Day 01
2021-08-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 5 | Typical Week 04 | Setpoint Day 01
2021-08-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 34 | 6 | Typical Week 04 | Setpoint Day 01
2021-08-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 7 | Typical Week 05 | Setpoint Day 01
2021-08-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 1 | Typical Week 05 | Setpoint Day 01
2021-08-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 2 | Typical Week 05 | Setpoint Day 01
2021-08-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 3 | Typical Week 05 | Setpoint Day 01
2021-08-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 4 | Typical Week 05 | Setpoint Day 01
2021-08-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 5 | Typical Week 05 | Setpoint Day 01
2021-08-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 35 | 6 | Typical Week 05 | Setpoint Day 01
2021-08-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 7 | Typical Week 06 | Setpoint Day 01
2021-08-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 1 | Typical Week 06 | Setpoint Day 01
2021-08-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 2 | Typical Week 06 | Setpoint Day 01
2021-09-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 3 | Typical Week 06 | Setpoint Day 01
2021-09-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 4 | Typical Week 06 | Setpoint Day 01
2021-09-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 5 | Typical Week 06 | Setpoint Day 01
2021-09-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 36 | 6 | Typical Week 06 | Setpoint Day 01
2021-09-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 7 | Typical Week 07 | Setpoint Day 01
2021-09-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 1 | Typical Week 07 | Setpoint Day 01
2021-09-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 2 | Typical Week 07 | Setpoint Day 01
2021-09-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 3 | Typical Week 07 | Setpoint Day 01
2021-09-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 4 | Typical Week 07 | Setpoint Day 01
2021-09-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 5 | Typical Week 07 | Setpoint Day 01
2021-09-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 37 | 6 | Typical Week 07 | Setpoint Day 01
2021-09-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 7 | Typical Week 08 | Setpoint Day 01
2021-09-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 1 | Typical Week 08 | Setpoint Day 01
2021-09-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 2 | Typical Week 08 | Setpoint Day 01
2021-09-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 3 | Typical Week 08 | Setpoint Day 01
2021-09-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 4 | Typical Week 08 | Setpoint Day 01
2021-09-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 5 | Typical Week 08 | Setpoint Day 01
2021-09-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 38 | 6 | Typical Week 08 | Setpoint Day 01
2021-09-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 7 | Typical Week 09 | Setpoint Day 01
2021-09-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 1 | Typical Week 09 | Setpoint Day 01
2021-09-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 2 | Typical Week 09 | Setpoint Day 01
2021-09-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 3 | Typical Week 09 | Setpoint Day 01
2021-09-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 4 | Typical Week 09 | Setpoint Day 01
2021-09-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 5 | Typical Week 09 | Setpoint Day 01
2021-09-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 39 | 6 | Typical Week 09 | Setpoint Day 01
2021-09-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 7 | Typical Week 10 | Setpoint Day 01
2021-09-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 1 | Typical Week 10 | Setpoint Day 01
2021-09-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 2 | Typical Week 10 | Setpoint Day 01
2021-09-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 3 | Typical Week 10 | Setpoint Day 01
2021-09-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 4 | Typical Week 10 | Setpoint Day 01
2021-10-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 5 | Typical Week 10 | Setpoint Day 01
2021-10-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 40 | 6 | Typical Week 10 | Setpoint Day 01
2021-10-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 7 | Typical Week 01 | Setpoint Day 01
2021-10-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 1 | Typical Week 01 | Setpoint Day 01
2021-10-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 2 | Typical Week 01 | Setpoint Day 01
2021-10-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 3 | Typical Week 01 | Setpoint Day 01
2021-10-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 4 | Typical Week 01 | Setpoint Day 01
2021-10-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 5 | Typical Week 01 | Setpoint Day 01
2021-10-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 41 | 6 | Typical Week 01 | Setpoint Day 01
2021-10-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 7 | Typical Week 02 | Setpoint Day 01
2021-10-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 1 | Typical Week 02 | Setpoint Day 01
2021-10-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 2 | Typical Week 02 | Setpoint Day 01
2021-10-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 3 | Typical Week 02 | Setpoint Day 01
2021-10-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 4 | Typical Week 02 | Setpoint Day 01
2021-10-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 5 | Typical Week 02 | Setpoint Day 01
2021-10-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 42 | 6 | Typical Week 02 | Setpoint Day 01
2021-10-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 7 | Typical Week 03 | Setpoint Day 01
2021-10-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 1 | Typical Week 03 | Setpoint Day 01
2021-10-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 2 | Typical Week 03 | Setpoint Day 01
2021-10-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 3 | Typical Week 03 | Setpoint Day 01
2021-10-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 4 | Typical Week 03 | Setpoint Day 01
2021-10-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 5 | Typical Week 03 | Setpoint Day 01
2021-10-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 43 | 6 | Typical Week 03 | Setpoint Day 01
2021-10-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 7 | Typical Week 04 | Setpoint Day 01
2021-10-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 1 | Typical Week 04 | Setpoint Day 01
2021-10-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 2 | Typical Week 04 | Setpoint Day 01
2021-10-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 3 | Typical Week 04 | Setpoint Day 01
2021-10-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 4 | Typical Week 04 | Setpoint Day 01
2021-10-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 5 | Typical Week 04 | Setpoint Day 01
2021-10-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 44 | 6 | Typical Week 04 | Setpoint Day 01
2021-10-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 7 | Typical Week 05 | Setpoint Day 01
2021-11-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 1 | Typical Week 05 | Setpoint Day 01
2021-11-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 2 | Typical Week 05 | Setpoint Day 01
2021-11-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 3 | Typical Week 05 | Setpoint Day 01
2021-11-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 4 | Typical Week 05 | Setpoint Day 01
2021-11-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 5 | Typical Week 05 | Setpoint Day 01
2021-11-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 45 | 6 | Typical Week 05 | Setpoint Day 01
2021-11-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 7 | Typical Week 06 | Setpoint Day 01
2021-11-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 1 | Typical Week 06 | Setpoint Day 01
2021-11-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 2 | Typical Week 06 | Setpoint Day 01
2021-11-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 3 | Typical Week 06 | Setpoint Day 01
2021-11-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 4 | Typical Week 06 | Setpoint Day 01
2021-11-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 5 | Typical Week 06 | Setpoint Day 01
2021-11-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 46 | 6 | Typical Week 06 | Setpoint Day 01
2021-11-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 7 | Typical Week 07 | Setpoint Day 01
2021-11-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 1 | Typical Week 07 | Setpoint Day 01
2021-11-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 2 | Typical Week 07 | Setpoint Day 01
2021-11-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 3 | Typical Week 07 | Setpoint Day 01
2021-11-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 4 | Typical Week 07 | Setpoint Day 01
2021-11-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 5 | Typical Week 07 | Setpoint Day 01
2021-11-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 47 | 6 | Typical Week 07 | Setpoint Day 01
2021-11-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 7 | Typical Week 08 | Setpoint Day 01
2021-11-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 1 | Typical Week 08 | Setpoint Day 01
2021-11-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 2 | Typical Week 08 | Setpoint Day 01
2021-11-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 3 | Typical Week 08 | Setpoint Day 01
2021-11-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 4 | Typical Week 08 | Setpoint Day 01
2021-11-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 5 | Typical Week 08 | Setpoint Day 01
2021-11-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 48 | 6 | Typical Week 08 | Setpoint Day 01
2021-11-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 7 | Typical Week 09 | Setpoint Day 01
2021-11-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 1 | Typical Week 09 | Setpoint Day 01
2021-11-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 2 | Typical Week 09 | Setpoint Day 01
2021-12-01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 3 | Typical Week 09 | Setpoint Day 01
2021-12-02 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 4 | Typical Week 09 | Setpoint Day 01
2021-12-03 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 5 | Typical Week 09 | Setpoint Day 01
2021-12-04 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 49 | 6 | Typical Week 09 | Setpoint Day 01
2021-12-05 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 7 | Typical Week 10 | Setpoint Day 01
2021-12-06 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 1 | Typical Week 10 | Setpoint Day 01
2021-12-07 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 2 | Typical Week 10 | Setpoint Day 01
2021-12-08 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 3 | Typical Week 10 | Setpoint Day 01
2021-12-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 4 | Typical Week 10 | Setpoint Day 01
2021-12-10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 5 | Typical Week 10 | Setpoint Day 01
2021-12-11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 50 | 6 | Typical Week 10 | Setpoint Day 01
2021-12-12 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 7 | Typical Week 01 | Setpoint Day 01
2021-12-13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 1 | Typical Week 01 | Setpoint Day 01
2021-12-14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 2 | Typical Week 01 | Setpoint Day 01
2021-12-15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 3 | Typical Week 01 | Setpoint Day 01
2021-12-16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 4 | Typical Week 01 | Setpoint Day 01
2021-12-17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 5 | Typical Week 01 | Setpoint Day 01
2021-12-18 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 51 | 6 | Typical Week 01 | Setpoint Day 01
2021-12-19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 7 | Typical Week 02 | Setpoint Day 01
2021-12-20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 1 | Typical Week 02 | Setpoint Day 01
2021-12-21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 2 | Typical Week 02 | Setpoint Day 01
2021-12-22 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 3 | Typical Week 02 | Setpoint Day 01
2021-12-23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 4 | Typical Week 02 | Setpoint Day 01
2021-12-24 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 5 | Typical Week 02 | Setpoint Day 01
2021-12-25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 52 | 6 | Typical Week 02 | Setpoint Day 01
2021-12-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 53 | 7 | Typical Week 03 | Setpoint Day 01
2021-12-27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 53 | 1 | Typical Week 03 | Setpoint Day 01
2021-12-28 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 53 | 2 | Typical Week 03 | Setpoint Day 01
2021-12-29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 53 | 3 | Typical Week 03 | Setpoint Day 01
2021-12-30 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 53 | 4 | Typical Week 03 | Setpoint Day 01
2021-12-31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 53 | 5 | Typical Week 03 | Setpoint Day 01