## Model Inputs
No. | Type | Parameter | Description | Units | 0 | 1
1 | General Description | Site Location | Site reference | - | MSD Brinny | MSD Brinny
2 |  | Building | Building reference | - | Building 21 | Building 21
3 |  | AHU | Air Handling Unit Reference | - | Multiple Combined | Multiple Combined
4 | Room | Room Area |  | m² | 3000 | 6000
5 |  | Room Height |  | m | 2.5 | 1.8
6 | HVAC Modules | HVAC Module 1 |  | - | Mixing Box | Heating Coil
7 |  | HVAC Module 2 |  | - | Cooling Coil | Cooling Coil
8 |  | HVAC Module 3 |  | - | Heating Coil
9 |  | HVAC Module 4 |  | -
10 |  | HVAC Module 5 |  | -
11 |  | HVAC Module 6 |  | -
12 |  | HVAC Module 7 |  | -
13 |  | HVAC Module 8 |  | -
14 |  | HVAC Module 9 |  | -
15 |  | HVAC Module 10 |  | -
16 | Air Flow | Supply Airflow |  | m³/s | 27.78 | 35
17 |  | Return Airflow |  | m³/s | 27.78 | 35
18 |  | Air Changes | Air Changes per Hour calculated |  | 13.3344 | 11.6667
19 | Mixing | Minimum Fresh Air Percentage |  |  | 30% | 30%
20 |  | Active Mixing | See Note 1 |  | No | No
21 | Heat Recovery | Heat Recovery Efficiency (S) | See Note 2 | Sensible | 70% | 70%
22 | Fan Power | Supply Fan Total Static Pressure | See Note 3 | Pascals | 1100 | 1100
23 |  | Supply Fan Efficiency | See Note 4 |  | 70% | 70%
24 |  | Return Fan Total Static Pressure | See Note 3 | Pascals | 900 | 900
25 |  | Return Fan Efficiency | See Note 4 |  | 70% | 70%
26 | Settings | Preheat Temperature Setpoint - Tdb | See Note 5 | °C dry bulb | 15 | 15
27 |  | Average Cooling Coil Temperature - Tdb | See Note 6 | °C dry bulb | 9 | 9
28 | 1 Setpoint summer (April - September) | Room Temperature Setpoint | The setpoint no. 1 values are applied to months April - September |  | 22 | 22
29 |  | Room Temperature Lower Band |  |  | 20 | 20
30 |  | Room Temperature Upper Band |  |  | 24 | 24
31 |  | Room Humidity Setpoint |  |  | 50% | 50%
32 |  | Room Humidity Lower Band |  |  | 30% | 30%
33 |  | Room Humidity Upper Band |  |  | 100% | 100%
34 | 2 Setpoint winter (October - March) | Room Temperature Setpoint | The setpoint no. 2 values are applied to months October - March |  | 22 | 22
35 |  | Room Temperature Lower Band |  |  | 20 | 20
36 |  | Room Temperature Upper Band |  |  | 24 | 24
37 |  | Room Humidity Setpoint |  |  | 50% | 50%
38 |  | Room Humidity Lower Band |  |  | 30% | 30%
39 |  | Room Humidity Upper Band |  |  | 100% | 100%
40 | 3 Setpoint Platzhalter | Room Temperature Setpoint | The setpoint no. 3 values are applied to months October - March |  | 22 | 22
41 |  | Room Temperature Lower Band |  |  | 20 | 20
42 |  | Room Temperature Upper Band |  |  | 24 | 24
43 |  | Room Humidity Setpoint |  |  | 50% | 50%
44 |  | Room Humidity Lower Band |  |  | 30% | 30%
45 |  | Room Humidity Upper Band |  |  | 100% | 100%
46 | Profile | Sensible gains (Heat) | Defines internal heat loads in the room (e.g., people, light, equipment) |  | High EPD (26 W/m²) | High EPD (26 W/m²)
47 | Profile | Latent gains (Steam) | Defines internal moisture loads in the room (e.g., peoples breath, steam equipment) |  | High SPD (15 W/m²) | High SPD (15 W/m²)
48 | Profile | Hours of operation / Part load operation | Defines when the AHU is operating (e.g., always on = every time 100% air flow rate) |  | Daytime on, Nighttime off, Sat&Sun off | Always on, Sat&Sun off
Notes
Note 1 | Active mixing is a function only applicable when a mixing box is specified, if active mixing is set to yes the mixing box will modulate between the minimum fresh air % and 100% fresh air
Note 2 | Where heat recovery is specified the efficiency of the heat recovery must be specified. Typical values are as follows, thermal wheel = 79%, plate heat exchanger = 79%, run arund coils = 69%
Note 3 | The fan total static pressure is the system total static pressure i.e. total static pressure = (the pressure drop in the AHU + pressure drop of the ductwork)
Note 4 | The fan efficiency is used with the pressure drop to estimate fan power. A typical fan efficiency would be 70%
Note 5 | Where a preheat coil is specified as a module in the system this is the temperature to which the preheat coil will preheat
Note 6 | Used to determine the Apparatus dew point, this will be the average coil temperature i.e. chilled water flow 6oC and chilled water return 6oC would result in an average coil temperature of 9°C
Note 7
Note 8
Note 9
Note 10
Possible Values
|  | HVAC Module | hours of operation |  | sensible gains | latent gains
|  | Blank | Always on |  | High EPD (26 W/m²) | High SPD (15 W/m²)
|  | Thermal Wheel | Always on, Sat&Sun off |  | Moderate EPD (15 W/m²) | Moderate SPD (10 W/m²)
|  | Mixing Box | Always on, Sat&Sun halfpower |  | Low EPD (4 W/m²) | Low SPD (5 W/m²)
|  | Run Around Coil | Daytime on, Nighttime off, Sat&Sun off
|  | Plate Heat Exchanger | Daytime on, Nighttime halfpower, Sat&Sun half power
|  | Preheating Coil | Daytime on, Nighttime halfpower, Sat&Sun off
Heating Coil
Cooling Coil
Humidifier (Steam)
Humidifier (Spray)

## Weather Data
Location |  | Cork Airport
Hour | Dry_Bulb_Temperature(°C) | Relative_Humidity(%)
1 | 8.5 | 0.81
2 | 8.5 | 0.81
3 | 8.4 | 0.83
4 | 8.5 | 0.75
5 | 8.5 | 0.75
6 | 8.2 | 0.78
7 | 8 | 0.78
8 | 7.9 | 0.76
9 | 8 | 0.74
10 | 7.9 | 0.78
11 | 8 | 0.75
12 | 8.2 | 0.77
13 | 8.4 | 0.75
14 | 8.4 | 0.77
15 | 8.5 | 0.75
16 | 8.3 | 0.78
17 | 8.3 | 0.78
18 | 8.1 | 0.81
19 | 8.1 | 0.79
20 | 8.1 | 0.78
21 | 8 | 0.8
22 | 7.8 | 0.82
23 | 7.6 | 0.87
24 | 7.3 | 0.93
25 | 7.5 | 0.97
26 | 7.3 | 0.97
27 | 7.3 | 0.97
28 | 7.2 | 0.97
29 | 7 | 0.97
30 | 7 | 0.99
31 | 7.2 | 0.99
32 | 7 | 1
33 | 6.9 | 0.99
34 | 7 | 1
35 | 7.3 | 1
36 | 7.2 | 0.99
37 | 7.2 | 1
38 | 7 | 0.99
39 | 6.7 | 0.97
40 | 6.6 | 0.97
41 | 6.9 | 0.88
42 | 6.4 | 0.91
43 | 6.8 | 0.87
44 | 6.9 | 0.88
45 | 6.9 | 0.91
46 | 6.6 | 0.94
47 | 6.8 | 0.93
48 | 6.6 | 0.95
49 | 6.3 | 0.98
50 | 6.5 | 0.98
51 | 6.4 | 0.97
52 | 6.7 | 0.97
53 | 7.4 | 0.99
54 | 7.2 | 0.97
55 | 7.2 | 0.99
56 | 7.2 | 0.97
57 | 7.2 | 0.97
58 | 7.4 | 0.93
59 | 7.3 | 0.88
60 | 7.4 | 0.84
61 | 7.4 | 0.8
62 | 7.4 | 0.79
63 | 7.1 | 0.75
64 | 6.6 | 0.76
65 | 6.6 | 0.79
66 | 6.7 | 0.79
67 | 6.8 | 0.77
68 | 6.7 | 0.78
69 | 6.6 | 0.76
70 | 6.4 | 0.75
71 | 6.5 | 0.76
72 | 6.5 | 0.76
73 | 6.4 | 0.75
74 | 6.5 | 0.78
75 | 6.4 | 0.78
76 | 6.4 | 0.78
77 | 6.3 | 0.75
78 | 6.4 | 0.76
79 | 6.2 | 0.8
80 | 6.4 | 0.76
81 | 6.6 | 0.72
82 | 6.3 | 0.82
83 | 6.4 | 0.85
84 | 6.9 | 0.77
85 | 7.3 | 0.77
86 | 7.4 | 0.73
87 | 7.4 | 0.8
88 | 7.2 | 0.8
89 | 6.7 | 0.76
90 | 6.4 | 0.76
91 | 6.2 | 0.8
92 | 6.2 | 0.8
93 | 6.1 | 0.79
94 | 6.3 | 0.8
95 | 6.3 | 0.79
96 | 6.3 | 0.79
97 | 6.3 | 0.8
98 | 6.2 | 0.82
99 | 6.4 | 0.81
100 | 6.4 | 0.81
101 | 6.4 | 0.82
102 | 6.5 | 0.84
103 | 6.6 | 0.76
104 | 6.9 | 0.82
105 | 6.9 | 0.81
106 | 7.1 | 0.81
107 | 7.4 | 0.8
108 | 7.7 | 0.79
109 | 7.9 | 0.82
110 | 8.1 | 0.81
111 | 8.3 | 0.83
112 | 8.2 | 0.86
113 | 8.2 | 0.87
114 | 8 | 0.89
115 | 8 | 0.89
116 | 8 | 0.9
117 | 8.1 | 0.92
118 | 8.1 | 0.93
119 | 8.1 | 0.93
120 | 8.2 | 0.92
121 | 8.1 | 0.92
122 | 8 | 0.92
123 | 8.1 | 0.86
124 | 8.3 | 0.83
125 | 8 | 0.86
126 | 8.1 | 0.86
127 | 8.2 | 0.86
128 | 8 | 0.87
129 | 7.9 | 0.9
130 | 7.1 | 0.91
131 | 7.8 | 0.93
132 | 9 | 0.89
133 | 9.5 | 0.89
134 | 9.7 | 0.89
135 | 9.9 | 0.88
136 | 9.7 | 0.91
137 | 9.6 | 0.91
138 | 9.1 | 0.91
139 | 8.9 | 0.93
140 | 8.9 | 0.9
141 | 8.7 | 0.9
142 | 8.3 | 0.92
143 | 8.6 | 0.93
144 | 8.9 | 0.93
145 | 9.1 | 0.99
146 | 9.3 | 0.99
147 | 9.4 | 1
148 | 9.6 | 1
149 | 9.8 | 1
150 | 9.5 | 0.97
151 | 9.8 | 0.97
152 | 9.9 | 0.95
153 | 9.9 | 0.92
154 | 9.9 | 0.87
155 | 10 | 0.87
156 | 10.1 | 0.86
157 | 10 | 0.82
158 | 10.1 | 0.81
159 | 10.2 | 0.82
160 | 10.1 | 0.84
161 | 10.4 | 0.85
162 | 10.3 | 0.86
163 | 10.2 | 0.88
164 | 10.5 | 0.9
165 | 10.5 | 0.91
166 | 10.5 | 0.92
167 | 10.9 | 0.9
168 | 10.9 | 0.9
169 | 10.1 | 0.93
170 | 9.4 | 0.95
171 | 8.8 | 0.92
172 | 8.1 | 0.89
173 | 7.9 | 0.91
174 | 8 | 0.9
175 | 7.9 | 0.9
176 | 7.8 | 0.9
177 | 7.8 | 0.89
178 | 7.9 | 0.87
179 | 7.8 | 0.87
180 | 8.2 | 0.86
181 | 8.2 | 0.86
182 | 8.6 | 0.84
183 | 8.9 | 0.82
184 | 8.8 | 0.78
185 | 8.8 | 0.8
186 | 8.1 | 0.83
187 | 7.6 | 0.87
188 | 7.3 | 0.9
189 | 7.6 | 0.91
190 | 7.5 | 0.93
191 | 7.6 | 0.91
192 | 7.7 | 0.91
193 | 7.8 | 0.97
194 | 7.8 | 0.99
195 | 7.9 | 0.99
196 | 8 | 0.99
197 | 7.9 | 1
198 | 7.8 | 1
199 | 7.9 | 0.99
200 | 8.6 | 1
201 | 9 | 0.99
202 | 9.2 | 0.97
203 | 9.3 | 0.97
204 | 9.3 | 0.99
205 | 9.4 | 0.99
206 | 9.7 | 0.99
207 | 10 | 1
208 | 10.2 | 0.99
209 | 9.5 | 0.99
210 | 9.6 | 0.99
211 | 9.1 | 1
212 | 8.4 | 0.99
213 | 8.5 | 1
214 | 8.4 | 1
215 | 8.2 | 1
216 | 8.1 | 1
217 | 8.3 | 1
218 | 8.3 | 1
219 | 8.5 | 1
220 | 8.8 | 1
221 | 8.8 | 1
222 | 9.1 | 1
223 | 8.9 | 1
224 | 8.7 | 1
225 | 8.7 | 0.99
226 | 8.9 | 0.99
227 | 9.1 | 0.99
228 | 9.2 | 0.99
229 | 9.8 | 0.97
230 | 10 | 0.92
231 | 9.9 | 0.96
232 | 10.5 | 0.91
233 | 10.6 | 0.9
234 | 10.2 | 0.91
235 | 9.7 | 0.92
236 | 9.3 | 0.96
237 | 9.1 | 0.96
238 | 8.9 | 0.97
239 | 8.9 | 0.97
240 | 8.9 | 0.99
241 | 8.9 | 0.96
242 | 8.8 | 0.97
243 | 8.6 | 0.97
244 | 8.6 | 0.97
245 | 8.5 | 0.99
246 | 8.6 | 0.96
247 | 8.6 | 0.97
248 | 8 | 0.97
249 | 8.2 | 0.97
250 | 8.4 | 0.96
251 | 8.7 | 0.94
252 | 9.2 | 0.92
253 | 9.2 | 0.91
254 | 10.2 | 0.83
255 | 9.8 | 0.87
256 | 9.6 | 0.85
257 | 9.6 | 0.85
258 | 9.3 | 0.88
259 | 8.7 | 0.92
260 | 8.4 | 0.93
261 | 8.3 | 0.92
262 | 8.3 | 0.92
263 | 7.8 | 0.97
264 | 8.3 | 0.92
265 | 8.1 | 0.94
266 | 7.8 | 0.94
267 | 7.9 | 0.94
268 | 8.4 | 0.94
269 | 8.2 | 0.97
270 | 8.6 | 0.97
271 | 9 | 0.96
272 | 8.6 | 0.93
273 | 8.1 | 0.87
274 | 7.9 | 0.84
275 | 8.3 | 0.86
276 | 9.1 | 0.84
277 | 9.1 | 0.88
278 | 9.5 | 0.87
279 | 9.6 | 0.85
280 | 9.7 | 0.87
281 | 9.5 | 0.88
282 | 9.2 | 0.92
283 | 9.2 | 0.91
284 | 8.7 | 0.92
285 | 8.7 | 0.92
286 | 8.7 | 0.93
287 | 8.8 | 0.92
288 | 8.6 | 0.92
289 | 8.6 | 0.85
290 | 8 | 0.86
291 | 8.1 | 0.86
292 | 7.8 | 0.89
293 | 8.4 | 0.85
294 | 8.6 | 0.84
295 | 8.4 | 0.86
296 | 8 | 0.87
297 | 8.8 | 0.84
298 | 8.2 | 0.86
299 | 8.2 | 0.86
300 | 9.1 | 0.84
301 | 9.8 | 0.84
302 | 10.6 | 0.85
303 | 10.4 | 0.87
304 | 10.6 | 0.87
305 | 10.6 | 0.82
306 | 9.8 | 0.87
307 | 9.6 | 0.84
308 | 9.4 | 0.79
309 | 9.1 | 0.76
310 | 8.1 | 0.76
311 | 8.1 | 0.72
312 | 7.9 | 0.75
313 | 7.7 | 0.71
314 | 7.8 | 0.72
315 | 7.8 | 0.71
316 | 7.7 | 0.75
317 | 7.4 | 0.79
318 | 7.3 | 0.8
319 | 7.5 | 0.74
320 | 7.3 | 0.76
321 | 6.3 | 0.79
322 | 4.6 | 0.87
323 | 6.6 | 0.82
324 | 7.7 | 0.77
325 | 8 | 0.76
326 | 8.3 | 0.74
327 | 8.5 | 0.71
328 | 8.4 | 0.74
329 | 8 | 0.79
330 | 7.6 | 0.84
331 | 6.6 | 0.88
332 | 7.3 | 0.9
333 | 7.3 | 0.93
334 | 7.5 | 0.99
335 | 7.6 | 1
336 | 7.3 | 1
337 | 6.1 | 0.98
338 | 5.1 | 0.98
339 | 6.5 | 1
340 | 7 | 1
341 | 7 | 1
342 | 6.9 | 1
343 | 6 | 0.98
344 | 6.2 | 1
345 | 7 | 1
346 | 7 | 1
347 | 7.3 | 1
348 | 7.8 | 0.99
349 | 8.5 | 0.97
350 | 9 | 0.93
351 | 8.9 | 0.92
352 | 8.9 | 0.95
353 | 8.5 | 0.96
354 | 8.2 | 0.93
355 | 7.9 | 0.94
356 | 7.9 | 0.94
357 | 8.3 | 0.96
358 | 8.4 | 0.99
359 | 8.2 | 0.97
360 | 8.2 | 0.97
361 | 7.3 | 0.99
362 | 7.8 | 0.97
363 | 8.1 | 0.97
364 | 5.3 | 0.97
365 | 4.8 | 0.95
366 | 4.7 | 0.97
367 | 4.9 | 0.94
368 | 4.5 | 0.97
369 | 4.5 | 0.93
370 | 2.9 | 0.96
371 | 3.9 | 0.97
372 | 5.7 | 0.88
373 | 6.7 | 0.81
374 | 7.5 | 0.77
375 | 7.2 | 0.77
376 | 7.2 | 0.73
377 | 5.7 | 0.88
378 | 4.8 | 0.86
379 | 4.4 | 0.87
380 | 3.8 | 0.85
381 | 3.5 | 0.83
382 | 3.3 | 0.85
383 | 3.3 | 0.88
384 | 4.2 | 0.85
385 | 4.2 | 0.85
386 | 5 | 0.81
387 | 5.5 | 0.83
388 | 4.9 | 0.81
389 | 3.8 | 0.82
390 | 3.7 | 0.8
391 | 2.7 | 0.84
392 | 1.8 | 0.85
393 | 1.8 | 0.83
394 | 1.2 | 0.85
395 | 2.1 | 0.75
396 | 2.7 | 0.75
397 | 3 | 0.76
398 | 4.2 | 0.71
399 | 4.8 | 0.65
400 | 3.9 | 0.73
401 | 3.2 | 0.78
402 | 2.5 | 0.8
403 | 2.4 | 0.77
404 | 2.7 | 0.77
405 | 3.4 | 0.73
406 | 3.8 | 0.77
407 | 4.4 | 0.8
408 | 4.9 | 0.84
409 | 5 | 0.9
410 | 5.2 | 0.98
411 | 6 | 0.98
412 | 6.7 | 0.98
413 | 7.3 | 0.99
414 | 6 | 0.98
415 | 4 | 0.97
416 | 3.6 | 0.97
417 | 2.8 | 1
418 | 2.9 | 0.98
419 | 4.9 | 0.97
420 | 6.6 | 0.94
421 | 7.5 | 0.91
422 | 7.5 | 0.88
423 | 7.4 | 0.88
424 | 6.8 | 0.93
425 | 7 | 0.91
426 | 6.8 | 0.96
427 | 6.6 | 0.94
428 | 6.2 | 0.95
429 | 6 | 0.95
430 | 5.7 | 0.95
431 | 5.5 | 0.95
432 | 4.9 | 0.95
433 | 4.5 | 0.97
434 | 4.5 | 0.97
435 | 4.8 | 0.98
436 | 4.7 | 0.97
437 | 4.6 | 0.97
438 | 4.9 | 0.95
439 | 4.7 | 0.95
440 | 4.6 | 0.97
441 | 4.4 | 0.97
442 | 4.1 | 0.98
443 | 4.6 | 0.95
444 | 6.1 | 0.91
445 | 7.1 | 0.88
446 | 7.8 | 0.87
447 | 7.4 | 0.88
448 | 7.9 | 0.87
449 | 8.1 | 0.85
450 | 7.6 | 0.9
451 | 7.1 | 0.97
452 | 6.8 | 0.94
453 | 6.6 | 0.94
454 | 6.3 | 0.94
455 | 6.4 | 0.95
456 | 6.3 | 0.97
457 | 6.3 | 0.95
458 | 6.5 | 0.94
459 | 6.6 | 0.98
460 | 6.5 | 0.94
461 | 6.4 | 0.95
462 | 6.7 | 0.97
463 | 6.8 | 0.99
464 | 6.4 | 0.95
465 | 6.1 | 0.94
466 | 6 | 0.86
467 | 5.9 | 0.83
468 | 6.6 | 0.76
469 | 6.6 | 0.78
470 | 6.7 | 0.75
471 | 7.1 | 0.73
472 | 6.8 | 0.72
473 | 6.4 | 0.72
474 | 5.3 | 0.77
475 | 4.9 | 0.75
476 | 4.8 | 0.76
477 | 3.7 | 0.8
478 | 2.8 | 0.84
479 | 2.5 | 0.87
480 | 2.4 | 0.87
481 | 2.1 | 0.89
482 | 2.1 | 0.87
483 | 1.4 | 0.91
484 | 1.3 | 0.89
485 | 2.1 | 0.84
486 | 2.6 | 0.81
487 | 1.6 | 0.85
488 | 0.5 | 0.88
489 | 0.6 | 0.9
490 | 1.2 | 0.94
491 | 3.2 | 0.88
492 | 4.9 | 0.87
493 | 5.3 | 0.91
494 | 6.1 | 0.92
495 | 6.5 | 0.88
496 | 6.3 | 0.92
497 | 6.4 | 0.95
498 | 5.3 | 0.89
499 | 3.9 | 0.9
500 | 3.7 | 0.83
501 | 3.4 | 0.76
502 | 2.9 | 0.81
503 | 1.9 | 0.91
504 | 1.5 | 0.94
505 | 2 | 0.93
506 | 1.1 | 0.92
507 | 0.8 | 0.92
508 | 0.2 | 0.88
509 | 1 | 0.9
510 | 1.3 | 0.91
511 | 2.1 | 0.91
512 | 1.5 | 0.94
513 | 1.6 | 0.94
514 | 1.2 | 0.96
515 | 1.8 | 0.96
516 | 2.9 | 0.91
517 | 3.7 | 0.92
518 | 3.7 | 0.92
519 | 4.2 | 0.92
520 | 3.9 | 0.92
521 | 3.9 | 0.9
522 | 3.8 | 0.93
523 | 4.1 | 0.93
524 | 4 | 0.95
525 | 3.9 | 0.93
526 | 4.1 | 0.92
527 | 3.7 | 0.9
528 | 4.3 | 0.87
529 | 3.6 | 0.9
530 | 4.3 | 0.87
531 | 4.4 | 0.87
532 | 4.1 | 0.9
533 | 4 | 0.87
534 | 3.8 | 0.88
535 | 4.1 | 0.87
536 | 4.1 | 0.83
537 | 4.1 | 0.85
538 | 4.6 | 0.85
539 | 5.1 | 0.86
540 | 5.6 | 0.84
541 | 6.1 | 0.86
542 | 6.3 | 0.92
543 | 6.1 | 0.95
544 | 6 | 0.98
545 | 6.6 | 0.98
546 | 6.4 | 0.98
547 | 6.3 | 0.98
548 | 6.3 | 0.98
549 | 6.4 | 1
550 | 6.8 | 0.99
551 | 6.7 | 1
552 | 6.7 | 1
553 | 8.7 | 1
554 | 8.9 | 0.97
555 | 9.1 | 0.97
556 | 9.3 | 0.95
557 | 9.1 | 0.97
558 | 9.1 | 0.95
559 | 8.9 | 0.99
560 | 9.1 | 0.97
561 | 9.3 | 0.97
562 | 9.5 | 0.99
563 | 9.7 | 0.83
564 | 9.7 | 0.89
565 | 10.3 | 0.91
566 | 10.1 | 0.93
567 | 10.4 | 0.91
568 | 10.6 | 0.87
569 | 10.2 | 0.87
570 | 9.8 | 0.93
571 | 9.9 | 0.93
572 | 10 | 0.92
573 | 9.8 | 0.92
574 | 9.7 | 0.91
575 | 9.8 | 0.89
576 | 9.7 | 0.88
577 | 9.6 | 0.91
578 | 9.7 | 0.91
579 | 9.4 | 0.92
580 | 9.5 | 0.91
581 | 9.5 | 0.89
582 | 9.2 | 0.92
583 | 8.5 | 0.93
584 | 9.1 | 0.89
585 | 8.8 | 0.93
586 | 8.5 | 0.97
587 | 8.6 | 0.97
588 | 9.2 | 0.91
589 | 9.5 | 0.88
590 | 10.2 | 0.82
591 | 10.5 | 0.8
592 | 10.4 | 0.78
593 | 9.6 | 0.83
594 | 8.7 | 0.89
595 | 7.7 | 0.94
596 | 7.1 | 0.93
597 | 7.3 | 0.9
598 | 5.5 | 0.95
599 | 6.6 | 0.95
600 | 6.3 | 0.98
601 | 7.1 | 0.99
602 | 7.7 | 1
603 | 8.1 | 1
604 | 8 | 0.99
605 | 7.8 | 0.97
606 | 7.7 | 0.97
607 | 7.9 | 0.97
608 | 8.2 | 0.96
609 | 8.5 | 0.97
610 | 8.9 | 0.97
611 | 9.5 | 0.96
612 | 8.6 | 0.97
613 | 8.5 | 0.86
614 | 8.2 | 0.82
615 | 7.8 | 0.91
616 | 8.3 | 0.89
617 | 8.4 | 0.81
618 | 7.7 | 0.87
619 | 7.5 | 0.9
620 | 7.5 | 0.87
621 | 7.7 | 0.86
622 | 7.4 | 0.86
623 | 6.2 | 0.79
624 | 5.4 | 0.78
625 | 4 | 0.87
626 | 4 | 0.72
627 | 3.9 | 0.67
628 | 3.6 | 0.7
629 | 3.4 | 0.71
630 | 3.2 | 0.71
631 | 3.2 | 0.73
632 | 3.5 | 0.68
633 | 3.2 | 0.73
634 | 3.5 | 0.75
635 | 3.8 | 0.78
636 | 4.8 | 0.74
637 | 5.9 | 0.71
638 | 6.2 | 0.67
639 | 5.5 | 0.77
640 | 5.3 | 0.8
641 | 4.8 | 0.81
642 | 4.2 | 0.87
643 | 3.8 | 0.9
644 | 3.3 | 0.97
645 | 3.1 | 0.96
646 | 3.1 | 0.96
647 | 3.1 | 0.98
648 | 3.1 | 0.98
649 | 3.2 | 1
650 | 3.9 | 0.97
651 | 5.2 | 0.95
652 | 5.4 | 0.87
653 | 5.2 | 0.83
654 | 4.9 | 0.86
655 | 4.9 | 0.84
656 | 5.2 | 0.86
657 | 5.6 | 0.81
658 | 6 | 0.82
659 | 5.8 | 0.89
660 | 5.3 | 0.83
661 | 5.2 | 0.83
662 | 5.6 | 0.77
663 | 5.8 | 0.76
664 | 5.7 | 0.85
665 | 5.7 | 0.83
666 | 4.3 | 0.87
667 | 2.6 | 0.93
668 | 3 | 0.88
669 | 2.9 | 0.88
670 | 3 | 0.88
671 | 3.8 | 0.85
672 | 4 | 0.85
673 | 3.4 | 0.91
674 | 3.7 | 0.9
675 | 3.3 | 0.97
676 | 3.2 | 0.97
677 | 3.1 | 0.96
678 | 3.1 | 0.98
679 | 2.8 | 0.98
680 | 2.5 | 0.96
681 | 2.6 | 0.93
682 | 2.1 | 0.93
683 | 2.2 | 0.93
684 | 2.8 | 0.84
685 | 1.1 | 0.94
686 | 3.1 | 0.79
687 | 1.3 | 0.92
688 | 2.4 | 0.82
689 | 2.3 | 0.78
690 | 0 | 0.98
691 | 0.2 | 0.96
692 | 0.1 | 0.96
693 | 0.1 | 0.98
694 | -0.1 | 0.98
695 | -0.7 | 0.98
696 | 0 | 0.98
697 | -1.8 | 0.98
698 | -1.1 | 0.96
699 | -0.8 | 0.96
700 | -0.5 | 0.98
701 | -1.1 | 0.96
702 | -0.5 | 0.96
703 | -0.2 | 0.96
704 | -0.5 | 0.96
705 | -0.2 | 0.96
706 | 0.3 | 0.92
707 | 0.5 | 0.9
708 | 1.4 | 0.89
709 | 1.5 | 0.87
710 | 2.2 | 0.87
711 | 2.6 | 0.82
712 | 3.4 | 0.8
713 | 3.1 | 0.84
714 | 2.7 | 0.81
715 | 1 | 0.88
716 | 0 | 0.92
717 | -0.1 | 0.94
718 | -0.1 | 0.94
719 | -0.3 | 0.92
720 | 0.5 | 0.92
721 | 1.5 | 0.89
722 | 1.4 | 0.89
723 | 2.3 | 0.87
724 | 2.5 | 0.87
725 | 3.2 | 0.86
726 | 3.5 | 0.88
727 | 3.8 | 0.9
728 | 3.9 | 0.9
729 | 4 | 0.93
730 | 3.8 | 0.97
731 | 3.8 | 0.95
732 | 3.6 | 0.97
733 | 4.7 | 0.92
734 | 5.9 | 0.86
735 | 4.6 | 0.9
736 | 6 | 0.7
737 | 5.2 | 0.7
738 | 3.6 | 0.75
739 | 2.7 | 0.82
740 | 2.5 | 0.95
741 | 2.7 | 0.96
742 | 3.1 | 0.96
743 | 2.8 | 0.96
744 | 2.6 | 0.98
745 | 4.1 | 0.92
746 | 0.5 | 0.98
747 | 1.2 | 0.96
748 | 1.1 | 0.94
749 | 0.9 | 0.9
750 | 0.9 | 0.9
751 | 0.8 | 0.9
752 | 0.7 | 0.82
753 | 0.3 | 0.86
754 | 0.5 | 0.82
755 | 1.3 | 0.79
756 | 1.8 | 0.74
757 | 1.9 | 0.76
758 | 2.2 | 0.78
759 | 3.2 | 0.73
760 | 3.5 | 0.66
761 | 2.8 | 0.7
762 | 2 | 0.73
763 | 1.2 | 0.75
764 | 1 | 0.77
765 | 0.8 | 0.79
766 | 0.8 | 0.79
767 | 0.5 | 0.8
768 | 0.8 | 0.79
769 | 1 | 0.75
770 | -0.1 | 0.82
771 | -0.1 | 0.84
772 | -0.4 | 0.86
773 | -0.1 | 0.84
774 | -0.2 | 0.84
775 | -0.1 | 0.82
776 | -0.4 | 0.84
777 | 0.2 | 0.78
778 | 0.3 | 0.76
779 | 1.4 | 0.74
780 | 3.2 | 0.73
781 | 4.3 | 0.71
782 | 5.1 | 0.7
783 | 5.7 | 0.68
784 | 4.6 | 0.74
785 | 4.5 | 0.74
786 | 4 | 0.78
787 | 2.2 | 0.87
788 | 2.4 | 0.84
789 | 2 | 0.84
790 | 2.3 | 0.84
791 | 2.1 | 0.82
792 | 2.3 | 0.82
793 | 1.7 | 0.85
794 | 1.6 | 0.87
795 | 1.3 | 0.91
796 | 1.5 | 0.92
797 | 1.9 | 0.93
798 | 2.1 | 0.95
799 | 3.1 | 0.93
800 | 2.8 | 0.96
801 | 3.3 | 0.95
802 | 4.1 | 0.93
803 | 5.6 | 0.88
804 | 7.7 | 0.84
805 | 8.7 | 0.77
806 | 8.5 | 0.78
807 | 8.4 | 0.78
808 | 8.3 | 0.82
809 | 8.1 | 0.86
810 | 8.1 | 0.86
811 | 7.9 | 0.89
812 | 7.7 | 0.96
813 | 7.8 | 0.99
814 | 7.6 | 0.99
815 | 8.1 | 0.99
816 | 8.9 | 1
817 | 9.3 | 1
818 | 9 | 1
819 | 8.7 | 1
820 | 8.6 | 0.94
821 | 8 | 0.87
822 | 7.4 | 0.9
823 | 7.2 | 0.87
824 | 6.7 | 0.87
825 | 6.1 | 0.88
826 | 5.8 | 0.88
827 | 7.5 | 0.79
828 | 8.3 | 0.79
829 | 8.9 | 0.77
830 | 9.4 | 0.7
831 | 10.2 | 0.66
832 | 10.1 | 0.63
833 | 9.8 | 0.68
834 | 6.2 | 0.89
835 | 5.6 | 0.92
836 | 4.8 | 0.95
837 | 4.6 | 0.97
838 | 3.6 | 0.97
839 | 3.7 | 0.97
840 | 6.2 | 0.95
841 | 6.7 | 0.93
842 | 6.9 | 0.93
843 | 7.1 | 0.97
844 | 7.3 | 0.99
845 | 7.4 | 1
846 | 7.7 | 1
847 | 8.5 | 1
848 | 9.4 | 0.99
849 | 9.7 | 1
850 | 10 | 1
851 | 10.4 | 1
852 | 10.4 | 1
853 | 10.6 | 1
854 | 10.6 | 1
855 | 10.8 | 0.99
856 | 10.8 | 0.99
857 | 9.2 | 0.95
858 | 9.4 | 0.92
859 | 7.9 | 0.89
860 | 6.1 | 0.91
861 | 5.4 | 0.87
862 | 3.2 | 0.93
863 | 2.7 | 0.93
864 | 3 | 0.91
865 | 2.7 | 0.91
866 | 2.5 | 0.95
867 | 3.3 | 0.91
868 | 3.3 | 0.93
869 | 4.8 | 0.92
870 | 5.3 | 0.92
871 | 6.6 | 0.91
872 | 6.1 | 0.89
873 | 6.7 | 0.9
874 | 6.6 | 0.91
875 | 7.4 | 0.9
876 | 8.8 | 0.85
877 | 9.1 | 0.8
878 | 9.5 | 0.78
879 | 9 | 0.88
880 | 9 | 0.86
881 | 8.1 | 0.87
882 | 7.9 | 0.93
883 | 7.6 | 0.91
884 | 7.2 | 0.94
885 | 6.7 | 0.94
886 | 5.4 | 0.95
887 | 2.3 | 0.91
888 | 3.2 | 0.9
889 | 3 | 0.89
890 | 3.5 | 0.86
891 | 3.7 | 0.88
892 | 2.6 | 0.96
893 | 3.9 | 0.85
894 | 2.7 | 0.91
895 | 4.1 | 0.85
896 | 3.6 | 0.88
897 | 3.6 | 0.88
898 | 3.7 | 0.88
899 | 4.7 | 0.85
900 | 6.1 | 0.82
901 | 6.6 | 0.82
902 | 6.9 | 0.82
903 | 7 | 0.8
904 | 6.6 | 0.87
905 | 6.7 | 0.91
906 | 7.3 | 0.88
907 | 7 | 0.96
908 | 7.3 | 0.99
909 | 8 | 0.99
910 | 8.4 | 0.94
911 | 8.5 | 0.96
912 | 8.5 | 0.97
913 | 8.8 | 0.97
914 | 8.9 | 0.95
915 | 9.1 | 0.97
916 | 9.3 | 0.97
917 | 9.6 | 0.99
918 | 9.7 | 0.99
919 | 9.8 | 0.96
920 | 8.9 | 0.9
921 | 7.8 | 0.8
922 | 7.3 | 0.83
923 | 7.2 | 0.85
924 | 8.5 | 0.78
925 | 8 | 0.76
926 | 8.7 | 0.74
927 | 8.8 | 0.74
928 | 7.6 | 0.77
929 | 6.2 | 0.83
930 | 5.9 | 0.79
931 | 6.1 | 0.77
932 | 5.7 | 0.75
933 | 5.1 | 0.78
934 | 4.7 | 0.76
935 | 5.2 | 0.66
936 | 4.8 | 0.65
937 | 3.9 | 0.83
938 | 4.8 | 0.73
939 | 5.3 | 0.64
940 | 5.1 | 0.72
941 | 5.4 | 0.63
942 | 4.9 | 0.72
943 | 5.4 | 0.63
944 | 5 | 0.76
945 | 5 | 0.73
946 | 5.7 | 0.74
947 | 5.8 | 0.73
948 | 7.6 | 0.72
949 | 7.5 | 0.77
950 | 7.9 | 0.75
951 | 7.2 | 0.77
952 | 7.4 | 0.81
953 | 6.4 | 0.81
954 | 5.2 | 0.83
955 | 2.8 | 0.91
956 | 2.7 | 0.95
957 | 2.8 | 0.96
958 | 4.4 | 0.87
959 | 3.8 | 0.9
960 | 3.4 | 0.91
961 | 2.6 | 0.91
962 | 2.8 | 0.95
963 | 2.9 | 0.93
964 | 2.4 | 0.91
965 | 2.8 | 0.91
966 | 3 | 0.88
967 | 2.9 | 0.88
968 | 2.5 | 0.87
969 | 2.8 | 0.86
970 | 3 | 0.84
971 | 3.9 | 0.8
972 | 3.1 | 0.88
973 | 4.1 | 0.87
974 | 5.8 | 0.8
975 | 6.6 | 0.69
976 | 6.2 | 0.64
977 | 5.9 | 0.71
978 | 6 | 0.64
979 | 5.5 | 0.66
980 | 4.8 | 0.68
981 | 5.4 | 0.68
982 | 5.9 | 0.67
983 | 6.2 | 0.69
984 | 6.5 | 0.75
985 | 6.4 | 0.81
986 | 6.2 | 0.83
987 | 6 | 0.86
988 | 6.1 | 0.86
989 | 5.9 | 0.88
990 | 5.6 | 0.86
991 | 5.8 | 0.83
992 | 4.5 | 0.87
993 | 5.1 | 0.84
994 | 5.2 | 0.83
995 | 6.2 | 0.79
996 | 6.9 | 0.8
997 | 8 | 0.76
998 | 8.9 | 0.77
999 | 9.3 | 0.79
1000 | 9.3 | 0.83
1001 | 8.9 | 0.86
1002 | 8.4 | 0.9
1003 | 7.8 | 0.94
1004 | 7.2 | 0.96
1005 | 7.1 | 0.97
1006 | 7.5 | 0.97
1007 | 8.1 | 0.96
1008 | 8.4 | 0.96
1009 | 8.6 | 0.96
1010 | 8.7 | 0.93
1011 | 8 | 0.97
1012 | 8.2 | 0.97
1013 | 8.2 | 0.99
1014 | 8.4 | 0.99
1015 | 8.7 | 0.99
1016 | 8.9 | 1
1017 | 9.1 | 1
1018 | 9.2 | 1
1019 | 9.6 | 0.99
1020 | 9.5 | 0.97
1021 | 9.8 | 0.99
1022 | 9.9 | 0.99
1023 | 9.9 | 0.99
1024 | 10 | 1
1025 | 9.8 | 0.99
1026 | 9.6 | 1
1027 | 9.4 | 0.99
1028 | 9.3 | 0.99
1029 | 9.1 | 0.99
1030 | 9 | 0.99
1031 | 8.9 | 0.99
1032 | 8.9 | 0.97
1033 | 8.8 | 0.95
1034 | 8.8 | 0.95
1035 | 8.7 | 0.93
1036 | 8.5 | 0.93
1037 | 8.5 | 0.93
1038 | 8.6 | 0.96
1039 | 8.6 | 0.93
1040 | 8.6 | 0.93
1041 | 8.6 | 0.92
1042 | 8.8 | 0.93
1043 | 9.1 | 0.91
1044 | 9.2 | 0.89
1045 | 9.4 | 0.89
1046 | 9.5 | 0.88
1047 | 9.5 | 0.88
1048 | 9.3 | 0.91
1049 | 9.3 | 0.89
1050 | 9 | 0.89
1051 | 8.6 | 0.92
1052 | 8.8 | 0.9
1053 | 8.7 | 0.9
1054 | 8.5 | 0.93
1055 | 8.8 | 0.9
1056 | 8.7 | 0.9
1057 | 8.6 | 0.92
1058 | 8.9 | 0.89
1059 | 8.9 | 0.89
1060 | 8.8 | 0.88
1061 | 8.9 | 0.89
1062 | 8.8 | 0.86
1063 | 8.6 | 0.89
1064 | 8.5 | 0.9
1065 | 8.3 | 0.92
1066 | 8.3 | 0.9
1067 | 8.5 | 0.88
1068 | 8.5 | 0.9
1069 | 8.5 | 0.89
1070 | 8.5 | 0.9
1071 | 8.6 | 0.92
1072 | 8.6 | 0.9
1073 | 8.5 | 0.92
1074 | 8.1 | 0.93
1075 | 7.9 | 0.93
1076 | 7.7 | 0.94
1077 | 7.7 | 0.93
1078 | 7.5 | 0.91
1079 | 7.4 | 0.93
1080 | 7.4 | 0.93
1081 | 7.5 | 0.96
1082 | 7.8 | 0.96
1083 | 8.1 | 0.97
1084 | 8.2 | 0.96
1085 | 8.2 | 0.99
1086 | 7.7 | 0.97
1087 | 7.9 | 0.99
1088 | 7.6 | 0.99
1089 | 7.6 | 0.97
1090 | 9.2 | 0.93
1091 | 9.7 | 0.91
1092 | 10 | 0.88
1093 | 10.7 | 0.89
1094 | 10.5 | 0.9
1095 | 10.3 | 0.95
1096 | 10.3 | 0.99
1097 | 10.5 | 1
1098 | 10.4 | 0.99
1099 | 9.6 | 0.92
1100 | 9.3 | 0.91
1101 | 9.1 | 0.93
1102 | 9 | 0.93
1103 | 8.8 | 0.93
1104 | 8.1 | 0.92
1105 | 7.8 | 0.93
1106 | 7.3 | 0.96
1107 | 6.7 | 0.94
1108 | 6.3 | 0.92
1109 | 6 | 0.92
1110 | 6.9 | 0.94
1111 | 7 | 0.99
1112 | 7 | 0.94
1113 | 7.2 | 0.87
1114 | 8.2 | 0.92
1115 | 8.6 | 0.92
1116 | 9.4 | 0.89
1117 | 9.8 | 0.89
1118 | 9.9 | 0.91
1119 | 10.1 | 0.92
1120 | 9.9 | 0.95
1121 | 10 | 0.95
1122 | 10.1 | 0.96
1123 | 9.8 | 0.99
1124 | 9.7 | 0.99
1125 | 9.7 | 0.99
1126 | 9.9 | 0.97
1127 | 9.9 | 0.97
1128 | 9.7 | 0.97
1129 | 9.8 | 0.96
1130 | 9.6 | 0.99
1131 | 8.6 | 0.99
1132 | 8.4 | 0.97
1133 | 8.3 | 0.99
1134 | 8.5 | 0.97
1135 | 8.6 | 0.96
1136 | 7.1 | 0.9
1137 | 6.6 | 0.84
1138 | 7.4 | 0.86
1139 | 8.6 | 0.8
1140 | 9.2 | 0.75
1141 | 9.2 | 0.8
1142 | 8.9 | 0.84
1143 | 8.6 | 0.93
1144 | 9.8 | 0.86
1145 | 8.5 | 0.86
1146 | 8.5 | 0.84
1147 | 7.6 | 0.86
1148 | 7.8 | 0.86
1149 | 6.8 | 0.88
1150 | 7 | 0.87
1151 | 7.3 | 0.88
1152 | 6.2 | 0.88
1153 | 5.6 | 0.94
1154 | 4.6 | 0.97
1155 | 3.6 | 0.95
1156 | 3.2 | 0.95
1157 | 2.8 | 0.95
1158 | 2.8 | 0.91
1159 | 3.2 | 0.9
1160 | 4.4 | 0.87
1161 | 4.9 | 0.89
1162 | 5 | 0.89
1163 | 6.9 | 0.85
1164 | 7.5 | 0.81
1165 | 8.3 | 0.78
1166 | 8.5 | 0.73
1167 | 9.4 | 0.67
1168 | 9.1 | 0.7
1169 | 8.7 | 0.7
1170 | 7.9 | 0.72
1171 | 6.7 | 0.79
1172 | 5.1 | 0.84
1173 | 4.5 | 0.84
1174 | 3.1 | 0.91
1175 | 2.2 | 0.93
1176 | 2.2 | 0.91
1177 | 2.6 | 0.91
1178 | 1.6 | 0.93
1179 | 3 | 0.91
1180 | 2.9 | 0.98
1181 | 3.2 | 0.95
1182 | 5 | 0.94
1183 | 5.7 | 0.86
1184 | 6.1 | 0.91
1185 | 6.9 | 0.88
1186 | 7.5 | 0.9
1187 | 8 | 0.86
1188 | 8.2 | 0.86
1189 | 7.8 | 0.93
1190 | 7.7 | 0.99
1191 | 7.9 | 0.99
1192 | 8.1 | 0.99
1193 | 8.4 | 0.99
1194 | 8.4 | 0.99
1195 | 8.6 | 0.99
1196 | 8.9 | 0.99
1197 | 9 | 0.99
1198 | 9.1 | 0.99
1199 | 9.2 | 0.97
1200 | 9.1 | 0.99
1201 | 9.2 | 0.97
1202 | 9.2 | 0.97
1203 | 9.2 | 0.96
1204 | 9.3 | 0.96
1205 | 9.3 | 0.97
1206 | 9.2 | 1
1207 | 9.3 | 0.99
1208 | 9.4 | 0.99
1209 | 9.5 | 1
1210 | 9.8 | 0.99
1211 | 10 | 0.99
1212 | 10.3 | 1
1213 | 10.5 | 0.99
1214 | 10.5 | 1
1215 | 10.7 | 0.99
1216 | 10.3 | 1
1217 | 10.2 | 1
1218 | 10.2 | 1
1219 | 10.2 | 1
1220 | 10.2 | 1
1221 | 10.3 | 1
1222 | 10.3 | 1
1223 | 10.4 | 1
1224 | 10.4 | 1
1225 | 10.4 | 1
1226 | 10.3 | 1
1227 | 10.1 | 1
1228 | 9.9 | 0.99
1229 | 9.8 | 1
1230 | 9.9 | 0.97
1231 | 9.9 | 0.97
1232 | 9.9 | 0.95
1233 | 9.9 | 0.93
1234 | 9.9 | 0.93
1235 | 10.5 | 0.91
1236 | 10.6 | 0.9
1237 | 10.8 | 0.89
1238 | 10.4 | 0.9
1239 | 10 | 0.92
1240 | 9.8 | 0.92
1241 | 9.7 | 0.95
1242 | 9.6 | 0.96
1243 | 9.6 | 0.96
1244 | 9.4 | 0.96
1245 | 9.5 | 0.95
1246 | 9.9 | 0.91
1247 | 10.4 | 0.86
1248 | 10.6 | 0.85
1249 | 10.8 | 0.85
1250 | 10.7 | 0.85
1251 | 10.2 | 0.92
1252 | 9.8 | 0.97
1253 | 10.1 | 0.96
1254 | 10.1 | 0.97
1255 | 10 | 0.97
1256 | 10 | 0.96
1257 | 9.9 | 0.96
1258 | 10.1 | 0.96
1259 | 10.1 | 0.96
1260 | 10.1 | 0.97
1261 | 10.3 | 0.97
1262 | 10.7 | 0.95
1263 | 10.9 | 0.94
1264 | 11.1 | 0.91
1265 | 10.5 | 0.92
1266 | 10.3 | 0.91
1267 | 9.7 | 0.92
1268 | 9.7 | 0.89
1269 | 9.6 | 0.89
1270 | 9.6 | 0.88
1271 | 9.6 | 0.87
1272 | 9.7 | 0.87
1273 | 9.7 | 0.87
1274 | 9.8 | 0.86
1275 | 10.1 | 0.84
1276 | 10.2 | 0.85
1277 | 10.2 | 0.85
1278 | 10.4 | 0.86
1279 | 9.6 | 0.97
1280 | 9.8 | 0.99
1281 | 9.9 | 0.99
1282 | 10.3 | 1
1283 | 10.6 | 0.99
1284 | 11.1 | 0.94
1285 | 11.3 | 0.91
1286 | 11.4 | 0.89
1287 | 12.2 | 0.86
1288 | 13.1 | 0.74
1289 | 13.1 | 0.69
1290 | 11.4 | 0.8
1291 | 8.3 | 0.92
1292 | 7.2 | 0.96
1293 | 7.5 | 0.99
1294 | 7 | 1
1295 | 6.2 | 1
1296 | 7 | 1
1297 | 8.3 | 1
1298 | 8.4 | 1
1299 | 8.4 | 1
1300 | 8.3 | 1
1301 | 8.4 | 1
1302 | 7.6 | 1
1303 | 8.8 | 1
1304 | 9 | 1
1305 | 9.1 | 0.99
1306 | 9.3 | 1
1307 | 9.3 | 1
1308 | 9.2 | 1
1309 | 9.2 | 1
1310 | 9.1 | 1
1311 | 9.1 | 1
1312 | 9.1 | 1
1313 | 8.9 | 1
1314 | 8.6 | 1
1315 | 8.4 | 1
1316 | 8.3 | 0.99
1317 | 8.4 | 1
1318 | 8.1 | 1
1319 | 8.1 | 1
1320 | 8.1 | 0.99
1321 | 8.2 | 1
1322 | 8.4 | 1
1323 | 8.4 | 1
1324 | 8.8 | 1
1325 | 8.6 | 1
1326 | 8.7 | 1
1327 | 8.6 | 1
1328 | 8.4 | 1
1329 | 8.2 | 1
1330 | 8.6 | 1
1331 | 9.4 | 0.99
1332 | 10.5 | 0.88
1333 | 10.7 | 0.86
1334 | 11.2 | 0.84
1335 | 11 | 0.85
1336 | 10.5 | 0.85
1337 | 10 | 0.86
1338 | 9.6 | 0.87
1339 | 8.2 | 0.96
1340 | 7.8 | 0.97
1341 | 8.2 | 0.99
1342 | 8.1 | 0.99
1343 | 8.3 | 0.99
1344 | 8.2 | 0.99
1345 | 7.7 | 1
1346 | 7.6 | 1
1347 | 7.8 | 1
1348 | 7.1 | 1
1349 | 7.8 | 1
1350 | 7.9 | 1
1351 | 7.8 | 1
1352 | 7.9 | 1
1353 | 7.2 | 1
1354 | 7.6 | 1
1355 | 8 | 0.99
1356 | 8.8 | 0.96
1357 | 11.1 | 0.77
1358 | 11.5 | 0.7
1359 | 12.2 | 0.62
1360 | 10.8 | 0.73
1361 | 10.1 | 0.81
1362 | 9.1 | 0.88
1363 | 7.9 | 0.96
1364 | 7.8 | 0.99
1365 | 7.6 | 0.99
1366 | 7.6 | 1
1367 | 7.6 | 1
1368 | 6.9 | 1
1369 | 7.8 | 0.99
1370 | 8.2 | 1
1371 | 7.8 | 0.96
1372 | 7.9 | 0.96
1373 | 7.9 | 0.97
1374 | 7.7 | 0.93
1375 | 7.7 | 0.93
1376 | 7.6 | 0.94
1377 | 7.6 | 0.93
1378 | 7.9 | 0.93
1379 | 8 | 0.92
1380 | 8.6 | 0.92
1381 | 8.8 | 0.9
1382 | 8.9 | 0.9
1383 | 8.8 | 0.9
1384 | 8.5 | 0.9
1385 | 8.1 | 0.93
1386 | 7.5 | 0.94
1387 | 7.2 | 0.96
1388 | 6.8 | 0.96
1389 | 6.7 | 0.97
1390 | 6.8 | 0.97
1391 | 6.9 | 1
1392 | 7.1 | 0.99
1393 | 7.4 | 1
1394 | 7.7 | 1
1395 | 8.2 | 1
1396 | 8.9 | 1
1397 | 8.8 | 1
1398 | 8.6 | 1
1399 | 8.6 | 0.99
1400 | 8.2 | 0.97
1401 | 7.6 | 0.96
1402 | 8.3 | 0.96
1403 | 9.9 | 0.87
1404 | 10.8 | 0.82
1405 | 11.9 | 0.78
1406 | 11.7 | 0.83
1407 | 12.1 | 0.79
1408 | 11.6 | 0.81
1409 | 11.4 | 0.85
1410 | 10.4 | 0.78
1411 | 9.6 | 0.85
1412 | 9.9 | 0.84
1413 | 9.2 | 0.85
1414 | 8.7 | 0.89
1415 | 8.1 | 0.89
1416 | 6.6 | 0.94
1417 | 5.3 | 0.95
1418 | 4.4 | 0.95
1419 | 3.9 | 0.97
1420 | 4.3 | 0.98
1421 | 5.4 | 0.97
1422 | 5.8 | 0.97
1423 | 7.1 | 1
1424 | 7.8 | 1
1425 | 7 | 1
1426 | 8.2 | 0.99
1427 | 8.7 | 0.99
1428 | 9 | 1
1429 | 9.1 | 1
1430 | 9.6 | 1
1431 | 9.6 | 1
1432 | 9.9 | 0.99
1433 | 9.9 | 0.99
1434 | 9.4 | 1
1435 | 8.9 | 1
1436 | 8.9 | 0.99
1437 | 9.4 | 1
1438 | 8.9 | 1
1439 | 8.6 | 0.99
1440 | 7.7 | 0.99
1441 | 6.9 | 0.97
1442 | 6.6 | 0.94
1443 | 4.6 | 0.97
1444 | 4 | 0.98
1445 | 5 | 0.98
1446 | 5.4 | 1
1447 | 6.5 | 0.97
1448 | 7.9 | 0.97
1449 | 8.4 | 0.99
1450 | 9.1 | 0.99
1451 | 9.8 | 0.96
1452 | 10.1 | 0.95
1453 | 10.1 | 0.99
1454 | 10.5 | 0.99
1455 | 9.5 | 0.93
1456 | 9.2 | 0.85
1457 | 9.2 | 0.76
1458 | 8.7 | 0.69
1459 | 7.4 | 0.73
1460 | 6.4 | 0.76
1461 | 6.2 | 0.8
1462 | 5.9 | 0.8
1463 | 5.7 | 0.8
1464 | 5.8 | 0.85
1465 | 5.8 | 0.83
1466 | 5.7 | 0.78
1467 | 5.8 | 0.79
1468 | 5.4 | 0.81
1469 | 4.9 | 0.86
1470 | 4.9 | 0.89
1471 | 5.3 | 0.86
1472 | 5.1 | 0.9
1473 | 4.8 | 0.94
1474 | 5.2 | 0.98
1475 | 4.9 | 0.98
1476 | 5.4 | 0.98
1477 | 6.5 | 1
1478 | 7 | 0.99
1479 | 3.5 | 0.98
1480 | 2.2 | 0.96
1481 | 1.9 | 0.94
1482 | 1.8 | 0.96
1483 | 2 | 0.94
1484 | 1.1 | 0.94
1485 | 1.6 | 0.93
1486 | 1.4 | 0.94
1487 | 0.6 | 0.92
1488 | -0.1 | 0.96
1489 | 1.9 | 0.89
1490 | 1.6 | 0.91
1491 | 2 | 0.89
1492 | 2 | 0.91
1493 | 2.1 | 0.95
1494 | 3.3 | 0.93
1495 | 2.3 | 0.93
1496 | 2.5 | 0.93
1497 | 4.1 | 0.88
1498 | 4.5 | 0.84
1499 | 5.7 | 0.75
1500 | 5.6 | 0.75
1501 | 6.6 | 0.66
1502 | 7 | 0.61
1503 | 5.1 | 0.78
1504 | 5.9 | 0.76
1505 | 5.2 | 0.81
1506 | 5.6 | 0.78
1507 | 3.8 | 0.82
1508 | 3.5 | 0.88
1509 | 2.2 | 0.89
1510 | 3 | 0.88
1511 | 2.9 | 0.89
1512 | 2.1 | 0.91
1513 | 3.6 | 0.86
1514 | 3.5 | 0.88
1515 | 3.1 | 0.9
1516 | 4 | 0.88
1517 | 4 | 0.87
1518 | 4.2 | 0.88
1519 | 4.1 | 0.87
1520 | 3.5 | 0.88
1521 | 4.4 | 0.82
1522 | 5.7 | 0.8
1523 | 7.8 | 0.76
1524 | 8.1 | 0.74
1525 | 8.1 | 0.79
1526 | 8.1 | 0.79
1527 | 8 | 0.89
1528 | 7.6 | 0.94
1529 | 7.8 | 0.99
1530 | 8 | 0.97
1531 | 7.5 | 0.99
1532 | 7.8 | 0.99
1533 | 9.5 | 0.99
1534 | 10 | 0.99
1535 | 9.7 | 1
1536 | 9.7 | 1
1537 | 9.8 | 1
1538 | 9.3 | 1
1539 | 9.1 | 0.99
1540 | 8.9 | 0.99
1541 | 8.9 | 0.97
1542 | 8.9 | 0.97
1543 | 8.9 | 0.96
1544 | 8.9 | 0.97
1545 | 6 | 0.95
1546 | 4.7 | 0.95
1547 | 4.8 | 0.9
1548 | 5.5 | 0.86
1549 | 6.7 | 0.78
1550 | 7.5 | 0.79
1551 | 8.5 | 0.69
1552 | 8.8 | 0.63
1553 | 8.1 | 0.72
1554 | 6.9 | 0.82
1555 | 6.4 | 0.84
1556 | 5.9 | 0.86
1557 | 5.2 | 0.89
1558 | 5.2 | 0.84
1559 | 4.4 | 0.87
1560 | 4.6 | 0.89
1561 | 4.5 | 0.85
1562 | 4.5 | 0.84
1563 | 5.1 | 0.89
1564 | 5.2 | 0.89
1565 | 4.5 | 0.89
1566 | 4.8 | 0.84
1567 | 4.6 | 0.85
1568 | 4.6 | 0.87
1569 | 5.2 | 0.84
1570 | 6.5 | 0.79
1571 | 7.3 | 0.73
1572 | 7.8 | 0.72
1573 | 9 | 0.67
1574 | 9.3 | 0.65
1575 | 9.2 | 0.63
1576 | 10.3 | 0.55
1577 | 10.1 | 0.55
1578 | 9.1 | 0.53
1579 | 7.9 | 0.63
1580 | 6.8 | 0.67
1581 | 3.8 | 0.8
1582 | 5.7 | 0.77
1583 | 5 | 0.81
1584 | 3.9 | 0.83
1585 | 3.3 | 0.85
1586 | 3.5 | 0.81
1587 | 3.1 | 0.86
1588 | 3.1 | 0.9
1589 | 3.6 | 0.93
1590 | 3.5 | 0.95
1591 | 4.4 | 0.95
1592 | 5.4 | 0.91
1593 | 6.3 | 0.88
1594 | 6.8 | 0.93
1595 | 7.1 | 0.96
1596 | 7.7 | 0.99
1597 | 8.4 | 0.99
1598 | 9.2 | 0.99
1599 | 10.6 | 0.99
1600 | 12.9 | 0.84
1601 | 11.5 | 0.68
1602 | 10.3 | 0.61
1603 | 9 | 0.64
1604 | 7.9 | 0.75
1605 | 7.5 | 0.74
1606 | 6.5 | 0.78
1607 | 5.5 | 0.84
1608 | 5 | 0.87
1609 | 4.2 | 0.93
1610 | 5.3 | 0.92
1611 | 7.1 | 0.91
1612 | 7.6 | 0.91
1613 | 8.4 | 0.88
1614 | 8.1 | 0.76
1615 | 7.8 | 0.79
1616 | 7.4 | 0.74
1617 | 7.6 | 0.61
1618 | 7.9 | 0.57
1619 | 8.6 | 0.52
1620 | 8.5 | 0.56
1621 | 9.1 | 0.56
1622 | 9.1 | 0.51
1623 | 8.6 | 0.52
1624 | 8.5 | 0.6
1625 | 7.7 | 0.68
1626 | 7.3 | 0.71
1627 | 6 | 0.88
1628 | 5.3 | 0.95
1629 | 4.9 | 0.97
1630 | 5.3 | 0.98
1631 | 5.4 | 0.98
1632 | 5.8 | 1
1633 | 7.4 | 0.99
1634 | 8.2 | 0.99
1635 | 1.9 | 0.96
1636 | 2 | 0.94
1637 | 2.1 | 0.95
1638 | 4.8 | 0.86
1639 | 4.8 | 0.59
1640 | 4.1 | 0.72
1641 | 4 | 0.69
1642 | 4 | 0.74
1643 | 5.7 | 0.64
1644 | 7.1 | 0.55
1645 | 7.1 | 0.62
1646 | 4.4 | 0.9
1647 | 5.7 | 0.82
1648 | 7.6 | 0.53
1649 | 5 | 0.75
1650 | 4.5 | 0.76
1651 | 3.7 | 0.76
1652 | 3.3 | 0.73
1653 | 2.8 | 0.82
1654 | 2.3 | 0.91
1655 | 2 | 0.89
1656 | 2.2 | 0.93
1657 | 2.7 | 0.84
1658 | 3.4 | 0.71
1659 | 2.2 | 0.78
1660 | 2.6 | 0.84
1661 | 1.3 | 0.87
1662 | 2.7 | 0.81
1663 | 2.1 | 0.84
1664 | 2.4 | 0.86
1665 | 2.5 | 0.89
1666 | 5.7 | 0.85
1667 | 7.2 | 0.81
1668 | 7.9 | 0.83
1669 | 8.8 | 0.77
1670 | 8.6 | 0.77
1671 | 9.1 | 0.73
1672 | 8.1 | 0.83
1673 | 8.1 | 0.83
1674 | 7.4 | 0.94
1675 | 7.3 | 0.97
1676 | 7.6 | 0.99
1677 | 8.3 | 0.99
1678 | 8.9 | 0.99
1679 | 9.4 | 0.99
1680 | 9.9 | 0.99
1681 | 10.1 | 0.99
1682 | 9.8 | 0.97
1683 | 7.6 | 0.94
1684 | 5 | 0.89
1685 | 4.7 | 0.85
1686 | 4.5 | 0.87
1687 | 4.1 | 0.9
1688 | 4.1 | 0.9
1689 | 3.7 | 0.86
1690 | 3.6 | 0.88
1691 | 3.3 | 0.86
1692 | 4 | 0.9
1693 | 6.1 | 0.82
1694 | 7 | 0.73
1695 | 6.1 | 0.64
1696 | 7.4 | 0.65
1697 | 4.9 | 0.76
1698 | 6 | 0.7
1699 | 5.1 | 0.75
1700 | 4.4 | 0.77
1701 | 4.7 | 0.76
1702 | 4.7 | 0.79
1703 | 4.7 | 0.78
1704 | 4.3 | 0.82
1705 | 4.5 | 0.77
1706 | 5 | 0.76
1707 | 5.5 | 0.74
1708 | 5.4 | 0.78
1709 | 5.1 | 0.78
1710 | 5.7 | 0.68
1711 | 4.8 | 0.78
1712 | 5 | 0.75
1713 | 5.4 | 0.8
1714 | 6.5 | 0.75
1715 | 7.1 | 0.73
1716 | 8.6 | 0.61
1717 | 7.8 | 0.72
1718 | 6.9 | 0.85
1719 | 8.6 | 0.7
1720 | 8.6 | 0.68
1721 | 8.6 | 0.65
1722 | 7.6 | 0.82
1723 | 7.6 | 0.82
1724 | 7 | 0.85
1725 | 7 | 0.85
1726 | 7.1 | 0.88
1727 | 7.3 | 0.88
1728 | 7.7 | 0.89
1729 | 8.4 | 0.85
1730 | 8.5 | 0.89
1731 | 8.9 | 0.89
1732 | 9.3 | 0.89
1733 | 9.8 | 0.88
1734 | 9.9 | 0.9
1735 | 10.1 | 0.92
1736 | 10.1 | 0.93
1737 | 10.2 | 0.95
1738 | 10.8 | 0.91
1739 | 11.7 | 0.85
1740 | 9.8 | 0.96
1741 | 10.6 | 0.89
1742 | 11.8 | 0.82
1743 | 11.6 | 0.82
1744 | 11.4 | 0.88
1745 | 11.8 | 0.88
1746 | 11.9 | 0.87
1747 | 11.8 | 0.88
1748 | 11.1 | 0.9
1749 | 11.2 | 0.9
1750 | 11.4 | 0.89
1751 | 11.1 | 0.91
1752 | 11.1 | 0.91
1753 | 11 | 0.89
1754 | 10.9 | 0.91
1755 | 11 | 0.9
1756 | 11 | 0.91
1757 | 11.3 | 0.89
1758 | 11.2 | 0.9
1759 | 11 | 0.92
1760 | 11 | 0.92
1761 | 9.7 | 0.95
1762 | 9.3 | 0.91
1763 | 9.3 | 0.88
1764 | 9 | 0.85
1765 | 9.1 | 0.81
1766 | 10.1 | 0.83
1767 | 10.1 | 0.81
1768 | 10.3 | 0.77
1769 | 9.7 | 0.87
1770 | 8.9 | 0.95
1771 | 8.2 | 0.99
1772 | 8.2 | 1
1773 | 9.7 | 0.99
1774 | 10.4 | 0.97
1775 | 10.4 | 0.96
1776 | 10.3 | 0.96
1777 | 10.2 | 0.93
1778 | 10.3 | 0.91
1779 | 10.1 | 0.92
1780 | 10 | 0.88
1781 | 9.8 | 0.92
1782 | 9.8 | 0.93
1783 | 9.8 | 0.96
1784 | 9.7 | 0.97
1785 | 9.7 | 0.97
1786 | 10 | 0.97
1787 | 10.1 | 0.96
1788 | 10.2 | 0.96
1789 | 9.6 | 0.91
1790 | 8.8 | 0.89
1791 | 7 | 0.85
1792 | 5.9 | 0.88
1793 | 6.3 | 0.82
1794 | 5 | 0.84
1795 | 5.1 | 0.79
1796 | 3.5 | 0.86
1797 | 2.4 | 0.91
1798 | 2.3 | 0.91
1799 | 1.5 | 0.92
1800 | 1.3 | 0.92
1801 | 1.2 | 0.92
1802 | 1.2 | 0.89
1803 | 1.2 | 0.9
1804 | 1.3 | 0.91
1805 | 1.4 | 0.92
1806 | 1.4 | 0.92
1807 | 2 | 0.91
1808 | 1.5 | 0.94
1809 | 2.1 | 0.91
1810 | 4 | 0.85
1811 | 5.9 | 0.76
1812 | 7.6 | 0.66
1813 | 7.8 | 0.69
1814 | 8.8 | 0.64
1815 | 9.2 | 0.65
1816 | 9.1 | 0.63
1817 | 7.7 | 0.77
1818 | 8.7 | 0.65
1819 | 8 | 0.67
1820 | 6.7 | 0.74
1821 | 6 | 0.74
1822 | 5.7 | 0.8
1823 | 5.1 | 0.84
1824 | 5.3 | 0.84
1825 | 5.5 | 0.83
1826 | 5 | 0.86
1827 | 4.9 | 0.81
1828 | 5.3 | 0.84
1829 | 4.9 | 0.89
1830 | 4.5 | 0.9
1831 | 5 | 0.87
1832 | 4.8 | 0.92
1833 | 5.5 | 0.92
1834 | 6.5 | 0.91
1835 | 7.4 | 0.87
1836 | 8.4 | 0.81
1837 | 7.8 | 0.91
1838 | 8.3 | 0.92
1839 | 9.1 | 0.81
1840 | 9.7 | 0.77
1841 | 9.6 | 0.8
1842 | 9.8 | 0.75
1843 | 9.4 | 0.75
1844 | 8.8 | 0.77
1845 | 8.3 | 0.79
1846 | 7.9 | 0.83
1847 | 7.6 | 0.87
1848 | 6.9 | 0.9
1849 | 7.3 | 0.88
1850 | 6 | 0.92
1851 | 4.1 | 0.93
1852 | 5.3 | 0.97
1853 | 6.5 | 0.95
1854 | 6.7 | 0.98
1855 | 7.1 | 0.99
1856 | 7.5 | 0.99
1857 | 8.3 | 0.99
1858 | 9.1 | 1
1859 | 9.9 | 1
1860 | 11.8 | 0.94
1861 | 13 | 0.8
1862 | 14 | 0.69
1863 | 15.2 | 0.67
1864 | 15.4 | 0.67
1865 | 16.3 | 0.62
1866 | 15.6 | 0.67
1867 | 14.4 | 0.72
1868 | 12 | 0.82
1869 | 10.6 | 0.89
1870 | 9.4 | 0.92
1871 | 8.7 | 0.94
1872 | 8.1 | 0.96
1873 | 8 | 0.96
1874 | 7.5 | 0.97
1875 | 7 | 0.99
1876 | 5.3 | 0.98
1877 | 5.6 | 1
1878 | 4.3 | 1
1879 | 4.6 | 1
1880 | 3.9 | 1
1881 | 5.4 | 1
1882 | 7.9 | 1
1883 | 9 | 1
1884 | 10.7 | 0.99
1885 | 11.2 | 0.97
1886 | 12 | 0.96
1887 | 13.2 | 0.9
1888 | 13.6 | 0.87
1889 | 12.5 | 0.95
1890 | 12.3 | 0.95
1891 | 11.6 | 0.96
1892 | 11.1 | 0.96
1893 | 10.4 | 0.96
1894 | 10.2 | 0.95
1895 | 9.5 | 0.96
1896 | 9.4 | 0.95
1897 | 9.3 | 0.97
1898 | 9.2 | 0.97
1899 | 9.1 | 0.99
1900 | 9 | 0.97
1901 | 8.8 | 0.96
1902 | 8.6 | 0.97
1903 | 8.6 | 0.99
1904 | 8.5 | 1
1905 | 9 | 0.96
1906 | 9.5 | 0.92
1907 | 10.2 | 0.92
1908 | 10.1 | 0.92
1909 | 10.8 | 0.91
1910 | 10.9 | 0.91
1911 | 11.1 | 0.86
1912 | 10.7 | 0.92
1913 | 10.3 | 0.95
1914 | 9.6 | 0.93
1915 | 8.8 | 1
1916 | 8.8 | 1
1917 | 9 | 1
1918 | 9.1 | 1
1919 | 9.4 | 1
1920 | 9.4 | 1
1921 | 9.2 | 1
1922 | 9.2 | 0.99
1923 | 8.9 | 0.97
1924 | 8.6 | 0.99
1925 | 8.3 | 0.96
1926 | 8.7 | 0.92
1927 | 8.4 | 0.93
1928 | 8.7 | 0.92
1929 | 8.9 | 0.93
1930 | 9.4 | 0.93
1931 | 9.2 | 0.97
1932 | 9.3 | 0.99
1933 | 9.7 | 0.99
1934 | 10.5 | 0.96
1935 | 9.1 | 0.96
1936 | 9.4 | 0.8
1937 | 10.1 | 0.68
1938 | 9.8 | 0.67
1939 | 8.6 | 0.63
1940 | 7.8 | 0.69
1941 | 6.9 | 0.72
1942 | 6.5 | 0.71
1943 | 6 | 0.73
1944 | 5.3 | 0.78
1945 | 4.8 | 0.81
1946 | 4.3 | 0.85
1947 | 4.9 | 0.81
1948 | 4.1 | 0.87
1949 | 4 | 0.83
1950 | 3.9 | 0.83
1951 | 3.7 | 0.83
1952 | 4 | 0.8
1953 | 4.3 | 0.8
1954 | 5.2 | 0.8
1955 | 6.5 | 0.73
1956 | 7.5 | 0.66
1957 | 8.1 | 0.5
1958 | 8.6 | 0.55
1959 | 8.8 | 0.54
1960 | 8 | 0.62
1961 | 7 | 0.64
1962 | 6.8 | 0.67
1963 | 6.3 | 0.7
1964 | 6.5 | 0.65
1965 | 6.5 | 0.63
1966 | 6.4 | 0.63
1967 | 6 | 0.7
1968 | 5.5 | 0.74
1969 | 4.7 | 0.79
1970 | 4.3 | 0.82
1971 | 3.9 | 0.82
1972 | 3.6 | 0.81
1973 | 3.4 | 0.83
1974 | 2.7 | 0.86
1975 | 2.5 | 0.86
1976 | 2.7 | 0.84
1977 | 3.5 | 0.83
1978 | 5.7 | 0.75
1979 | 7 | 0.71
1980 | 8.5 | 0.6
1981 | 9.1 | 0.58
1982 | 9.2 | 0.57
1983 | 9.4 | 0.59
1984 | 9.1 | 0.62
1985 | 9.6 | 0.58
1986 | 8.9 | 0.6
1987 | 8.8 | 0.65
1988 | 7.2 | 0.76
1989 | 6.5 | 0.81
1990 | 6.6 | 0.81
1991 | 6.3 | 0.82
1992 | 6.5 | 0.84
1993 | 6.6 | 0.84
1994 | 6 | 0.83
1995 | 6.2 | 0.86
1996 | 5.6 | 0.89
1997 | 5.4 | 0.91
1998 | 6 | 0.86
1999 | 6 | 0.88
2000 | 5.7 | 0.89
2001 | 6.2 | 0.89
2002 | 7.7 | 0.83
2003 | 9.3 | 0.71
2004 | 10.6 | 0.63
2005 | 11.3 | 0.55
2006 | 12 | 0.53
2007 | 12.9 | 0.51
2008 | 12.8 | 0.57
2009 | 10.8 | 0.66
2010 | 10.3 | 0.65
2011 | 8 | 0.75
2012 | 6.8 | 0.79
2013 | 6.6 | 0.85
2014 | 6.3 | 0.85
2015 | 7.7 | 0.73
2016 | 7.6 | 0.77
2017 | 6.8 | 0.79
2018 | 6.3 | 0.8
2019 | 5.8 | 0.8
2020 | 4.8 | 0.86
2021 | 5.2 | 0.81
2022 | 4.6 | 0.89
2023 | 4.4 | 0.85
2024 | 4.9 | 0.81
2025 | 6.8 | 0.75
2026 | 7.6 | 0.76
2027 | 9 | 0.71
2028 | 10.5 | 0.6
2029 | 11.6 | 0.64
2030 | 12.2 | 0.58
2031 | 11.8 | 0.65
2032 | 12.1 | 0.65
2033 | 11.5 | 0.65
2034 | 10.8 | 0.66
2035 | 9.4 | 0.7
2036 | 6.7 | 0.79
2037 | 7.6 | 0.8
2038 | 8.6 | 0.78
2039 | 8.2 | 0.79
2040 | 7.7 | 0.79
2041 | 6.8 | 0.82
2042 | 6.4 | 0.84
2043 | 6.2 | 0.82
2044 | 5.5 | 0.87
2045 | 5.5 | 0.84
2046 | 4.4 | 0.92
2047 | 4.4 | 0.9
2048 | 4.3 | 0.9
2049 | 7.8 | 0.78
2050 | 9.1 | 0.73
2051 | 10.1 | 0.73
2052 | 10.1 | 0.76
2053 | 11.4 | 0.7
2054 | 12.7 | 0.62
2055 | 12.6 | 0.67
2056 | 12.4 | 0.73
2057 | 12.2 | 0.73
2058 | 11.5 | 0.76
2059 | 10.2 | 0.8
2060 | 7.7 | 0.86
2061 | 6.1 | 0.91
2062 | 5.7 | 0.91
2063 | 6.8 | 0.87
2064 | 6.8 | 0.85
2065 | 6.2 | 0.86
2066 | 6 | 0.86
2067 | 5.2 | 0.89
2068 | 3.9 | 0.95
2069 | 4 | 0.95
2070 | 3.8 | 0.95
2071 | 2 | 0.96
2072 | 1.2 | 0.98
2073 | 5.1 | 0.97
2074 | 7.8 | 0.91
2075 | 8.6 | 0.88
2076 | 9.7 | 0.82
2077 | 10.9 | 0.76
2078 | 11.1 | 0.74
2079 | 11.2 | 0.73
2080 | 10.8 | 0.74
2081 | 10.8 | 0.76
2082 | 10 | 0.79
2083 | 8.9 | 0.84
2084 | 6.8 | 0.9
2085 | 5.5 | 0.94
2086 | 5.5 | 0.94
2087 | 4.3 | 0.97
2088 | 5.9 | 0.95
2089 | 6.6 | 0.94
2090 | 6.5 | 0.94
2091 | 6.1 | 0.94
2092 | 6.4 | 0.94
2093 | 6.1 | 0.94
2094 | 6.2 | 0.94
2095 | 6.5 | 0.94
2096 | 6.9 | 0.9
2097 | 7.4 | 0.88
2098 | 7.9 | 0.86
2099 | 8.9 | 0.82
2100 | 9.8 | 0.79
2101 | 10.8 | 0.76
2102 | 10.6 | 0.75
2103 | 11.2 | 0.73
2104 | 11.1 | 0.73
2105 | 10.5 | 0.74
2106 | 9.6 | 0.78
2107 | 8.5 | 0.81
2108 | 6.3 | 0.86
2109 | 4.7 | 0.9
2110 | 4.1 | 0.9
2111 | 4.5 | 0.89
2112 | 5 | 0.84
2113 | 6.5 | 0.81
2114 | 6.7 | 0.79
2115 | 6.7 | 0.79
2116 | 6.7 | 0.78
2117 | 6.7 | 0.76
2118 | 6.7 | 0.75
2119 | 6.8 | 0.72
2120 | 6.8 | 0.72
2121 | 7.1 | 0.71
2122 | 7.5 | 0.7
2123 | 8.3 | 0.66
2124 | 8.8 | 0.62
2125 | 9.3 | 0.62
2126 | 10.1 | 0.6
2127 | 10.6 | 0.59
2128 | 10.8 | 0.6
2129 | 11.6 | 0.61
2130 | 11.4 | 0.58
2131 | 11.3 | 0.62
2132 | 10.8 | 0.67
2133 | 10.1 | 0.72
2134 | 8.3 | 0.75
2135 | 8.5 | 0.78
2136 | 8.5 | 0.79
2137 | 7.9 | 0.83
2138 | 7.2 | 0.83
2139 | 7.5 | 0.84
2140 | 6.2 | 0.86
2141 | 5.4 | 0.86
2142 | 4.1 | 0.83
2143 | 3.7 | 0.81
2144 | 4.2 | 0.75
2145 | 5.3 | 0.74
2146 | 6.9 | 0.68
2147 | 8.3 | 0.61
2148 | 9.5 | 0.56
2149 | 10.4 | 0.56
2150 | 11.7 | 0.55
2151 | 11.1 | 0.67
2152 | 10.9 | 0.7
2153 | 9.6 | 0.76
2154 | 9.4 | 0.75
2155 | 8.2 | 0.79
2156 | 7.4 | 0.86
2157 | 6.8 | 0.9
2158 | 6.4 | 0.89
2159 | 6.2 | 0.91
2160 | 5.9 | 0.94
2161 | 5.6 | 0.94
2162 | 5.3 | 0.92
2163 | 5.2 | 0.92
2164 | 5.3 | 0.92
2165 | 5.2 | 0.94
2166 | 5.1 | 0.92
2167 | 5.6 | 0.92
2168 | 6.4 | 0.92
2169 | 6.7 | 0.91
2170 | 6.6 | 0.93
2171 | 7.5 | 0.9
2172 | 7.8 | 0.89
2173 | 8.3 | 0.87
2174 | 9.1 | 0.89
2175 | 10.4 | 0.85
2176 | 10.2 | 0.86
2177 | 10 | 0.84
2178 | 10.2 | 0.72
2179 | 9.4 | 0.7
2180 | 8.5 | 0.68
2181 | 7.7 | 0.79
2182 | 6.3 | 0.86
2183 | 5.5 | 0.83
2184 | 4.8 | 0.81
2185 | 4.2 | 0.85
2186 | 3.8 | 0.87
2187 | 3.7 | 0.81
2188 | 3.2 | 0.84
2189 | 2.9 | 0.86
2190 | 2.2 | 0.89
2191 | 0.4 | 0.92
2192 | 2.5 | 0.89
2193 | 2.3 | 0.93
2194 | 4.5 | 0.79
2195 | 3.8 | 0.82
2196 | 3.5 | 0.86
2197 | 3.4 | 0.93
2198 | 3.5 | 0.83
2199 | 4.8 | 0.76
2200 | 5.1 | 0.73
2201 | 4.2 | 0.85
2202 | 3.5 | 0.86
2203 | 2.8 | 0.89
2204 | 2.9 | 0.81
2205 | 2.2 | 0.91
2206 | 2.1 | 0.89
2207 | 2.3 | 0.89
2208 | 3.2 | 0.83
2209 | 3.1 | 0.84
2210 | 2.9 | 0.86
2211 | 2.4 | 0.87
2212 | 2.2 | 0.87
2213 | 2.4 | 0.87
2214 | 2.4 | 0.86
2215 | 2.8 | 0.86
2216 | 3.1 | 0.86
2217 | 4 | 0.82
2218 | 5 | 0.73
2219 | 5 | 0.75
2220 | 5.9 | 0.65
2221 | 4.8 | 0.76
2222 | 5.7 | 0.68
2223 | 6 | 0.7
2224 | 7.7 | 0.62
2225 | 7.1 | 0.62
2226 | 6.8 | 0.65
2227 | 6.6 | 0.62
2228 | 5.9 | 0.68
2229 | 5.3 | 0.67
2230 | 4.7 | 0.73
2231 | 4.6 | 0.77
2232 | 5 | 0.79
2233 | 5 | 0.83
2234 | 4.8 | 0.89
2235 | 5 | 0.9
2236 | 4.5 | 0.9
2237 | 4 | 0.9
2238 | 3.6 | 0.9
2239 | 3.2 | 0.86
2240 | 2.5 | 0.89
2241 | 3.6 | 0.85
2242 | 4.3 | 0.8
2243 | 5.2 | 0.73
2244 | 6.2 | 0.66
2245 | 7.3 | 0.55
2246 | 7.2 | 0.58
2247 | 7.7 | 0.51
2248 | 7.8 | 0.61
2249 | 4.7 | 0.73
2250 | 6.9 | 0.63
2251 | 6.6 | 0.61
2252 | 5 | 0.69
2253 | 4.3 | 0.72
2254 | 3.3 | 0.79
2255 | 2.7 | 0.81
2256 | 2.1 | 0.84
2257 | 1.5 | 0.85
2258 | 0.5 | 0.86
2259 | 0.7 | 0.9
2260 | 0.8 | 0.9
2261 | 0.9 | 0.86
2262 | 0.2 | 0.9
2263 | 0.1 | 0.94
2264 | 1.1 | 0.9
2265 | 2 | 0.85
2266 | 4.4 | 0.82
2267 | 6.3 | 0.76
2268 | 7.6 | 0.72
2269 | 9.2 | 0.62
2270 | 9.5 | 0.58
2271 | 8.8 | 0.58
2272 | 9.3 | 0.59
2273 | 8.5 | 0.69
2274 | 8 | 0.75
2275 | 7.1 | 0.88
2276 | 7 | 0.85
2277 | 6.7 | 0.9
2278 | 6 | 0.94
2279 | 5.7 | 0.95
2280 | 5.5 | 0.95
2281 | 6 | 0.98
2282 | 6.6 | 0.97
2283 | 6.5 | 0.97
2284 | 6.4 | 0.97
2285 | 6.4 | 0.98
2286 | 6.7 | 0.98
2287 | 7 | 0.99
2288 | 7 | 0.97
2289 | 7.7 | 0.94
2290 | 8.1 | 0.9
2291 | 8.8 | 0.89
2292 | 9.2 | 0.81
2293 | 10.4 | 0.8
2294 | 9.6 | 0.83
2295 | 9.3 | 0.83
2296 | 9.6 | 0.82
2297 | 9.6 | 0.79
2298 | 9.6 | 0.78
2299 | 9.1 | 0.79
2300 | 8.4 | 0.81
2301 | 7.6 | 0.84
2302 | 8 | 0.82
2303 | 7.2 | 0.83
2304 | 6.8 | 0.79
2305 | 6.3 | 0.79
2306 | 5.8 | 0.74
2307 | 5.4 | 0.66
2308 | 4.8 | 0.68
2309 | 4.4 | 0.79
2310 | 3.3 | 0.83
2311 | 2.9 | 0.83
2312 | 3.7 | 0.75
2313 | 5.3 | 0.67
2314 | 7.1 | 0.7
2315 | 9.1 | 0.73
2316 | 9.4 | 0.76
2317 | 10.4 | 0.7
2318 | 10.9 | 0.7
2319 | 10 | 0.73
2320 | 9.1 | 0.79
2321 | 8.6 | 0.85
2322 | 8.6 | 0.82
2323 | 8.4 | 0.86
2324 | 8.1 | 0.89
2325 | 7.8 | 0.91
2326 | 7.7 | 0.93
2327 | 8.1 | 0.92
2328 | 8.2 | 0.94
2329 | 8.2 | 0.94
2330 | 8.2 | 0.94
2331 | 8.2 | 0.96
2332 | 8 | 0.96
2333 | 8.1 | 0.96
2334 | 8.1 | 0.97
2335 | 8.1 | 0.96
2336 | 8.3 | 0.96
2337 | 8.4 | 0.96
2338 | 8.7 | 0.97
2339 | 9.8 | 0.88
2340 | 9.9 | 0.87
2341 | 10.5 | 0.86
2342 | 10.5 | 0.83
2343 | 10.4 | 0.78
2344 | 10.3 | 0.81
2345 | 9.6 | 0.87
2346 | 9.6 | 0.84
2347 | 9.2 | 0.87
2348 | 8.7 | 0.94
2349 | 8.6 | 0.96
2350 | 8.6 | 0.96
2351 | 8.7 | 0.94
2352 | 8.4 | 0.96
2353 | 8 | 0.97
2354 | 7.6 | 0.96
2355 | 7.4 | 0.97
2356 | 7.4 | 0.99
2357 | 8 | 0.99
2358 | 7.9 | 0.97
2359 | 7.8 | 0.97
2360 | 7.8 | 0.97
2361 | 7.7 | 0.96
2362 | 8.9 | 0.9
2363 | 9.6 | 0.87
2364 | 10.3 | 0.83
2365 | 9.8 | 0.84
2366 | 10.8 | 0.79
2367 | 10.2 | 0.88
2368 | 9.4 | 0.95
2369 | 8.4 | 0.94
2370 | 8.3 | 0.93
2371 | 8.1 | 0.93
2372 | 7.9 | 0.93
2373 | 7.8 | 0.93
2374 | 7.6 | 0.91
2375 | 7.2 | 0.93
2376 | 7.5 | 0.9
2377 | 7.5 | 0.91
2378 | 7.4 | 0.93
2379 | 7.4 | 0.9
2380 | 7.3 | 0.93
2381 | 7.3 | 0.91
2382 | 7.1 | 0.94
2383 | 6.9 | 0.94
2384 | 7.2 | 0.93
2385 | 8 | 0.87
2386 | 8.8 | 0.8
2387 | 9.4 | 0.81
2388 | 10.1 | 0.78
2389 | 10.6 | 0.76
2390 | 8.7 | 0.85
2391 | 9.5 | 0.85
2392 | 9 | 0.86
2393 | 8.2 | 0.87
2394 | 8.1 | 0.82
2395 | 7.6 | 0.82
2396 | 7.2 | 0.84
2397 | 6.9 | 0.87
2398 | 6.9 | 0.87
2399 | 6.7 | 0.88
2400 | 6.7 | 0.88
2401 | 5.3 | 0.92
2402 | 6.4 | 0.89
2403 | 6.5 | 0.88
2404 | 6.5 | 0.88
2405 | 6.2 | 0.88
2406 | 6.2 | 0.86
2407 | 5.6 | 0.89
2408 | 6.5 | 0.87
2409 | 7.4 | 0.84
2410 | 8.8 | 0.77
2411 | 9.4 | 0.75
2412 | 10.2 | 0.72
2413 | 10.5 | 0.74
2414 | 10.4 | 0.75
2415 | 10.4 | 0.7
2416 | 10.4 | 0.72
2417 | 10.3 | 0.7
2418 | 9.6 | 0.71
2419 | 8.4 | 0.83
2420 | 8.1 | 0.86
2421 | 7 | 0.91
2422 | 6.7 | 0.91
2423 | 5.7 | 0.91
2424 | 5.5 | 0.91
2425 | 6.5 | 0.89
2426 | 7.4 | 0.88
2427 | 7.2 | 0.88
2428 | 7.7 | 0.9
2429 | 7.8 | 0.9
2430 | 8 | 0.92
2431 | 7.8 | 0.89
2432 | 7.8 | 0.84
2433 | 8.1 | 0.83
2434 | 8 | 0.79
2435 | 8.1 | 0.79
2436 | 8.9 | 0.72
2437 | 8.7 | 0.73
2438 | 9 | 0.72
2439 | 8.7 | 0.76
2440 | 8.4 | 0.78
2441 | 8.1 | 0.81
2442 | 8.2 | 0.77
2443 | 7.9 | 0.79
2444 | 7.6 | 0.8
2445 | 7.6 | 0.82
2446 | 6.9 | 0.82
2447 | 7.6 | 0.82
2448 | 7.5 | 0.81
2449 | 7.5 | 0.83
2450 | 7.3 | 0.81
2451 | 7.1 | 0.81
2452 | 7.4 | 0.84
2453 | 7.4 | 0.88
2454 | 7.7 | 0.87
2455 | 7.8 | 0.87
2456 | 7.9 | 0.84
2457 | 7.8 | 0.83
2458 | 8 | 0.8
2459 | 7.9 | 0.8
2460 | 8 | 0.8
2461 | 8 | 0.79
2462 | 8.1 | 0.79
2463 | 8.2 | 0.78
2464 | 8 | 0.79
2465 | 7.4 | 0.86
2466 | 7.1 | 0.87
2467 | 6.7 | 0.93
2468 | 6.6 | 0.93
2469 | 6.4 | 0.94
2470 | 6.3 | 0.94
2471 | 6.4 | 0.95
2472 | 6.3 | 0.94
2473 | 5.7 | 0.95
2474 | 5.6 | 0.95
2475 | 5.7 | 0.95
2476 | 5.9 | 0.95
2477 | 5.9 | 0.97
2478 | 5.7 | 0.97
2479 | 5.8 | 0.98
2480 | 6 | 0.97
2481 | 5.9 | 0.98
2482 | 5.7 | 0.97
2483 | 5.6 | 0.97
2484 | 5.7 | 0.98
2485 | 5.8 | 0.97
2486 | 5.7 | 0.98
2487 | 5.7 | 0.97
2488 | 5.6 | 0.97
2489 | 5.4 | 0.97
2490 | 5.6 | 0.97
2491 | 5.1 | 0.97
2492 | 5.1 | 0.97
2493 | 4.8 | 0.94
2494 | 5.1 | 0.95
2495 | 4.7 | 0.93
2496 | 4.8 | 0.95
2497 | 5.2 | 0.95
2498 | 5.5 | 0.98
2499 | 6 | 0.97
2500 | 6.5 | 0.97
2501 | 6.4 | 0.97
2502 | 6.6 | 0.98
2503 | 6.7 | 0.98
2504 | 7 | 0.99
2505 | 7 | 0.99
2506 | 7.2 | 0.99
2507 | 7.1 | 0.97
2508 | 6.9 | 0.97
2509 | 7 | 0.97
2510 | 7 | 0.96
2511 | 7 | 0.99
2512 | 7 | 0.97
2513 | 7.1 | 0.97
2514 | 7.3 | 0.99
2515 | 7.6 | 0.99
2516 | 8 | 1
2517 | 8.2 | 1
2518 | 8.3 | 0.99
2519 | 7.6 | 0.99
2520 | 6.3 | 1
2521 | 6.3 | 0.98
2522 | 6.5 | 1
2523 | 6.6 | 1
2524 | 7.2 | 1
2525 | 6.7 | 1
2526 | 6.6 | 1
2527 | 6.6 | 1
2528 | 6.7 | 0.98
2529 | 6.8 | 1
2530 | 8 | 1
2531 | 8.5 | 1
2532 | 10.4 | 0.95
2533 | 11 | 0.86
2534 | 11.7 | 0.83
2535 | 11.9 | 0.82
2536 | 11.1 | 0.81
2537 | 10.8 | 0.85
2538 | 10.8 | 0.89
2539 | 9.7 | 0.91
2540 | 9.3 | 0.95
2541 | 9.1 | 0.97
2542 | 8.9 | 0.97
2543 | 9 | 0.97
2544 | 8.9 | 0.97
2545 | 8.7 | 0.97
2546 | 8.9 | 0.97
2547 | 8.9 | 0.99
2548 | 8.8 | 0.99
2549 | 8.6 | 1
2550 | 8.8 | 0.99
2551 | 8.9 | 0.99
2552 | 8.9 | 1
2553 | 8.9 | 0.97
2554 | 8.9 | 0.97
2555 | 9.1 | 0.99
2556 | 9.4 | 0.96
2557 | 10.4 | 0.91
2558 | 11.8 | 0.79
2559 | 11.1 | 0.83
2560 | 10 | 0.88
2561 | 10 | 0.87
2562 | 10.7 | 0.84
2563 | 9.9 | 0.86
2564 | 9.6 | 0.85
2565 | 9.6 | 0.85
2566 | 9.6 | 0.83
2567 | 9 | 0.82
2568 | 9.2 | 0.83
2569 | 9 | 0.84
2570 | 9.2 | 0.87
2571 | 9.1 | 0.88
2572 | 9.3 | 0.88
2573 | 9.5 | 0.87
2574 | 9.2 | 0.88
2575 | 9.2 | 0.88
2576 | 9.6 | 0.87
2577 | 11.1 | 0.83
2578 | 12 | 0.8
2579 | 12.8 | 0.77
2580 | 13.3 | 0.75
2581 | 13.6 | 0.74
2582 | 14.1 | 0.72
2583 | 15 | 0.7
2584 | 14.3 | 0.72
2585 | 13.5 | 0.74
2586 | 13.7 | 0.72
2587 | 13 | 0.74
2588 | 11.9 | 0.77
2589 | 11.7 | 0.77
2590 | 11.1 | 0.8
2591 | 11.3 | 0.83
2592 | 11.1 | 0.84
2593 | 10.9 | 0.85
2594 | 10.2 | 0.87
2595 | 10.3 | 0.87
2596 | 10.1 | 0.87
2597 | 10.2 | 0.86
2598 | 10.1 | 0.88
2599 | 10.3 | 0.87
2600 | 11 | 0.87
2601 | 12.5 | 0.83
2602 | 13.9 | 0.8
2603 | 15.2 | 0.75
2604 | 16.6 | 0.7
2605 | 17.4 | 0.65
2606 | 16.5 | 0.67
2607 | 16.4 | 0.7
2608 | 17.4 | 0.63
2609 | 17.6 | 0.65
2610 | 15.8 | 0.61
2611 | 14.1 | 0.78
2612 | 12.1 | 0.81
2613 | 11.9 | 0.8
2614 | 10.7 | 0.84
2615 | 11.6 | 0.72
2616 | 10.4 | 0.83
2617 | 11.1 | 0.69
2618 | 10.6 | 0.75
2619 | 10.5 | 0.76
2620 | 9.6 | 0.88
2621 | 9.2 | 0.89
2622 | 9.1 | 0.89
2623 | 9.8 | 0.84
2624 | 11 | 0.78
2625 | 12.8 | 0.76
2626 | 15.5 | 0.61
2627 | 16.1 | 0.63
2628 | 17.1 | 0.52
2629 | 18.4 | 0.52
2630 | 18.9 | 0.53
2631 | 18.8 | 0.48
2632 | 17.5 | 0.57
2633 | 16.8 | 0.58
2634 | 16.6 | 0.58
2635 | 15.5 | 0.63
2636 | 13.6 | 0.72
2637 | 12.6 | 0.76
2638 | 12 | 0.75
2639 | 11 | 0.75
2640 | 11.5 | 0.7
2641 | 10.4 | 0.73
2642 | 10.1 | 0.79
2643 | 9.4 | 0.83
2644 | 9.2 | 0.84
2645 | 8.6 | 0.85
2646 | 7.3 | 0.93
2647 | 6.2 | 0.95
2648 | 6.5 | 0.98
2649 | 8.3 | 1
2650 | 8.5 | 1
2651 | 9.9 | 0.99
2652 | 11.8 | 0.95
2653 | 13.1 | 0.88
2654 | 12.8 | 0.89
2655 | 13.3 | 0.83
2656 | 13.5 | 0.77
2657 | 12.7 | 0.81
2658 | 11.5 | 0.85
2659 | 10.4 | 0.63
2660 | 9 | 0.95
2661 | 8.4 | 0.94
2662 | 8 | 0.96
2663 | 8.1 | 0.97
2664 | 7.9 | 0.96
2665 | 7.8 | 0.97
2666 | 7.4 | 0.97
2667 | 7.6 | 0.99
2668 | 8 | 0.99
2669 | 8.5 | 1
2670 | 8.4 | 0.99
2671 | 8.8 | 0.95
2672 | 10.4 | 0.87
2673 | 12 | 0.81
2674 | 13.2 | 0.78
2675 | 14.4 | 0.75
2676 | 14.4 | 0.73
2677 | 15.8 | 0.63
2678 | 15.7 | 0.62
2679 | 13.5 | 0.73
2680 | 14 | 0.72
2681 | 13.6 | 0.77
2682 | 11.7 | 0.89
2683 | 11.1 | 0.94
2684 | 10.8 | 0.96
2685 | 10.5 | 0.97
2686 | 10.4 | 0.99
2687 | 10.4 | 0.97
2688 | 10.1 | 0.97
2689 | 10 | 0.99
2690 | 9.9 | 0.99
2691 | 10 | 0.97
2692 | 10 | 0.96
2693 | 10.2 | 0.9
2694 | 10.6 | 0.87
2695 | 10.6 | 0.86
2696 | 10.9 | 0.86
2697 | 11.3 | 0.85
2698 | 12.2 | 0.83
2699 | 13.2 | 0.78
2700 | 13.5 | 0.76
2701 | 13.4 | 0.78
2702 | 14.3 | 0.78
2703 | 14 | 0.84
2704 | 14 | 0.83
2705 | 13.7 | 0.83
2706 | 13.6 | 0.84
2707 | 12.4 | 0.88
2708 | 11.3 | 0.91
2709 | 10.2 | 0.95
2710 | 10.5 | 0.96
2711 | 10.7 | 0.96
2712 | 10.5 | 0.96
2713 | 10.6 | 0.95
2714 | 10.7 | 0.99
2715 | 11 | 0.99
2716 | 11 | 1
2717 | 10.8 | 0.99
2718 | 10.4 | 1
2719 | 10.2 | 1
2720 | 10.1 | 0.99
2721 | 10.1 | 0.97
2722 | 10.4 | 0.94
2723 | 10.7 | 0.9
2724 | 10.5 | 0.92
2725 | 10.9 | 0.92
2726 | 11.1 | 0.92
2727 | 11.9 | 0.85
2728 | 11 | 0.87
2729 | 11.4 | 0.77
2730 | 10.2 | 0.82
2731 | 9.8 | 0.77
2732 | 9.1 | 0.84
2733 | 8.4 | 0.89
2734 | 7.5 | 0.93
2735 | 7.3 | 0.94
2736 | 7.4 | 0.96
2737 | 8.3 | 0.94
2738 | 7.9 | 0.96
2739 | 8 | 0.96
2740 | 8.6 | 0.94
2741 | 8.5 | 0.94
2742 | 7.7 | 0.97
2743 | 7.3 | 0.97
2744 | 8.4 | 0.96
2745 | 9.4 | 0.93
2746 | 10.3 | 0.85
2747 | 10.8 | 0.74
2748 | 11.3 | 0.77
2749 | 10.5 | 0.76
2750 | 12.6 | 0.68
2751 | 10.3 | 0.78
2752 | 10 | 0.82
2753 | 9 | 0.86
2754 | 11.8 | 0.82
2755 | 10.8 | 0.81
2756 | 9.2 | 0.87
2757 | 8.4 | 0.92
2758 | 7.9 | 0.94
2759 | 8.2 | 0.97
2760 | 8.2 | 0.97
2761 | 8.5 | 0.97
2762 | 8.9 | 0.97
2763 | 8.6 | 0.96
2764 | 8.3 | 0.94
2765 | 8 | 0.93
2766 | 7.7 | 0.9
2767 | 7.4 | 0.9
2768 | 7.3 | 0.87
2769 | 7.7 | 0.83
2770 | 7.8 | 0.8
2771 | 9.7 | 0.68
2772 | 9.2 | 0.72
2773 | 8.5 | 0.79
2774 | 8.1 | 0.93
2775 | 8.3 | 0.97
2776 | 9.9 | 0.88
2777 | 9.4 | 0.76
2778 | 7.8 | 0.8
2779 | 7 | 0.85
2780 | 6.3 | 0.89
2781 | 6.1 | 0.86
2782 | 5.9 | 0.85
2783 | 5.3 | 0.89
2784 | 4.7 | 0.84
2785 | 5.4 | 0.81
2786 | 5 | 0.75
2787 | 5.4 | 0.74
2788 | 3.9 | 0.85
2789 | 5 | 0.7
2790 | 4.7 | 0.79
2791 | 5 | 0.75
2792 | 6.2 | 0.7
2793 | 6.2 | 0.77
2794 | 7.1 | 0.73
2795 | 9.1 | 0.57
2796 | 9.6 | 0.57
2797 | 8.3 | 0.65
2798 | 10.5 | 0.51
2799 | 10.6 | 0.5
2800 | 10.5 | 0.53
2801 | 10.8 | 0.48
2802 | 9.8 | 0.61
2803 | 9.3 | 0.62
2804 | 8.7 | 0.61
2805 | 7.9 | 0.67
2806 | 5.9 | 0.79
2807 | 6.2 | 0.76
2808 | 7 | 0.77
2809 | 6.8 | 0.82
2810 | 6.7 | 0.84
2811 | 7 | 0.88
2812 | 7.1 | 0.96
2813 | 7.2 | 0.99
2814 | 7.6 | 1
2815 | 8.4 | 0.99
2816 | 9.6 | 1
2817 | 10.3 | 0.96
2818 | 12.3 | 0.87
2819 | 13.3 | 0.82
2820 | 14.3 | 0.75
2821 | 14.5 | 0.76
2822 | 14.7 | 0.75
2823 | 16.3 | 0.76
2824 | 14.9 | 0.8
2825 | 14.2 | 0.83
2826 | 13.7 | 0.83
2827 | 12.4 | 0.87
2828 | 11.2 | 0.89
2829 | 10.6 | 0.89
2830 | 10.3 | 0.95
2831 | 9.8 | 0.96
2832 | 9.9 | 0.99
2833 | 10.1 | 1
2834 | 10 | 0.99
2835 | 10.1 | 1
2836 | 10.1 | 1
2837 | 10.1 | 0.99
2838 | 9.7 | 0.99
2839 | 9.5 | 0.99
2840 | 9.9 | 0.99
2841 | 9.8 | 0.99
2842 | 9.4 | 0.99
2843 | 10.1 | 0.93
2844 | 9.9 | 0.93
2845 | 10.5 | 0.85
2846 | 11.2 | 0.8
2847 | 10.5 | 0.86
2848 | 10.3 | 0.9
2849 | 9.5 | 0.96
2850 | 9.5 | 0.96
2851 | 9.6 | 0.93
2852 | 9.3 | 0.97
2853 | 9.5 | 0.97
2854 | 9.6 | 0.97
2855 | 9.6 | 0.97
2856 | 9.6 | 0.97
2857 | 9.6 | 0.99
2858 | 9.7 | 0.99
2859 | 9.7 | 0.99
2860 | 9.8 | 0.99
2861 | 9.8 | 0.99
2862 | 9.8 | 1
2863 | 9.5 | 1
2864 | 9.7 | 0.99
2865 | 10 | 0.86
2866 | 10.9 | 0.8
2867 | 12.1 | 0.76
2868 | 12.4 | 0.73
2869 | 13.4 | 0.6
2870 | 14.4 | 0.63
2871 | 13.8 | 0.63
2872 | 15 | 0.61
2873 | 15.1 | 0.52
2874 | 13.6 | 0.51
2875 | 12.9 | 0.55
2876 | 11.6 | 0.53
2877 | 10.3 | 0.61
2878 | 9.4 | 0.74
2879 | 8.6 | 0.8
2880 | 7.8 | 0.82
2881 | 7.3 | 0.81
2882 | 6.8 | 0.84
2883 | 6.2 | 0.86
2884 | 5.7 | 0.91
2885 | 4.9 | 0.95
2886 | 5 | 0.9
2887 | 5.3 | 0.87
2888 | 6.4 | 0.84
2889 | 8.6 | 0.77
2890 | 10.2 | 0.68
2891 | 11.3 | 0.64
2892 | 11.9 | 0.65
2893 | 12.1 | 0.72
2894 | 11.9 | 0.67
2895 | 10.5 | 0.86
2896 | 12 | 0.75
2897 | 12.6 | 0.65
2898 | 13.6 | 0.57
2899 | 12 | 0.59
2900 | 10.8 | 0.7
2901 | 10 | 0.73
2902 | 9.1 | 0.79
2903 | 8.8 | 0.8
2904 | 8.5 | 0.81
2905 | 8.2 | 0.83
2906 | 7.7 | 0.86
2907 | 7.8 | 0.83
2908 | 7.3 | 0.86
2909 | 7 | 0.84
2910 | 7 | 0.84
2911 | 7.8 | 0.83
2912 | 8.2 | 0.79
2913 | 8.8 | 0.8
2914 | 9.2 | 0.83
2915 | 10.4 | 0.81
2916 | 10.3 | 0.75
2917 | 10.5 | 0.83
2918 | 10.1 | 0.88
2919 | 9.9 | 0.93
2920 | 9.9 | 0.96
2921 | 9.9 | 0.97
2922 | 10.1 | 0.97
2923 | 10.3 | 0.96
2924 | 10 | 0.96
2925 | 9.3 | 0.97
2926 | 9.1 | 0.97
2927 | 8.8 | 0.99
2928 | 9.1 | 0.99
2929 | 8.4 | 0.99
2930 | 8.3 | 1
2931 | 8.3 | 0.99
2932 | 8 | 0.99
2933 | 7.3 | 0.99
2934 | 6.8 | 0.99
2935 | 7.1 | 1
2936 | 7.4 | 0.97
2937 | 8.7 | 0.94
2938 | 9.6 | 0.82
2939 | 11.1 | 0.73
2940 | 11.7 | 0.66
2941 | 11.8 | 0.63
2942 | 12 | 0.61
2943 | 12.1 | 0.63
2944 | 12.2 | 0.62
2945 | 11.9 | 0.6
2946 | 11.8 | 0.54
2947 | 11.6 | 0.51
2948 | 11.1 | 0.56
2949 | 10.6 | 0.59
2950 | 10.1 | 0.6
2951 | 8.8 | 0.64
2952 | 7.1 | 0.74
2953 | 6 | 0.79
2954 | 5.4 | 0.83
2955 | 6 | 0.71
2956 | 4.8 | 0.73
2957 | 3.7 | 0.78
2958 | 2.9 | 0.79
2959 | 3.3 | 0.76
2960 | 4.4 | 0.72
2961 | 5.6 | 0.68
2962 | 6.7 | 0.62
2963 | 7.9 | 0.6
2964 | 9.4 | 0.54
2965 | 8.9 | 0.55
2966 | 9.9 | 0.55
2967 | 9.4 | 0.56
2968 | 10.3 | 0.62
2969 | 9.6 | 0.58
2970 | 9.7 | 0.6
2971 | 8.9 | 0.64
2972 | 7.6 | 0.7
2973 | 5.6 | 0.77
2974 | 5 | 0.73
2975 | 5.4 | 0.68
2976 | 5.4 | 0.65
2977 | 5.6 | 0.63
2978 | 5.6 | 0.66
2979 | 5.3 | 0.67
2980 | 4.8 | 0.71
2981 | 4.1 | 0.82
2982 | 3.9 | 0.83
2983 | 5 | 0.81
2984 | 6 | 0.77
2985 | 7.3 | 0.73
2986 | 9.8 | 0.61
2987 | 11 | 0.47
2988 | 12.3 | 0.48
2989 | 11.8 | 0.44
2990 | 12.8 | 0.47
2991 | 12.9 | 0.54
2992 | 12 | 0.55
2993 | 12 | 0.53
2994 | 11 | 0.49
2995 | 10.4 | 0.53
2996 | 8.5 | 0.64
2997 | 6 | 0.74
2998 | 4.3 | 0.82
2999 | 6 | 0.77
3000 | 5.7 | 0.78
3001 | 6.1 | 0.73
3002 | 5.7 | 0.75
3003 | 5.9 | 0.73
3004 | 6 | 0.73
3005 | 6.2 | 0.73
3006 | 6.6 | 0.69
3007 | 6.7 | 0.71
3008 | 7.8 | 0.71
3009 | 8.5 | 0.74
3010 | 9.1 | 0.71
3011 | 8.9 | 0.68
3012 | 10.2 | 0.67
3013 | 10.3 | 0.62
3014 | 11.4 | 0.61
3015 | 10.6 | 0.62
3016 | 10.5 | 0.64
3017 | 10 | 0.62
3018 | 9.8 | 0.67
3019 | 9.1 | 0.7
3020 | 8.4 | 0.71
3021 | 6.8 | 0.79
3022 | 6.6 | 0.81
3023 | 6.6 | 0.85
3024 | 6.6 | 0.9
3025 | 5.8 | 0.92
3026 | 5.8 | 0.92
3027 | 6.7 | 0.9
3028 | 7.6 | 0.91
3029 | 7.3 | 0.94
3030 | 6.8 | 0.96
3031 | 7 | 0.94
3032 | 7.8 | 0.96
3033 | 8.6 | 0.92
3034 | 9.7 | 0.86
3035 | 10.1 | 0.77
3036 | 11.3 | 0.66
3037 | 10.9 | 0.64
3038 | 10.2 | 0.71
3039 | 9.4 | 0.72
3040 | 10.1 | 0.61
3041 | 9.3 | 0.81
3042 | 8.5 | 0.88
3043 | 7.9 | 0.91
3044 | 7.7 | 0.96
3045 | 7.9 | 0.99
3046 | 7.9 | 0.97
3047 | 8.1 | 0.97
3048 | 7.9 | 0.99
3049 | 8.3 | 0.99
3050 | 8.1 | 0.99
3051 | 8.2 | 0.97
3052 | 7.9 | 0.97
3053 | 7.9 | 0.94
3054 | 7.6 | 0.99
3055 | 7.4 | 0.97
3056 | 7.3 | 0.97
3057 | 7.5 | 0.97
3058 | 7.7 | 0.94
3059 | 7.7 | 0.96
3060 | 7.9 | 0.91
3061 | 8.2 | 0.9
3062 | 8.4 | 0.89
3063 | 8.6 | 0.89
3064 | 8.8 | 0.85
3065 | 8.5 | 0.82
3066 | 8.3 | 0.82
3067 | 8 | 0.83
3068 | 8.2 | 0.82
3069 | 7.7 | 0.87
3070 | 7.7 | 0.87
3071 | 7.5 | 0.86
3072 | 6.9 | 0.87
3073 | 6.4 | 0.86
3074 | 6.2 | 0.89
3075 | 6.4 | 0.89
3076 | 5.7 | 0.91
3077 | 5.4 | 0.91
3078 | 4.9 | 0.89
3079 | 5.5 | 0.86
3080 | 6.5 | 0.81
3081 | 8 | 0.71
3082 | 8.7 | 0.67
3083 | 10.1 | 0.6
3084 | 10.8 | 0.56
3085 | 12 | 0.52
3086 | 11.9 | 0.5
3087 | 12.7 | 0.46
3088 | 13.1 | 0.43
3089 | 12.7 | 0.42
3090 | 12.5 | 0.39
3091 | 11.9 | 0.4
3092 | 11 | 0.45
3093 | 9.2 | 0.57
3094 | 7.8 | 0.64
3095 | 6.7 | 0.68
3096 | 5.9 | 0.71
3097 | 5.7 | 0.74
3098 | 5.4 | 0.77
3099 | 5.4 | 0.75
3100 | 5 | 0.75
3101 | 4.6 | 0.79
3102 | 4.8 | 0.78
3103 | 5.1 | 0.76
3104 | 7.6 | 0.66
3105 | 8.9 | 0.67
3106 | 9.4 | 0.57
3107 | 10.1 | 0.59
3108 | 10.8 | 0.53
3109 | 11.8 | 0.51
3110 | 11.9 | 0.62
3111 | 10.7 | 0.63
3112 | 12.1 | 0.6
3113 | 11.9 | 0.61
3114 | 12.2 | 0.63
3115 | 10 | 0.69
3116 | 9.2 | 0.79
3117 | 8.6 | 0.77
3118 | 8.1 | 0.82
3119 | 7.9 | 0.82
3120 | 7.4 | 0.81
3121 | 6.9 | 0.81
3122 | 5.8 | 0.86
3123 | 5.4 | 0.89
3124 | 5.1 | 0.92
3125 | 5 | 0.94
3126 | 5 | 0.94
3127 | 5.1 | 0.94
3128 | 5.6 | 0.92
3129 | 7.3 | 0.84
3130 | 9.7 | 0.74
3131 | 10.9 | 0.64
3132 | 11 | 0.58
3133 | 12.2 | 0.5
3134 | 13.5 | 0.43
3135 | 13 | 0.45
3136 | 13.4 | 0.45
3137 | 13.7 | 0.44
3138 | 13.7 | 0.64
3139 | 12.4 | 0.65
3140 | 10.9 | 0.66
3141 | 8.5 | 0.75
3142 | 7.3 | 0.74
3143 | 8.9 | 0.67
3144 | 8.6 | 0.66
3145 | 8.4 | 0.66
3146 | 8.5 | 0.7
3147 | 7.3 | 0.76
3148 | 5.4 | 0.83
3149 | 5.7 | 0.82
3150 | 6.1 | 0.86
3151 | 8.1 | 0.87
3152 | 9.3 | 0.89
3153 | 10.3 | 0.86
3154 | 11.8 | 0.73
3155 | 12.4 | 0.62
3156 | 12.8 | 0.65
3157 | 12.9 | 0.63
3158 | 12.9 | 0.67
3159 | 13.3 | 0.55
3160 | 13.3 | 0.53
3161 | 13.2 | 0.54
3162 | 12.4 | 0.48
3163 | 11.7 | 0.49
3164 | 9.8 | 0.65
3165 | 8.5 | 0.81
3166 | 7.8 | 0.89
3167 | 8.1 | 0.92
3168 | 8 | 0.93
3169 | 7.5 | 0.93
3170 | 7.6 | 0.93
3171 | 7.9 | 0.94
3172 | 8.1 | 0.96
3173 | 8.6 | 0.96
3174 | 8.6 | 0.96
3175 | 9.5 | 0.93
3176 | 10.6 | 0.86
3177 | 11.5 | 0.75
3178 | 12.6 | 0.7
3179 | 13.2 | 0.69
3180 | 13.6 | 0.66
3181 | 13.6 | 0.71
3182 | 13.6 | 0.71
3183 | 13.4 | 0.71
3184 | 13.2 | 0.72
3185 | 12.7 | 0.69
3186 | 12.3 | 0.7
3187 | 11.7 | 0.78
3188 | 10.5 | 0.8
3189 | 9.3 | 0.89
3190 | 8.5 | 0.92
3191 | 8.2 | 0.93
3192 | 8.2 | 0.9
3193 | 8.1 | 0.87
3194 | 8.1 | 0.85
3195 | 8.1 | 0.79
3196 | 8.5 | 0.86
3197 | 8.6 | 0.84
3198 | 8.9 | 0.88
3199 | 9.4 | 0.87
3200 | 10.2 | 0.85
3201 | 10.9 | 0.78
3202 | 12.1 | 0.74
3203 | 12.9 | 0.71
3204 | 13.6 | 0.68
3205 | 13.7 | 0.68
3206 | 13.9 | 0.7
3207 | 13.7 | 0.71
3208 | 13.6 | 0.72
3209 | 13.1 | 0.75
3210 | 12.7 | 0.72
3211 | 12.1 | 0.73
3212 | 11.5 | 0.72
3213 | 10.6 | 0.71
3214 | 10.4 | 0.69
3215 | 10.2 | 0.7
3216 | 9.8 | 0.74
3217 | 9.2 | 0.77
3218 | 9.1 | 0.89
3219 | 9.5 | 0.83
3220 | 9.6 | 0.82
3221 | 9.5 | 0.85
3222 | 10.4 | 0.8
3223 | 10.5 | 0.79
3224 | 10.7 | 0.77
3225 | 11.1 | 0.83
3226 | 11.5 | 0.78
3227 | 12.6 | 0.8
3228 | 13.2 | 0.8
3229 | 14.1 | 0.75
3230 | 14.6 | 0.76
3231 | 13.6 | 0.77
3232 | 13.1 | 0.78
3233 | 12.7 | 0.79
3234 | 12.3 | 0.82
3235 | 11.5 | 0.85
3236 | 11.1 | 0.89
3237 | 10.7 | 0.92
3238 | 10.4 | 0.94
3239 | 10.2 | 0.95
3240 | 10.1 | 0.93
3241 | 10 | 0.96
3242 | 10 | 0.95
3243 | 10.2 | 0.93
3244 | 10.1 | 0.88
3245 | 10 | 0.88
3246 | 9.8 | 0.93
3247 | 9.9 | 0.91
3248 | 10.2 | 0.91
3249 | 10.7 | 0.87
3250 | 11.3 | 0.85
3251 | 11.7 | 0.76
3252 | 12.3 | 0.68
3253 | 12.4 | 0.71
3254 | 13.3 | 0.7
3255 | 13.3 | 0.72
3256 | 12.3 | 0.73
3257 | 11.8 | 0.73
3258 | 11.6 | 0.73
3259 | 11.6 | 0.76
3260 | 11.1 | 0.77
3261 | 10.4 | 0.8
3262 | 9.8 | 0.84
3263 | 9.7 | 0.87
3264 | 9.9 | 0.91
3265 | 9.6 | 0.91
3266 | 9.4 | 0.93
3267 | 9.2 | 0.95
3268 | 9.2 | 0.96
3269 | 9.1 | 0.96
3270 | 8.9 | 0.96
3271 | 9 | 0.97
3272 | 9.7 | 0.93
3273 | 10.6 | 0.89
3274 | 11.6 | 0.81
3275 | 12.8 | 0.71
3276 | 14.5 | 0.64
3277 | 14.8 | 0.64
3278 | 15.3 | 0.62
3279 | 14.6 | 0.71
3280 | 12.8 | 0.73
3281 | 14.2 | 0.7
3282 | 13 | 0.64
3283 | 12 | 0.68
3284 | 11.4 | 0.72
3285 | 10.6 | 0.82
3286 | 10.6 | 0.9
3287 | 10.2 | 0.93
3288 | 9.7 | 0.96
3289 | 9.6 | 0.96
3290 | 9.4 | 0.95
3291 | 9.3 | 0.96
3292 | 9.4 | 0.96
3293 | 9.5 | 0.96
3294 | 9.4 | 0.95
3295 | 9.4 | 0.93
3296 | 9.3 | 0.92
3297 | 10 | 0.88
3298 | 11 | 0.83
3299 | 12.4 | 0.75
3300 | 13.7 | 0.7
3301 | 13.5 | 0.63
3302 | 13.5 | 0.63
3303 | 15.4 | 0.62
3304 | 15 | 0.58
3305 | 14.8 | 0.6
3306 | 14.1 | 0.64
3307 | 12.4 | 0.73
3308 | 11.5 | 0.82
3309 | 10.9 | 0.81
3310 | 10.6 | 0.82
3311 | 10.4 | 0.82
3312 | 10 | 0.83
3313 | 9.8 | 0.86
3314 | 9.6 | 0.85
3315 | 9 | 0.86
3316 | 8.6 | 0.89
3317 | 8.3 | 0.92
3318 | 8.2 | 0.92
3319 | 8.6 | 0.9
3320 | 10.2 | 0.81
3321 | 10.8 | 0.74
3322 | 11.6 | 0.68
3323 | 12.8 | 0.61
3324 | 14.7 | 0.56
3325 | 14.7 | 0.49
3326 | 14.1 | 0.51
3327 | 14.6 | 0.48
3328 | 15.1 | 0.49
3329 | 15.8 | 0.44
3330 | 15.5 | 0.46
3331 | 15.1 | 0.46
3332 | 13.9 | 0.54
3333 | 11.8 | 0.65
3334 | 10.3 | 0.69
3335 | 9 | 0.72
3336 | 8.3 | 0.79
3337 | 7.7 | 0.83
3338 | 7.7 | 0.84
3339 | 7.6 | 0.86
3340 | 7 | 0.88
3341 | 6.9 | 0.9
3342 | 6.6 | 0.9
3343 | 7.2 | 0.88
3344 | 8.4 | 0.85
3345 | 10.4 | 0.77
3346 | 12.6 | 0.67
3347 | 13.3 | 0.6
3348 | 14.2 | 0.52
3349 | 14.4 | 0.47
3350 | 14.4 | 0.62
3351 | 15.7 | 0.59
3352 | 15.4 | 0.56
3353 | 13.6 | 0.66
3354 | 13.7 | 0.63
3355 | 13.3 | 0.7
3356 | 12.6 | 0.73
3357 | 11.7 | 0.75
3358 | 11.3 | 0.76
3359 | 10.7 | 0.77
3360 | 10.5 | 0.77
3361 | 10.3 | 0.75
3362 | 10 | 0.73
3363 | 9.4 | 0.72
3364 | 8.6 | 0.73
3365 | 8.5 | 0.71
3366 | 8.5 | 0.7
3367 | 9.6 | 0.7
3368 | 9.6 | 0.73
3369 | 10.9 | 0.7
3370 | 13.3 | 0.63
3371 | 14.8 | 0.55
3372 | 15.5 | 0.51
3373 | 16.2 | 0.48
3374 | 16.1 | 0.47
3375 | 16.5 | 0.56
3376 | 15.1 | 0.6
3377 | 15.6 | 0.59
3378 | 15 | 0.61
3379 | 13.9 | 0.58
3380 | 12.8 | 0.54
3381 | 10.5 | 0.71
3382 | 8.4 | 0.88
3383 | 7.5 | 0.91
3384 | 8.6 | 0.89
3385 | 9.4 | 0.87
3386 | 9.3 | 0.87
3387 | 9.6 | 0.87
3388 | 9.8 | 0.84
3389 | 9.8 | 0.86
3390 | 9.3 | 0.87
3391 | 10.1 | 0.87
3392 | 11.1 | 0.84
3393 | 11.4 | 0.77
3394 | 12.1 | 0.71
3395 | 12.5 | 0.74
3396 | 14.4 | 0.69
3397 | 13.1 | 0.75
3398 | 12.7 | 0.74
3399 | 14.3 | 0.67
3400 | 15.2 | 0.66
3401 | 14.1 | 0.68
3402 | 13.8 | 0.7
3403 | 12.6 | 0.76
3404 | 12.1 | 0.81
3405 | 11 | 0.85
3406 | 9.5 | 0.91
3407 | 9.7 | 0.92
3408 | 10.1 | 0.92
3409 | 9.9 | 0.95
3410 | 10.3 | 0.94
3411 | 10.3 | 0.95
3412 | 10.3 | 0.95
3413 | 10.6 | 0.95
3414 | 10.5 | 0.96
3415 | 11.3 | 0.94
3416 | 11.7 | 0.93
3417 | 12.4 | 0.87
3418 | 12.3 | 0.88
3419 | 12.6 | 0.87
3420 | 11.9 | 0.93
3421 | 12.7 | 0.86
3422 | 14.7 | 0.74
3423 | 14.9 | 0.73
3424 | 14.9 | 0.71
3425 | 15.1 | 0.72
3426 | 15.3 | 0.74
3427 | 15.4 | 0.75
3428 | 13.5 | 0.85
3429 | 13.5 | 0.85
3430 | 12.7 | 0.87
3431 | 11.9 | 0.9
3432 | 11 | 0.9
3433 | 10.2 | 0.92
3434 | 10.1 | 0.93
3435 | 10.4 | 0.95
3436 | 10.6 | 0.96
3437 | 10.3 | 0.97
3438 | 10.5 | 0.96
3439 | 11.5 | 0.93
3440 | 12.3 | 0.92
3441 | 13.2 | 0.88
3442 | 13.4 | 0.87
3443 | 13.8 | 0.86
3444 | 14.2 | 0.84
3445 | 15.4 | 0.78
3446 | 15.5 | 0.72
3447 | 15.5 | 0.72
3448 | 16 | 0.67
3449 | 16.6 | 0.61
3450 | 16.5 | 0.62
3451 | 16.8 | 0.63
3452 | 15.7 | 0.65
3453 | 15.1 | 0.68
3454 | 14.6 | 0.72
3455 | 14.4 | 0.74
3456 | 13.4 | 0.85
3457 | 13 | 0.86
3458 | 12.8 | 0.85
3459 | 12.7 | 0.86
3460 | 12.4 | 0.89
3461 | 12.7 | 0.89
3462 | 12.6 | 0.92
3463 | 12.6 | 0.95
3464 | 13.2 | 0.93
3465 | 14.2 | 0.88
3466 | 16.2 | 0.76
3467 | 17.3 | 0.66
3468 | 17.7 | 0.67
3469 | 17.5 | 0.7
3470 | 17.1 | 0.74
3471 | 19 | 0.69
3472 | 19.5 | 0.7
3473 | 19.2 | 0.7
3474 | 20 | 0.67
3475 | 18.6 | 0.71
3476 | 17.3 | 0.73
3477 | 16.4 | 0.75
3478 | 15.1 | 0.84
3479 | 13.5 | 0.93
3480 | 13.5 | 0.94
3481 | 13.1 | 0.98
3482 | 13 | 0.98
3483 | 12.9 | 0.99
3484 | 13 | 0.98
3485 | 13.1 | 0.98
3486 | 13 | 0.98
3487 | 13.2 | 0.98
3488 | 14 | 0.94
3489 | 13.9 | 0.84
3490 | 12.8 | 0.77
3491 | 13.7 | 0.66
3492 | 14.7 | 0.61
3493 | 15.7 | 0.58
3494 | 15.8 | 0.56
3495 | 16.7 | 0.55
3496 | 16.8 | 0.51
3497 | 16.5 | 0.54
3498 | 15.8 | 0.54
3499 | 14.7 | 0.58
3500 | 14 | 0.63
3501 | 13.3 | 0.66
3502 | 12.5 | 0.72
3503 | 11.4 | 0.77
3504 | 10.3 | 0.82
3505 | 10.5 | 0.83
3506 | 10.7 | 0.89
3507 | 11 | 0.83
3508 | 10.7 | 0.8
3509 | 9.4 | 0.87
3510 | 9.5 | 0.84
3511 | 10.9 | 0.78
3512 | 11.4 | 0.77
3513 | 11.9 | 0.74
3514 | 13.3 | 0.67
3515 | 13.2 | 0.58
3516 | 14.6 | 0.58
3517 | 14.1 | 0.65
3518 | 15.5 | 0.59
3519 | 13.2 | 0.67
3520 | 12 | 0.76
3521 | 13.9 | 0.63
3522 | 12.8 | 0.62
3523 | 12.9 | 0.59
3524 | 11.8 | 0.65
3525 | 10.9 | 0.7
3526 | 10.2 | 0.76
3527 | 9.6 | 0.79
3528 | 9.3 | 0.83
3529 | 8.9 | 0.88
3530 | 8.8 | 0.86
3531 | 8.7 | 0.85
3532 | 9.2 | 0.84
3533 | 8.7 | 0.88
3534 | 8.4 | 0.86
3535 | 8.7 | 0.84
3536 | 10.1 | 0.77
3537 | 10.6 | 0.75
3538 | 11.8 | 0.66
3539 | 12.9 | 0.56
3540 | 13.4 | 0.55
3541 | 13.6 | 0.54
3542 | 14.3 | 0.5
3543 | 13.9 | 0.53
3544 | 14.8 | 0.51
3545 | 12.6 | 0.69
3546 | 13.1 | 0.69
3547 | 13.3 | 0.73
3548 | 12.6 | 0.74
3549 | 10.8 | 0.87
3550 | 9 | 0.92
3551 | 8.6 | 0.96
3552 | 8.9 | 0.97
3553 | 9.1 | 0.99
3554 | 9.8 | 0.99
3555 | 11.3 | 0.99
3556 | 11.4 | 0.99
3557 | 11.1 | 0.99
3558 | 11.6 | 0.99
3559 | 12.6 | 0.98
3560 | 13.1 | 0.96
3561 | 13.6 | 0.94
3562 | 14.6 | 0.91
3563 | 15.3 | 0.86
3564 | 15.4 | 0.93
3565 | 16.1 | 0.85
3566 | 15.8 | 0.87
3567 | 15.3 | 0.88
3568 | 16 | 0.84
3569 | 15.7 | 0.84
3570 | 15.5 | 0.87
3571 | 15.6 | 0.88
3572 | 14.8 | 0.88
3573 | 14.1 | 0.9
3574 | 13.3 | 0.91
3575 | 13 | 0.93
3576 | 13.3 | 0.93
3577 | 13.5 | 0.93
3578 | 13.3 | 0.94
3579 | 13.4 | 0.94
3580 | 13.3 | 0.93
3581 | 13.1 | 0.94
3582 | 12.9 | 0.94
3583 | 13.6 | 0.92
3584 | 15 | 0.86
3585 | 14.7 | 0.89
3586 | 15.4 | 0.86
3587 | 14.8 | 0.89
3588 | 15.6 | 0.86
3589 | 15.5 | 0.86
3590 | 17.2 | 0.8
3591 | 17.3 | 0.83
3592 | 17.4 | 0.76
3593 | 16.7 | 0.77
3594 | 16.1 | 0.82
3595 | 14.9 | 0.92
3596 | 14.4 | 0.94
3597 | 13.7 | 0.98
3598 | 13.4 | 1
3599 | 13.1 | 1
3600 | 13.1 | 0.99
3601 | 12.9 | 1
3602 | 12.8 | 0.99
3603 | 12.8 | 1
3604 | 12.7 | 1
3605 | 12.7 | 1
3606 | 12.7 | 1
3607 | 12.8 | 0.99
3608 | 12.5 | 1
3609 | 12.4 | 0.99
3610 | 12.3 | 0.95
3611 | 12.6 | 0.96
3612 | 13.5 | 0.9
3613 | 13 | 0.95
3614 | 13.2 | 0.93
3615 | 13.2 | 0.95
3616 | 13 | 0.98
3617 | 13.7 | 0.97
3618 | 14.8 | 0.9
3619 | 15 | 0.87
3620 | 14.8 | 0.86
3621 | 13.4 | 0.91
3622 | 11.5 | 0.93
3623 | 10.2 | 0.96
3624 | 9.4 | 0.99
3625 | 9.1 | 1
3626 | 10.1 | 0.99
3627 | 10.4 | 1
3628 | 10.6 | 1
3629 | 10.6 | 1
3630 | 10.9 | 0.99
3631 | 11 | 0.99
3632 | 11.4 | 1
3633 | 11.9 | 1
3634 | 12.6 | 1
3635 | 12.7 | 0.99
3636 | 14 | 0.92
3637 | 14.6 | 0.9
3638 | 14.3 | 0.93
3639 | 14 | 0.99
3640 | 14.1 | 0.98
3641 | 14 | 0.99
3642 | 13.9 | 0.99
3643 | 13.5 | 0.99
3644 | 13.3 | 0.99
3645 | 12.7 | 1
3646 | 12.6 | 1
3647 | 12.5 | 0.99
3648 | 12.9 | 0.99
3649 | 12.9 | 0.99
3650 | 13.1 | 1
3651 | 13.3 | 0.99
3652 | 13.6 | 0.99
3653 | 12.9 | 0.99
3654 | 12.2 | 0.95
3655 | 11.8 | 0.96
3656 | 12.1 | 0.95
3657 | 12.4 | 0.8
3658 | 13.4 | 0.72
3659 | 14.3 | 0.68
3660 | 13.9 | 0.65
3661 | 15 | 0.61
3662 | 13 | 0.73
3663 | 13.2 | 0.75
3664 | 13.1 | 0.85
3665 | 14.3 | 0.72
3666 | 14 | 0.67
3667 | 13.4 | 0.68
3668 | 13 | 0.69
3669 | 11.4 | 0.76
3670 | 10 | 0.76
3671 | 9.2 | 0.84
3672 | 8.2 | 0.92
3673 | 8.3 | 0.94
3674 | 8.2 | 0.96
3675 | 7.7 | 0.96
3676 | 6.9 | 0.97
3677 | 6.7 | 0.96
3678 | 7.2 | 0.94
3679 | 8.5 | 0.93
3680 | 10.2 | 0.88
3681 | 11.8 | 0.75
3682 | 11.8 | 0.7
3683 | 12.8 | 0.7
3684 | 12 | 0.75
3685 | 14.1 | 0.68
3686 | 10.7 | 0.85
3687 | 12.6 | 0.68
3688 | 12.6 | 0.77
3689 | 12.9 | 0.7
3690 | 12.6 | 0.77
3691 | 12.8 | 0.71
3692 | 11.3 | 0.79
3693 | 10.8 | 0.85
3694 | 10.1 | 0.92
3695 | 9.6 | 0.93
3696 | 9.9 | 0.95
3697 | 10.1 | 0.99
3698 | 9.9 | 0.99
3699 | 9.8 | 0.97
3700 | 9.6 | 0.97
3701 | 9.8 | 0.99
3702 | 9.5 | 0.99
3703 | 9.5 | 0.99
3704 | 9.6 | 0.97
3705 | 9.6 | 0.96
3706 | 9.6 | 0.95
3707 | 9.6 | 0.95
3708 | 10.4 | 0.92
3709 | 11.5 | 0.83
3710 | 11.5 | 0.73
3711 | 12 | 0.72
3712 | 12.6 | 0.68
3713 | 12.4 | 0.67
3714 | 11.9 | 0.71
3715 | 11.2 | 0.74
3716 | 11.1 | 0.73
3717 | 9 | 0.89
3718 | 9 | 0.88
3719 | 8.4 | 0.89
3720 | 8.4 | 0.9
3721 | 8.4 | 0.82
3722 | 8.2 | 0.9
3723 | 8.1 | 0.92
3724 | 8.2 | 0.92
3725 | 7.8 | 0.93
3726 | 7.7 | 0.9
3727 | 8.1 | 0.86
3728 | 9.7 | 0.82
3729 | 10.5 | 0.76
3730 | 11.5 | 0.68
3731 | 11.4 | 0.67
3732 | 13.6 | 0.59
3733 | 13.2 | 0.57
3734 | 13.1 | 0.58
3735 | 11.9 | 0.66
3736 | 10.5 | 0.79
3737 | 10.2 | 0.8
3738 | 8.9 | 0.89
3739 | 9.4 | 0.87
3740 | 9.3 | 0.91
3741 | 8.3 | 0.93
3742 | 8.1 | 0.96
3743 | 8.6 | 0.86
3744 | 8.3 | 0.82
3745 | 8 | 0.83
3746 | 7.3 | 0.88
3747 | 6.7 | 0.9
3748 | 6.3 | 0.91
3749 | 5.9 | 0.92
3750 | 5.9 | 0.92
3751 | 6.9 | 0.88
3752 | 8.3 | 0.86
3753 | 9.4 | 0.8
3754 | 10.9 | 0.73
3755 | 12.2 | 0.62
3756 | 11.5 | 0.53
3757 | 11.4 | 0.59
3758 | 11.2 | 0.71
3759 | 12.8 | 0.66
3760 | 13.4 | 0.62
3761 | 13.3 | 0.62
3762 | 12.8 | 0.67
3763 | 11.4 | 0.71
3764 | 11.2 | 0.72
3765 | 10.4 | 0.73
3766 | 9.3 | 0.79
3767 | 8.5 | 0.82
3768 | 8.3 | 0.82
3769 | 7.9 | 0.86
3770 | 7.7 | 0.87
3771 | 6.6 | 0.93
3772 | 6.4 | 0.95
3773 | 6.3 | 0.92
3774 | 6.8 | 0.9
3775 | 7.9 | 0.84
3776 | 8.9 | 0.82
3777 | 10.1 | 0.74
3778 | 11.8 | 0.69
3779 | 13.4 | 0.63
3780 | 13.5 | 0.64
3781 | 14.6 | 0.61
3782 | 15.3 | 0.6
3783 | 14.6 | 0.65
3784 | 12.7 | 0.8
3785 | 13.9 | 0.7
3786 | 13.3 | 0.72
3787 | 13.6 | 0.67
3788 | 13.1 | 0.68
3789 | 12.1 | 0.71
3790 | 10.4 | 0.75
3791 | 9.4 | 0.81
3792 | 8.8 | 0.84
3793 | 8.3 | 0.87
3794 | 8.2 | 0.87
3795 | 8 | 0.87
3796 | 7.8 | 0.89
3797 | 7.9 | 0.89
3798 | 7.9 | 0.9
3799 | 8.9 | 0.85
3800 | 9.9 | 0.81
3801 | 10.8 | 0.75
3802 | 11.2 | 0.73
3803 | 12.8 | 0.65
3804 | 13.6 | 0.63
3805 | 12.3 | 0.74
3806 | 14.2 | 0.6
3807 | 14.5 | 0.5
3808 | 14.7 | 0.57
3809 | 14.5 | 0.57
3810 | 14.6 | 0.57
3811 | 13.8 | 0.6
3812 | 12.9 | 0.67
3813 | 11.9 | 0.66
3814 | 10.8 | 0.73
3815 | 9.5 | 0.76
3816 | 8.1 | 0.86
3817 | 8.7 | 0.89
3818 | 8.2 | 0.89
3819 | 7.1 | 0.91
3820 | 7.6 | 0.91
3821 | 6 | 0.92
3822 | 6.8 | 0.94
3823 | 8.5 | 0.94
3824 | 10.1 | 0.86
3825 | 11.5 | 0.82
3826 | 11.8 | 0.71
3827 | 12.5 | 0.79
3828 | 11.1 | 0.86
3829 | 8.7 | 0.92
3830 | 13.1 | 0.8
3831 | 10 | 0.81
3832 | 10.5 | 0.9
3833 | 10.3 | 0.83
3834 | 12.2 | 0.77
3835 | 11 | 0.8
3836 | 11 | 0.79
3837 | 9.9 | 0.87
3838 | 8.7 | 0.93
3839 | 8.3 | 0.9
3840 | 8.2 | 0.93
3841 | 8.7 | 0.9
3842 | 8 | 0.94
3843 | 7.7 | 0.96
3844 | 7.2 | 0.97
3845 | 6.7 | 0.94
3846 | 6.3 | 0.97
3847 | 7.5 | 0.9
3848 | 8.4 | 0.89
3849 | 10 | 0.83
3850 | 11.6 | 0.7
3851 | 12.8 | 0.66
3852 | 13.3 | 0.63
3853 | 13.7 | 0.57
3854 | 14.6 | 0.58
3855 | 15.1 | 0.54
3856 | 15.6 | 0.52
3857 | 12.5 | 0.65
3858 | 13.8 | 0.72
3859 | 13.5 | 0.69
3860 | 13.1 | 0.69
3861 | 12.8 | 0.71
3862 | 11.3 | 0.82
3863 | 11.1 | 0.77
3864 | 10.1 | 0.83
3865 | 9.7 | 0.83
3866 | 9.2 | 0.85
3867 | 8.9 | 0.86
3868 | 8.1 | 0.9
3869 | 7.4 | 0.9
3870 | 7.7 | 0.87
3871 | 8.6 | 0.85
3872 | 9.1 | 0.8
3873 | 9.9 | 0.75
3874 | 10.7 | 0.74
3875 | 12.4 | 0.65
3876 | 13.5 | 0.61
3877 | 14.7 | 0.56
3878 | 15 | 0.55
3879 | 15.2 | 0.54
3880 | 15.6 | 0.5
3881 | 15.9 | 0.5
3882 | 15.6 | 0.5
3883 | 14.9 | 0.53
3884 | 14 | 0.57
3885 | 13.1 | 0.69
3886 | 10.9 | 0.89
3887 | 10.6 | 0.89
3888 | 10.6 | 0.86
3889 | 10.5 | 0.86
3890 | 10.4 | 0.85
3891 | 9.1 | 0.89
3892 | 8.8 | 0.88
3893 | 8 | 0.9
3894 | 8.6 | 0.88
3895 | 9 | 0.88
3896 | 9.1 | 0.89
3897 | 10.3 | 0.83
3898 | 10.5 | 0.83
3899 | 11.1 | 0.79
3900 | 11.9 | 0.71
3901 | 11.2 | 0.77
3902 | 10.9 | 0.79
3903 | 11.4 | 0.76
3904 | 11.3 | 0.74
3905 | 11.6 | 0.75
3906 | 11.9 | 0.75
3907 | 11.8 | 0.76
3908 | 11.5 | 0.77
3909 | 10.8 | 0.85
3910 | 10.5 | 0.85
3911 | 10.4 | 0.85
3912 | 10 | 0.95
3913 | 9.8 | 0.95
3914 | 9.6 | 0.92
3915 | 9.3 | 0.93
3916 | 9.2 | 0.93
3917 | 9.2 | 0.96
3918 | 9.3 | 0.96
3919 | 9.6 | 0.96
3920 | 9.9 | 0.95
3921 | 10.2 | 0.92
3922 | 10.4 | 0.91
3923 | 11.5 | 0.86
3924 | 11.4 | 0.89
3925 | 10.5 | 0.92
3926 | 11.8 | 0.81
3927 | 11.4 | 0.78
3928 | 10.7 | 0.81
3929 | 12 | 0.74
3930 | 12 | 0.66
3931 | 11.4 | 0.64
3932 | 11.1 | 0.67
3933 | 10.8 | 0.69
3934 | 10.2 | 0.75
3935 | 9.9 | 0.78
3936 | 8.8 | 0.84
3937 | 8.9 | 0.84
3938 | 7.2 | 0.91
3939 | 7.8 | 0.93
3940 | 8.7 | 0.85
3941 | 8.3 | 0.92
3942 | 7.5 | 0.96
3943 | 9 | 0.95
3944 | 10.2 | 0.92
3945 | 10.6 | 0.94
3946 | 11.1 | 0.96
3947 | 12.3 | 0.81
3948 | 12.2 | 0.74
3949 | 12.7 | 0.68
3950 | 12.4 | 0.64
3951 | 12.5 | 0.64
3952 | 10.4 | 0.86
3953 | 10.2 | 0.96
3954 | 10 | 0.95
3955 | 9.8 | 0.91
3956 | 9.8 | 0.86
3957 | 9.7 | 0.87
3958 | 9.8 | 0.87
3959 | 9.4 | 0.91
3960 | 8.7 | 0.96
3961 | 8.4 | 0.88
3962 | 7.7 | 0.87
3963 | 7.6 | 0.86
3964 | 7.2 | 0.84
3965 | 7.6 | 0.86
3966 | 7.5 | 0.86
3967 | 7.9 | 0.83
3968 | 9.5 | 0.78
3969 | 11 | 0.73
3970 | 11.8 | 0.66
3971 | 13.3 | 0.58
3972 | 13.1 | 0.68
3973 | 12.9 | 0.67
3974 | 11.9 | 0.68
3975 | 12.7 | 0.62
3976 | 13.4 | 0.63
3977 | 12.4 | 0.7
3978 | 12.3 | 0.66
3979 | 12.7 | 0.7
3980 | 11.2 | 0.72
3981 | 10.3 | 0.83
3982 | 7.9 | 0.89
3983 | 7.8 | 0.93
3984 | 7.6 | 0.96
3985 | 7.2 | 0.97
3986 | 7.9 | 0.96
3987 | 8.2 | 0.96
3988 | 8.6 | 0.93
3989 | 9 | 0.95
3990 | 9.2 | 0.96
3991 | 9.6 | 0.96
3992 | 11.2 | 0.92
3993 | 11.9 | 0.85
3994 | 11.9 | 0.85
3995 | 13.5 | 0.76
3996 | 13.9 | 0.83
3997 | 12.5 | 0.94
3998 | 12.2 | 0.99
3999 | 12.9 | 0.98
4000 | 14.2 | 0.89
4001 | 15.1 | 0.82
4002 | 15.2 | 0.75
4003 | 13.1 | 0.84
4004 | 12.7 | 0.79
4005 | 12 | 0.82
4006 | 10.5 | 0.92
4007 | 10.5 | 0.96
4008 | 10.2 | 0.95
4009 | 9.9 | 0.97
4010 | 9.7 | 0.96
4011 | 9.9 | 0.97
4012 | 9.7 | 0.96
4013 | 9.7 | 0.97
4014 | 10 | 0.97
4015 | 10.8 | 0.96
4016 | 12 | 0.91
4017 | 12.9 | 0.84
4018 | 13.2 | 0.79
4019 | 12.4 | 0.85
4020 | 13.7 | 0.83
4021 | 14 | 0.75
4022 | 14.6 | 0.73
4023 | 14.4 | 0.77
4024 | 14.3 | 0.78
4025 | 15.6 | 0.7
4026 | 15.4 | 0.69
4027 | 14.3 | 0.77
4028 | 13.7 | 0.78
4029 | 12.8 | 0.82
4030 | 10.5 | 0.88
4031 | 9.1 | 0.95
4032 | 9 | 0.96
4033 | 9.2 | 0.97
4034 | 9.5 | 0.96
4035 | 8.2 | 0.96
4036 | 9.1 | 0.96
4037 | 8.8 | 0.97
4038 | 8.6 | 0.97
4039 | 9.2 | 0.96
4040 | 9.9 | 0.93
4041 | 11.1 | 0.89
4042 | 12.5 | 0.86
4043 | 14.6 | 0.71
4044 | 15.6 | 0.61
4045 | 16.4 | 0.66
4046 | 14.8 | 0.71
4047 | 14.5 | 0.67
4048 | 15.4 | 0.71
4049 | 16 | 0.65
4050 | 15.4 | 0.75
4051 | 15 | 0.73
4052 | 14.1 | 0.78
4053 | 12.9 | 0.85
4054 | 13.1 | 0.79
4055 | 12.4 | 0.74
4056 | 11.5 | 0.76
4057 | 10.9 | 0.81
4058 | 10.3 | 0.86
4059 | 9.8 | 0.87
4060 | 9.1 | 0.91
4061 | 9.1 | 0.91
4062 | 8.9 | 0.92
4063 | 9.9 | 0.88
4064 | 10.9 | 0.84
4065 | 12.3 | 0.8
4066 | 13.9 | 0.72
4067 | 16.1 | 0.62
4068 | 15.9 | 0.58
4069 | 15.4 | 0.64
4070 | 15.9 | 0.58
4071 | 16 | 0.62
4072 | 14.7 | 0.71
4073 | 14.4 | 0.8
4074 | 14.9 | 0.67
4075 | 15.2 | 0.65
4076 | 13.1 | 0.68
4077 | 12.6 | 0.74
4078 | 10.9 | 0.81
4079 | 10.4 | 0.81
4080 | 9.7 | 0.87
4081 | 9.5 | 0.87
4082 | 9 | 0.9
4083 | 9.3 | 0.91
4084 | 8.6 | 0.9
4085 | 8.9 | 0.89
4086 | 8.9 | 0.88
4087 | 9.1 | 0.89
4088 | 11 | 0.81
4089 | 12 | 0.75
4090 | 12.7 | 0.65
4091 | 12.5 | 0.69
4092 | 14.3 | 0.61
4093 | 12.1 | 0.82
4094 | 14.6 | 0.59
4095 | 15 | 0.67
4096 | 14.9 | 0.58
4097 | 14.8 | 0.54
4098 | 15.6 | 0.56
4099 | 15.1 | 0.56
4100 | 14 | 0.6
4101 | 13.2 | 0.63
4102 | 11.6 | 0.7
4103 | 10.6 | 0.74
4104 | 9.9 | 0.75
4105 | 8.8 | 0.8
4106 | 8.9 | 0.78
4107 | 8 | 0.83
4108 | 8 | 0.86
4109 | 7.6 | 0.86
4110 | 8.2 | 0.83
4111 | 9.1 | 0.8
4112 | 10.5 | 0.76
4113 | 12.2 | 0.69
4114 | 13 | 0.63
4115 | 14.2 | 0.64
4116 | 14.4 | 0.63
4117 | 15 | 0.62
4118 | 14.3 | 0.68
4119 | 14.9 | 0.7
4120 | 14.8 | 0.71
4121 | 14.3 | 0.76
4122 | 13.7 | 0.83
4123 | 13.6 | 0.85
4124 | 14 | 0.8
4125 | 12.5 | 0.86
4126 | 11.2 | 0.92
4127 | 10.4 | 0.96
4128 | 10.3 | 0.95
4129 | 10.3 | 0.96
4130 | 10.1 | 0.96
4131 | 10.6 | 0.99
4132 | 10.8 | 0.99
4133 | 10.9 | 0.99
4134 | 11.5 | 0.99
4135 | 12 | 0.99
4136 | 12.6 | 0.94
4137 | 13.8 | 0.86
4138 | 13.8 | 0.84
4139 | 14.4 | 0.82
4140 | 15.7 | 0.73
4141 | 15.4 | 0.77
4142 | 14.4 | 0.78
4143 | 14.9 | 0.75
4144 | 15.1 | 0.77
4145 | 14.2 | 0.79
4146 | 13.8 | 0.8
4147 | 13.7 | 0.81
4148 | 13.6 | 0.84
4149 | 13.4 | 0.86
4150 | 12.9 | 0.91
4151 | 12.7 | 0.92
4152 | 12.6 | 0.94
4153 | 13.3 | 0.92
4154 | 13.5 | 0.88
4155 | 13.6 | 0.86
4156 | 13.3 | 0.88
4157 | 13.1 | 0.91
4158 | 13 | 0.92
4159 | 12.7 | 0.94
4160 | 12.7 | 0.95
4161 | 12.9 | 0.96
4162 | 13 | 0.99
4163 | 13 | 0.98
4164 | 13.1 | 0.98
4165 | 13.1 | 0.99
4166 | 13.2 | 0.98
4167 | 13.3 | 1
4168 | 13.5 | 0.99
4169 | 13.6 | 0.99
4170 | 13.5 | 0.99
4171 | 13.5 | 1
4172 | 13.5 | 0.99
4173 | 13.6 | 1
4174 | 13.6 | 0.99
4175 | 13.8 | 0.99
4176 | 13.8 | 0.99
4177 | 13.8 | 1
4178 | 13.9 | 0.99
4179 | 13.9 | 0.99
4180 | 13.8 | 0.99
4181 | 13.7 | 1
4182 | 13.7 | 0.99
4183 | 13.9 | 0.99
4184 | 14.3 | 0.98
4185 | 14.4 | 0.97
4186 | 17.1 | 0.81
4187 | 15.8 | 0.87
4188 | 16.8 | 0.78
4189 | 17 | 0.79
4190 | 17.8 | 0.75
4191 | 18.2 | 0.76
4192 | 18.4 | 0.72
4193 | 19.1 | 0.71
4194 | 19.6 | 0.68
4195 | 19.4 | 0.71
4196 | 17.9 | 0.82
4197 | 16.1 | 0.87
4198 | 14.1 | 0.94
4199 | 16.1 | 0.85
4200 | 15.3 | 0.85
4201 | 14.6 | 0.9
4202 | 14.4 | 0.9
4203 | 14.4 | 0.9
4204 | 13.9 | 0.93
4205 | 14.1 | 0.95
4206 | 14 | 0.97
4207 | 14.3 | 0.97
4208 | 14.8 | 0.94
4209 | 15.8 | 0.9
4210 | 16.4 | 0.88
4211 | 16.3 | 0.86
4212 | 16.8 | 0.87
4213 | 17.5 | 0.84
4214 | 18.8 | 0.84
4215 | 18.8 | 0.79
4216 | 18.5 | 0.83
4217 | 19.3 | 0.81
4218 | 19.3 | 0.78
4219 | 18.2 | 0.83
4220 | 18.1 | 0.82
4221 | 17 | 0.88
4222 | 16.5 | 0.86
4223 | 16.5 | 0.88
4224 | 15.9 | 0.9
4225 | 15.3 | 0.93
4226 | 14.9 | 0.92
4227 | 14.6 | 0.94
4228 | 14.7 | 0.96
4229 | 14.3 | 0.93
4230 | 14.3 | 0.93
4231 | 14.6 | 0.89
4232 | 15.6 | 0.83
4233 | 17.3 | 0.76
4234 | 17.7 | 0.76
4235 | 18 | 0.77
4236 | 18.8 | 0.75
4237 | 18.7 | 0.75
4238 | 18.5 | 0.73
4239 | 19.3 | 0.74
4240 | 19.1 | 0.72
4241 | 17.6 | 0.84
4242 | 18.4 | 0.82
4243 | 18.9 | 0.8
4244 | 18.9 | 0.74
4245 | 17.8 | 0.76
4246 | 16.9 | 0.78
4247 | 16.1 | 0.74
4248 | 15.5 | 0.74
4249 | 15.2 | 0.81
4250 | 15.4 | 0.84
4251 | 15 | 0.88
4252 | 14.8 | 0.89
4253 | 14.5 | 0.9
4254 | 14.9 | 0.87
4255 | 15.1 | 0.84
4256 | 16.1 | 0.78
4257 | 16.5 | 0.75
4258 | 17.3 | 0.71
4259 | 18.6 | 0.69
4260 | 19.3 | 0.68
4261 | 20.6 | 0.62
4262 | 21 | 0.59
4263 | 21.6 | 0.57
4264 | 22.2 | 0.55
4265 | 23.3 | 0.54
4266 | 22.1 | 0.55
4267 | 21.2 | 0.53
4268 | 20.5 | 0.56
4269 | 18.7 | 0.63
4270 | 17.2 | 0.7
4271 | 17.6 | 0.7
4272 | 17.6 | 0.72
4273 | 17.6 | 0.73
4274 | 17 | 0.76
4275 | 16.9 | 0.76
4276 | 16.2 | 0.79
4277 | 15.8 | 0.81
4278 | 15.4 | 0.83
4279 | 15.3 | 0.83
4280 | 15.3 | 0.84
4281 | 15 | 0.86
4282 | 14.7 | 0.89
4283 | 14.1 | 0.97
4284 | 14.3 | 0.98
4285 | 14.3 | 0.99
4286 | 14.7 | 0.99
4287 | 14.9 | 0.99
4288 | 15.1 | 0.99
4289 | 15.4 | 0.99
4290 | 15.6 | 0.99
4291 | 15.5 | 0.98
4292 | 15.6 | 0.98
4293 | 15 | 0.97
4294 | 14 | 0.97
4295 | 13.4 | 0.95
4296 | 13.4 | 0.96
4297 | 13.1 | 0.98
4298 | 13.3 | 0.98
4299 | 13.4 | 0.99
4300 | 13.6 | 1
4301 | 13.6 | 1
4302 | 13.8 | 0.99
4303 | 14.1 | 0.99
4304 | 14.2 | 0.98
4305 | 14.6 | 0.98
4306 | 15.8 | 0.81
4307 | 17.7 | 0.75
4308 | 17 | 0.79
4309 | 17.9 | 0.75
4310 | 17.9 | 0.71
4311 | 17.8 | 0.77
4312 | 17 | 0.79
4313 | 16.5 | 0.83
4314 | 17.2 | 0.79
4315 | 16.4 | 0.85
4316 | 15.7 | 0.89
4317 | 15.1 | 0.91
4318 | 14.6 | 0.92
4319 | 14.2 | 0.94
4320 | 13.3 | 0.93
4321 | 12.4 | 0.95
4322 | 12.7 | 0.96
4323 | 13.1 | 0.94
4324 | 12.7 | 0.95
4325 | 13.3 | 0.94
4326 | 13.4 | 0.93
4327 | 13.5 | 0.91
4328 | 13.9 | 0.88
4329 | 14.6 | 0.86
4330 | 15.4 | 0.81
4331 | 15.9 | 0.81
4332 | 15.8 | 0.78
4333 | 16.5 | 0.76
4334 | 14.7 | 0.92
4335 | 17.8 | 0.78
4336 | 17.1 | 0.76
4337 | 17.8 | 0.66
4338 | 16.4 | 0.7
4339 | 17 | 0.62
4340 | 15.2 | 0.62
4341 | 14.3 | 0.65
4342 | 13.2 | 0.69
4343 | 12.7 | 0.77
4344 | 12 | 0.81
4345 | 11.4 | 0.83
4346 | 12 | 0.81
4347 | 12.1 | 0.8
4348 | 11.8 | 0.82
4349 | 12.1 | 0.82
4350 | 12 | 0.83
4351 | 12.2 | 0.83
4352 | 12.6 | 0.81
4353 | 13.4 | 0.79
4354 | 13.7 | 0.74
4355 | 16.1 | 0.62
4356 | 16.5 | 0.59
4357 | 17.3 | 0.59
4358 | 17.5 | 0.6
4359 | 18.3 | 0.55
4360 | 18.5 | 0.55
4361 | 18.1 | 0.56
4362 | 18 | 0.55
4363 | 17.3 | 0.58
4364 | 16.1 | 0.62
4365 | 14.6 | 0.67
4366 | 13 | 0.74
4367 | 11.9 | 0.78
4368 | 11.4 | 0.8
4369 | 11 | 0.84
4370 | 10.7 | 0.84
4371 | 10.4 | 0.86
4372 | 10.4 | 0.88
4373 | 10.2 | 0.91
4374 | 9.9 | 0.92
4375 | 10.7 | 0.91
4376 | 11.8 | 0.87
4377 | 13.5 | 0.78
4378 | 15.1 | 0.66
4379 | 15.3 | 0.63
4380 | 16.4 | 0.58
4381 | 16.4 | 0.56
4382 | 16.9 | 0.55
4383 | 16 | 0.73
4384 | 15 | 0.78
4385 | 15 | 0.74
4386 | 15.4 | 0.74
4387 | 15.3 | 0.73
4388 | 14.9 | 0.77
4389 | 14.2 | 0.8
4390 | 13.8 | 0.81
4391 | 14.6 | 0.7
4392 | 14.2 | 0.66
4393 | 13.9 | 0.68
4394 | 13.4 | 0.73
4395 | 12.8 | 0.77
4396 | 12.8 | 0.78
4397 | 12.3 | 0.83
4398 | 12.6 | 0.78
4399 | 12.8 | 0.78
4400 | 13.2 | 0.78
4401 | 13.9 | 0.72
4402 | 15.2 | 0.67
4403 | 15.6 | 0.65
4404 | 16.7 | 0.65
4405 | 16 | 0.7
4406 | 17.2 | 0.68
4407 | 17.5 | 0.7
4408 | 17.7 | 0.7
4409 | 17.3 | 0.7
4410 | 16.5 | 0.71
4411 | 16 | 0.73
4412 | 15.1 | 0.72
4413 | 13.7 | 0.79
4414 | 11.6 | 0.83
4415 | 11.1 | 0.85
4416 | 11.1 | 0.84
4417 | 11.3 | 0.83
4418 | 11.8 | 0.82
4419 | 11.7 | 0.83
4420 | 11.1 | 0.89
4421 | 10.2 | 0.92
4422 | 10.4 | 0.92
4423 | 11.1 | 0.87
4424 | 12.5 | 0.82
4425 | 14.3 | 0.75
4426 | 16.1 | 0.65
4427 | 17.8 | 0.62
4428 | 19.2 | 0.58
4429 | 19.8 | 0.58
4430 | 20.6 | 0.55
4431 | 20 | 0.69
4432 | 20.3 | 0.68
4433 | 20.7 | 0.67
4434 | 19.8 | 0.7
4435 | 18.7 | 0.71
4436 | 19.9 | 0.59
4437 | 18.1 | 0.58
4438 | 15.8 | 0.6
4439 | 14.3 | 0.73
4440 | 13.5 | 0.76
4441 | 12.8 | 0.84
4442 | 12.5 | 0.86
4443 | 12.3 | 0.88
4444 | 12.1 | 0.88
4445 | 11.9 | 0.89
4446 | 11.6 | 0.89
4447 | 12 | 0.88
4448 | 13.1 | 0.83
4449 | 14.8 | 0.74
4450 | 15.2 | 0.72
4451 | 17.6 | 0.61
4452 | 18.6 | 0.6
4453 | 19.8 | 0.57
4454 | 20.4 | 0.55
4455 | 21.5 | 0.57
4456 | 22.3 | 0.53
4457 | 22.6 | 0.54
4458 | 22 | 0.56
4459 | 21.7 | 0.56
4460 | 20 | 0.65
4461 | 18.6 | 0.7
4462 | 16.4 | 0.77
4463 | 15.3 | 0.82
4464 | 14.7 | 0.84
4465 | 14.3 | 0.86
4466 | 13.8 | 0.9
4467 | 13.5 | 0.87
4468 | 13.2 | 0.86
4469 | 12.8 | 0.87
4470 | 12.3 | 0.89
4471 | 13 | 0.86
4472 | 13.9 | 0.83
4473 | 14.5 | 0.82
4474 | 14.9 | 0.8
4475 | 16.4 | 0.76
4476 | 16.9 | 0.78
4477 | 18.3 | 0.73
4478 | 18.7 | 0.71
4479 | 18.9 | 0.74
4480 | 18.7 | 0.73
4481 | 18 | 0.84
4482 | 18.7 | 0.77
4483 | 17.6 | 0.89
4484 | 17.5 | 0.86
4485 | 17 | 0.88
4486 | 16.3 | 0.85
4487 | 16 | 0.87
4488 | 15.6 | 0.88
4489 | 15.2 | 0.88
4490 | 15 | 0.9
4491 | 14.8 | 0.85
4492 | 14.6 | 0.91
4493 | 14.4 | 0.91
4494 | 14.4 | 0.92
4495 | 14.6 | 0.91
4496 | 15.1 | 0.9
4497 | 15.1 | 0.89
4498 | 15.6 | 0.86
4499 | 16.3 | 0.84
4500 | 16.8 | 0.82
4501 | 16.5 | 0.86
4502 | 16.3 | 0.91
4503 | 15.5 | 0.97
4504 | 14.9 | 0.98
4505 | 15.1 | 0.98
4506 | 15 | 0.98
4507 | 14.9 | 0.98
4508 | 14.9 | 0.98
4509 | 14.7 | 0.99
4510 | 14.6 | 0.99
4511 | 14.5 | 0.99
4512 | 14.5 | 0.99
4513 | 14.5 | 0.99
4514 | 14.5 | 0.99
4515 | 14.5 | 0.99
4516 | 14.7 | 0.99
4517 | 14.8 | 0.99
4518 | 14.9 | 1
4519 | 14.9 | 0.99
4520 | 15.3 | 0.99
4521 | 15.6 | 0.98
4522 | 16.8 | 0.92
4523 | 17.5 | 0.89
4524 | 17.7 | 0.88
4525 | 17.7 | 0.87
4526 | 17.9 | 0.88
4527 | 18.8 | 0.74
4528 | 19.2 | 0.76
4529 | 20.1 | 0.72
4530 | 19.3 | 0.73
4531 | 18.9 | 0.74
4532 | 17.2 | 0.8
4533 | 16.7 | 0.84
4534 | 15.5 | 0.9
4535 | 14 | 0.94
4536 | 15.2 | 0.92
4537 | 15.7 | 0.86
4538 | 15.1 | 0.87
4539 | 14.6 | 0.87
4540 | 14.6 | 0.87
4541 | 14 | 0.88
4542 | 15 | 0.85
4543 | 15.2 | 0.85
4544 | 16.2 | 0.8
4545 | 17.5 | 0.77
4546 | 18.4 | 0.77
4547 | 18.9 | 0.72
4548 | 19.5 | 0.71
4549 | 19.9 | 0.71
4550 | 20 | 0.68
4551 | 20 | 0.69
4552 | 21.6 | 0.63
4553 | 19.7 | 0.7
4554 | 18 | 0.73
4555 | 17.8 | 0.74
4556 | 16.8 | 0.76
4557 | 16 | 0.76
4558 | 13.7 | 0.91
4559 | 13.1 | 0.94
4560 | 12.9 | 0.92
4561 | 12.3 | 0.92
4562 | 12.7 | 0.94
4563 | 13.6 | 0.95
4564 | 14.2 | 0.95
4565 | 14.2 | 0.95
4566 | 14.4 | 0.95
4567 | 14.9 | 0.92
4568 | 15.3 | 0.97
4569 | 15.6 | 0.99
4570 | 15.5 | 0.98
4571 | 15.6 | 0.99
4572 | 16.8 | 0.99
4573 | 18.6 | 0.89
4574 | 18.1 | 0.91
4575 | 17.7 | 0.94
4576 | 16.8 | 0.91
4577 | 16.6 | 0.9
4578 | 16.2 | 0.89
4579 | 15.9 | 0.9
4580 | 15.9 | 0.89
4581 | 15.4 | 0.95
4582 | 15.4 | 0.96
4583 | 15.3 | 0.98
4584 | 15.3 | 0.98
4585 | 15.3 | 0.98
4586 | 15.3 | 0.98
4587 | 15.3 | 0.98
4588 | 15.3 | 0.99
4589 | 15.3 | 0.99
4590 | 15.3 | 0.99
4591 | 15.4 | 0.99
4592 | 15.7 | 0.98
4593 | 16.5 | 0.98
4594 | 17.3 | 0.96
4595 | 17.6 | 0.97
4596 | 18.3 | 0.96
4597 | 18.7 | 0.94
4598 | 19.1 | 0.9
4599 | 20.8 | 0.73
4600 | 21 | 0.68
4601 | 21.2 | 0.61
4602 | 20.3 | 0.61
4603 | 19.6 | 0.62
4604 | 18.3 | 0.68
4605 | 17.5 | 0.71
4606 | 16.1 | 0.8
4607 | 15.9 | 0.83
4608 | 15.5 | 0.87
4609 | 15.1 | 0.88
4610 | 14.9 | 0.86
4611 | 14.5 | 0.83
4612 | 13.8 | 0.83
4613 | 13.9 | 0.88
4614 | 13.2 | 0.88
4615 | 13.6 | 0.87
4616 | 14.4 | 0.83
4617 | 14.9 | 0.82
4618 | 15.7 | 0.78
4619 | 16.3 | 0.77
4620 | 17.9 | 0.68
4621 | 18.2 | 0.69
4622 | 18.7 | 0.7
4623 | 20.2 | 0.65
4624 | 19.6 | 0.65
4625 | 19.5 | 0.64
4626 | 18.3 | 0.64
4627 | 17.4 | 0.7
4628 | 16.2 | 0.71
4629 | 15.2 | 0.74
4630 | 14.4 | 0.76
4631 | 14.1 | 0.78
4632 | 13.2 | 0.83
4633 | 12.5 | 0.87
4634 | 12.1 | 0.87
4635 | 12 | 0.86
4636 | 11.9 | 0.87
4637 | 12.1 | 0.88
4638 | 12.4 | 0.88
4639 | 12.6 | 0.88
4640 | 13.5 | 0.86
4641 | 14.4 | 0.73
4642 | 15.4 | 0.67
4643 | 15.6 | 0.67
4644 | 17.1 | 0.64
4645 | 18.1 | 0.6
4646 | 19.2 | 0.56
4647 | 20 | 0.57
4648 | 20.2 | 0.57
4649 | 19.8 | 0.69
4650 | 18.5 | 0.71
4651 | 18.4 | 0.71
4652 | 17.6 | 0.75
4653 | 16.2 | 0.81
4654 | 14.5 | 0.89
4655 | 15.7 | 0.8
4656 | 15.1 | 0.82
4657 | 14.5 | 0.83
4658 | 13.6 | 0.87
4659 | 12.9 | 0.91
4660 | 12.6 | 0.9
4661 | 12.4 | 0.89
4662 | 12.1 | 0.9
4663 | 13.1 | 0.85
4664 | 14.2 | 0.81
4665 | 15.9 | 0.76
4666 | 16.9 | 0.72
4667 | 18.4 | 0.7
4668 | 18.8 | 0.67
4669 | 19.9 | 0.7
4670 | 20 | 0.7
4671 | 20 | 0.7
4672 | 20 | 0.71
4673 | 19.5 | 0.72
4674 | 19.2 | 0.73
4675 | 17.7 | 0.77
4676 | 16.6 | 0.8
4677 | 15.1 | 0.86
4678 | 13.6 | 0.92
4679 | 13.5 | 0.94
4680 | 14.1 | 0.92
4681 | 13.8 | 0.91
4682 | 13.8 | 0.95
4683 | 12.9 | 0.96
4684 | 12.3 | 0.96
4685 | 12.2 | 0.98
4686 | 11.6 | 0.98
4687 | 13.5 | 0.94
4688 | 14.9 | 0.87
4689 | 16.1 | 0.81
4690 | 17.2 | 0.82
4691 | 18.4 | 0.78
4692 | 19 | 0.76
4693 | 19.5 | 0.75
4694 | 18.7 | 0.76
4695 | 17.9 | 0.79
4696 | 17.5 | 0.82
4697 | 17.7 | 0.82
4698 | 17.5 | 0.82
4699 | 17.4 | 0.85
4700 | 17 | 0.89
4701 | 16.6 | 0.9
4702 | 16 | 0.94
4703 | 16 | 0.94
4704 | 15.7 | 0.96
4705 | 15.7 | 0.97
4706 | 15.6 | 0.97
4707 | 15.6 | 0.97
4708 | 15.7 | 0.99
4709 | 15.7 | 0.98
4710 | 15.1 | 0.99
4711 | 15.5 | 0.98
4712 | 16 | 0.96
4713 | 17.5 | 0.83
4714 | 18.1 | 0.76
4715 | 18.4 | 0.71
4716 | 20.3 | 0.7
4717 | 20.1 | 0.67
4718 | 19.1 | 0.71
4719 | 20.7 | 0.66
4720 | 21.3 | 0.63
4721 | 20.1 | 0.7
4722 | 21.2 | 0.63
4723 | 20 | 0.62
4724 | 18.3 | 0.64
4725 | 16.9 | 0.71
4726 | 15.1 | 0.82
4727 | 15 | 0.81
4728 | 14.4 | 0.88
4729 | 14.1 | 0.91
4730 | 13.6 | 0.94
4731 | 13.6 | 0.94
4732 | 13.4 | 0.96
4733 | 14.1 | 0.95
4734 | 14.4 | 0.95
4735 | 14.6 | 0.96
4736 | 15 | 0.96
4737 | 14.9 | 0.92
4738 | 14.2 | 0.93
4739 | 15.7 | 0.86
4740 | 15.2 | 0.97
4741 | 15.3 | 0.98
4742 | 16.4 | 0.98
4743 | 17.5 | 0.98
4744 | 19.3 | 0.83
4745 | 19.1 | 0.76
4746 | 18.6 | 0.8
4747 | 16.3 | 0.94
4748 | 16.2 | 0.86
4749 | 15.2 | 0.83
4750 | 14.4 | 0.77
4751 | 13.5 | 0.78
4752 | 12.8 | 0.85
4753 | 12.6 | 0.87
4754 | 12.2 | 0.88
4755 | 12.3 | 0.87
4756 | 12.5 | 0.89
4757 | 12.4 | 0.89
4758 | 12.6 | 0.87
4759 | 13.1 | 0.86
4760 | 14 | 0.85
4761 | 15.9 | 0.75
4762 | 16.9 | 0.61
4763 | 17.2 | 0.6
4764 | 18.4 | 0.62
4765 | 19.1 | 0.61
4766 | 19.7 | 0.55
4767 | 18.8 | 0.63
4768 | 17.9 | 0.71
4769 | 16.9 | 0.75
4770 | 16.7 | 0.77
4771 | 16.8 | 0.74
4772 | 15.9 | 0.81
4773 | 14.9 | 0.9
4774 | 14.4 | 0.9
4775 | 14.4 | 0.91
4776 | 14.2 | 0.94
4777 | 13.8 | 0.98
4778 | 13.8 | 0.99
4779 | 13.8 | 0.99
4780 | 13.9 | 0.98
4781 | 14.2 | 0.99
4782 | 14.6 | 1
4783 | 15.4 | 0.99
4784 | 16.9 | 0.99
4785 | 17 | 0.98
4786 | 17.8 | 0.92
4787 | 18.4 | 0.89
4788 | 17.2 | 0.95
4789 | 18.7 | 0.85
4790 | 17.6 | 0.92
4791 | 17.6 | 0.9
4792 | 17.8 | 0.89
4793 | 17.2 | 0.95
4794 | 17.9 | 0.88
4795 | 16.4 | 0.87
4796 | 15.9 | 0.87
4797 | 14.9 | 0.88
4798 | 14.4 | 0.89
4799 | 14.2 | 0.9
4800 | 14.7 | 0.86
4801 | 14.8 | 0.86
4802 | 14.5 | 0.88
4803 | 14.1 | 0.88
4804 | 13.7 | 0.85
4805 | 13.1 | 0.85
4806 | 13.2 | 0.86
4807 | 13.7 | 0.86
4808 | 14.4 | 0.82
4809 | 14.6 | 0.81
4810 | 15.7 | 0.73
4811 | 15.9 | 0.7
4812 | 17 | 0.61
4813 | 18 | 0.61
4814 | 17.7 | 0.62
4815 | 17.6 | 0.66
4816 | 17.9 | 0.71
4817 | 18.1 | 0.66
4818 | 17.8 | 0.65
4819 | 18 | 0.69
4820 | 17 | 0.72
4821 | 15.6 | 0.77
4822 | 14.4 | 0.86
4823 | 14.6 | 0.86
4824 | 14.2 | 0.92
4825 | 14.6 | 0.9
4826 | 13.5 | 0.93
4827 | 13.7 | 0.93
4828 | 13.7 | 0.95
4829 | 14 | 0.97
4830 | 14.8 | 0.96
4831 | 15.3 | 0.96
4832 | 16.1 | 0.98
4833 | 16.8 | 0.94
4834 | 16.7 | 0.94
4835 | 16.8 | 0.93
4836 | 17.6 | 0.86
4837 | 17.7 | 0.88
4838 | 16.3 | 0.97
4839 | 16.6 | 0.98
4840 | 17 | 0.99
4841 | 17.3 | 0.99
4842 | 17.6 | 0.99
4843 | 17.8 | 1
4844 | 17.6 | 0.99
4845 | 17.5 | 0.99
4846 | 17.4 | 0.99
4847 | 17.3 | 0.99
4848 | 17.4 | 0.98
4849 | 17.3 | 0.98
4850 | 17.3 | 0.95
4851 | 17 | 0.99
4852 | 17.1 | 0.95
4853 | 16.7 | 0.98
4854 | 16.6 | 0.99
4855 | 16.7 | 0.99
4856 | 17 | 0.98
4857 | 17.1 | 0.98
4858 | 18 | 0.96
4859 | 18.4 | 0.93
4860 | 19.2 | 0.91
4861 | 19.4 | 0.89
4862 | 19.9 | 0.86
4863 | 18.5 | 0.92
4864 | 18.2 | 0.93
4865 | 18 | 0.92
4866 | 17.7 | 0.94
4867 | 17.3 | 0.95
4868 | 17.4 | 0.95
4869 | 17 | 0.98
4870 | 16.7 | 0.98
4871 | 16.6 | 0.98
4872 | 16.5 | 0.96
4873 | 16.4 | 0.97
4874 | 16.4 | 0.97
4875 | 16.1 | 0.97
4876 | 16 | 0.97
4877 | 15.8 | 0.97
4878 | 15.8 | 0.94
4879 | 16.1 | 0.94
4880 | 16 | 0.94
4881 | 16 | 0.96
4882 | 16.2 | 0.98
4883 | 17 | 0.94
4884 | 17.6 | 0.91
4885 | 17.3 | 0.92
4886 | 17 | 0.92
4887 | 17.7 | 0.83
4888 | 18 | 0.83
4889 | 17.6 | 0.83
4890 | 17.1 | 0.86
4891 | 17.2 | 0.83
4892 | 16.7 | 0.88
4893 | 16.2 | 0.93
4894 | 15.7 | 0.94
4895 | 15.8 | 0.98
4896 | 16.2 | 0.99
4897 | 16.5 | 0.99
4898 | 15.2 | 0.98
4899 | 14.4 | 0.98
4900 | 14.5 | 0.98
4901 | 14.6 | 0.96
4902 | 14.2 | 0.98
4903 | 15.1 | 0.99
4904 | 16 | 0.98
4905 | 16.3 | 0.98
4906 | 16.7 | 0.96
4907 | 17.7 | 0.92
4908 | 18.1 | 0.87
4909 | 17.8 | 0.87
4910 | 17.7 | 0.87
4911 | 18.3 | 0.82
4912 | 17.4 | 0.89
4913 | 17.4 | 0.92
4914 | 17.1 | 0.95
4915 | 17.5 | 0.94
4916 | 17.1 | 0.95
4917 | 16.8 | 0.96
4918 | 16.7 | 0.96
4919 | 17 | 0.98
4920 | 17.3 | 0.98
4921 | 17.3 | 0.99
4922 | 17.4 | 1
4923 | 17.4 | 0.99
4924 | 17.1 | 0.99
4925 | 17.1 | 0.97
4926 | 16.9 | 0.98
4927 | 16.8 | 0.99
4928 | 16.9 | 0.99
4929 | 17.1 | 0.99
4930 | 17.6 | 0.99
4931 | 17.6 | 0.97
4932 | 17.9 | 0.95
4933 | 18 | 0.95
4934 | 18.3 | 0.94
4935 | 18.7 | 0.9
4936 | 18.4 | 0.92
4937 | 18.5 | 0.89
4938 | 18 | 0.92
4939 | 16.9 | 0.97
4940 | 16.8 | 0.96
4941 | 16.5 | 0.98
4942 | 16.5 | 0.98
4943 | 16.1 | 0.98
4944 | 15.6 | 0.97
4945 | 15.5 | 0.97
4946 | 15.7 | 0.99
4947 | 15.5 | 0.98
4948 | 14.8 | 0.98
4949 | 14.3 | 0.97
4950 | 14.2 | 0.98
4951 | 14.4 | 0.98
4952 | 14.7 | 0.98
4953 | 15.4 | 0.89
4954 | 16.9 | 0.85
4955 | 17.1 | 0.84
4956 | 18.5 | 0.75
4957 | 18.8 | 0.72
4958 | 18.7 | 0.7
4959 | 18.4 | 0.65
4960 | 19.3 | 0.62
4961 | 19.5 | 0.6
4962 | 17.7 | 0.63
4963 | 16.8 | 0.66
4964 | 16.3 | 0.68
4965 | 14.6 | 0.7
4966 | 13.2 | 0.77
4967 | 12.9 | 0.85
4968 | 12.1 | 0.89
4969 | 12.4 | 0.88
4970 | 12.2 | 0.88
4971 | 11.6 | 0.89
4972 | 11.1 | 0.91
4973 | 11 | 0.91
4974 | 10.9 | 0.94
4975 | 11.2 | 0.92
4976 | 12.5 | 0.88
4977 | 13.6 | 0.83
4978 | 15.2 | 0.73
4979 | 17.1 | 0.69
4980 | 17.8 | 0.6
4981 | 18.5 | 0.54
4982 | 17.7 | 0.63
4983 | 19.2 | 0.56
4984 | 18.5 | 0.59
4985 | 19 | 0.55
4986 | 18.5 | 0.59
4987 | 17.8 | 0.6
4988 | 17.6 | 0.6
4989 | 16.1 | 0.65
4990 | 14.7 | 0.73
4991 | 13.4 | 0.78
4992 | 12.9 | 0.83
4993 | 12.4 | 0.86
4994 | 12.1 | 0.89
4995 | 11.7 | 0.9
4996 | 11.5 | 0.89
4997 | 11.2 | 0.89
4998 | 11.1 | 0.9
4999 | 11.5 | 0.9
5000 | 12.7 | 0.87
5001 | 14 | 0.83
5002 | 15.7 | 0.76
5003 | 15.6 | 0.7
5004 | 16.4 | 0.7
5005 | 16.8 | 0.68
5006 | 16.1 | 0.67
5007 | 14.8 | 0.77
5008 | 15.7 | 0.73
5009 | 16.2 | 0.67
5010 | 15.1 | 0.81
5011 | 14.2 | 0.88
5012 | 13.7 | 0.91
5013 | 13.3 | 0.92
5014 | 13.1 | 0.93
5015 | 13 | 0.93
5016 | 12.7 | 0.94
5017 | 12.7 | 0.94
5018 | 12.4 | 0.95
5019 | 12 | 0.95
5020 | 11.9 | 0.95
5021 | 11.8 | 0.95
5022 | 11.1 | 0.96
5023 | 11.9 | 0.95
5024 | 12.9 | 0.89
5025 | 14.6 | 0.83
5026 | 17 | 0.76
5027 | 16.9 | 0.72
5028 | 17.8 | 0.66
5029 | 18 | 0.65
5030 | 17.4 | 0.67
5031 | 14.2 | 0.9
5032 | 14.5 | 0.93
5033 | 14.1 | 0.97
5034 | 13.8 | 0.98
5035 | 13.5 | 0.97
5036 | 13.5 | 0.97
5037 | 13.2 | 0.96
5038 | 13.2 | 0.98
5039 | 13.7 | 0.97
5040 | 13.9 | 0.95
5041 | 13.9 | 0.95
5042 | 14 | 0.94
5043 | 14 | 0.95
5044 | 13.7 | 0.94
5045 | 13.5 | 0.94
5046 | 13.2 | 0.93
5047 | 13.4 | 0.93
5048 | 13.9 | 0.9
5049 | 14.3 | 0.88
5050 | 15.4 | 0.81
5051 | 17.1 | 0.71
5052 | 16.8 | 0.72
5053 | 17.9 | 0.66
5054 | 17.4 | 0.68
5055 | 18.1 | 0.64
5056 | 17.5 | 0.65
5057 | 16.4 | 0.71
5058 | 16.4 | 0.7
5059 | 16.4 | 0.66
5060 | 15.8 | 0.69
5061 | 14.8 | 0.71
5062 | 13.4 | 0.75
5063 | 12.5 | 0.78
5064 | 12.1 | 0.81
5065 | 12.2 | 0.82
5066 | 12.2 | 0.86
5067 | 12.9 | 0.8
5068 | 12.9 | 0.8
5069 | 12.1 | 0.92
5070 | 12.4 | 0.92
5071 | 12.7 | 0.92
5072 | 13 | 0.93
5073 | 14.2 | 0.84
5074 | 14.7 | 0.85
5075 | 14.3 | 0.91
5076 | 15.9 | 0.86
5077 | 15.5 | 0.92
5078 | 15.9 | 0.88
5079 | 16.3 | 0.78
5080 | 18 | 0.67
5081 | 18.9 | 0.6
5082 | 18.9 | 0.61
5083 | 18.2 | 0.61
5084 | 17 | 0.63
5085 | 15.4 | 0.68
5086 | 14.1 | 0.74
5087 | 13.1 | 0.79
5088 | 12.8 | 0.8
5089 | 12.4 | 0.82
5090 | 12.1 | 0.84
5091 | 11.8 | 0.81
5092 | 11.6 | 0.85
5093 | 11.8 | 0.87
5094 | 11.7 | 0.89
5095 | 12.1 | 0.88
5096 | 13.3 | 0.86
5097 | 14.3 | 0.81
5098 | 16.5 | 0.72
5099 | 17.6 | 0.68
5100 | 19 | 0.6
5101 | 19.7 | 0.63
5102 | 19.5 | 0.62
5103 | 19.6 | 0.61
5104 | 19.6 | 0.65
5105 | 19.6 | 0.6
5106 | 19.1 | 0.64
5107 | 18.4 | 0.65
5108 | 17.4 | 0.72
5109 | 15.2 | 0.85
5110 | 13.1 | 0.92
5111 | 13.3 | 0.95
5112 | 13.3 | 0.95
5113 | 13.9 | 0.92
5114 | 12.8 | 0.95
5115 | 12.8 | 0.95
5116 | 11.9 | 0.98
5117 | 11.6 | 0.96
5118 | 11.5 | 1
5119 | 12.3 | 0.99
5120 | 12.4 | 1
5121 | 14.1 | 0.99
5122 | 14.7 | 0.98
5123 | 17.3 | 0.77
5124 | 19.1 | 0.67
5125 | 19.4 | 0.67
5126 | 19.6 | 0.68
5127 | 19.9 | 0.64
5128 | 18.9 | 0.74
5129 | 19.1 | 0.71
5130 | 18.1 | 0.76
5131 | 17.4 | 0.81
5132 | 16.7 | 0.88
5133 | 16.3 | 0.92
5134 | 15.8 | 0.94
5135 | 15.4 | 0.95
5136 | 15.4 | 0.96
5137 | 15.6 | 0.95
5138 | 15.9 | 0.95
5139 | 16 | 0.95
5140 | 16 | 0.96
5141 | 15.7 | 0.98
5142 | 14.9 | 0.98
5143 | 14.7 | 0.99
5144 | 15.1 | 0.99
5145 | 15.6 | 0.98
5146 | 16.1 | 0.93
5147 | 15.4 | 0.97
5148 | 15.9 | 0.97
5149 | 15.7 | 0.96
5150 | 15.7 | 0.94
5151 | 15.9 | 0.98
5152 | 16.6 | 0.99
5153 | 17.2 | 0.95
5154 | 17.1 | 0.92
5155 | 16.6 | 0.92
5156 | 16.4 | 0.91
5157 | 15.1 | 0.94
5158 | 14.2 | 0.97
5159 | 13.3 | 0.98
5160 | 13.5 | 0.98
5161 | 13.2 | 0.99
5162 | 13.1 | 0.99
5163 | 13.1 | 1
5164 | 13 | 1
5165 | 13.8 | 1
5166 | 14.2 | 0.99
5167 | 14.4 | 0.99
5168 | 15.3 | 0.97
5169 | 16.2 | 0.94
5170 | 16.7 | 0.9
5171 | 17.5 | 0.87
5172 | 16.7 | 0.92
5173 | 17.3 | 0.84
5174 | 17.5 | 0.83
5175 | 16.8 | 0.86
5176 | 15.2 | 0.97
5177 | 15.4 | 0.98
5178 | 15.9 | 0.99
5179 | 17.1 | 0.9
5180 | 16 | 0.82
5181 | 13.9 | 0.88
5182 | 12.7 | 0.94
5183 | 12.5 | 0.95
5184 | 12.3 | 0.95
5185 | 11.9 | 0.96
5186 | 11.4 | 0.97
5187 | 11.6 | 0.98
5188 | 12 | 0.96
5189 | 12.1 | 0.96
5190 | 11.8 | 0.98
5191 | 12.1 | 0.96
5192 | 13.7 | 0.94
5193 | 14.8 | 0.92
5194 | 15.1 | 0.91
5195 | 16.7 | 0.88
5196 | 17.4 | 0.84
5197 | 17.3 | 0.81
5198 | 18.5 | 0.73
5199 | 18.2 | 0.76
5200 | 17.9 | 0.73
5201 | 18.2 | 0.74
5202 | 16.7 | 0.79
5203 | 16 | 0.8
5204 | 15.6 | 0.82
5205 | 14.6 | 0.85
5206 | 14.1 | 0.91
5207 | 13.9 | 0.9
5208 | 13.5 | 0.91
5209 | 14.2 | 0.89
5210 | 14.3 | 0.93
5211 | 14.3 | 0.94
5212 | 14.1 | 0.95
5213 | 14.1 | 0.98
5214 | 13.8 | 0.98
5215 | 13.3 | 0.95
5216 | 13.6 | 0.95
5217 | 14.8 | 0.94
5218 | 16.5 | 0.81
5219 | 17.2 | 0.74
5220 | 17 | 0.76
5221 | 17.2 | 0.74
5222 | 18.6 | 0.7
5223 | 18.5 | 0.7
5224 | 17.9 | 0.74
5225 | 18 | 0.73
5226 | 18.7 | 0.71
5227 | 17.5 | 0.72
5228 | 16.4 | 0.75
5229 | 15.1 | 0.83
5230 | 14.6 | 0.86
5231 | 14.5 | 0.86
5232 | 14 | 0.89
5233 | 13.8 | 0.9
5234 | 13.5 | 0.93
5235 | 13.5 | 0.93
5236 | 12.7 | 0.94
5237 | 12.4 | 0.94
5238 | 12.5 | 0.92
5239 | 12.4 | 0.93
5240 | 13.9 | 0.89
5241 | 14.4 | 0.82
5242 | 15.7 | 0.79
5243 | 16 | 0.77
5244 | 17.3 | 0.74
5245 | 18.5 | 0.65
5246 | 19.1 | 0.63
5247 | 19.1 | 0.65
5248 | 19.9 | 0.61
5249 | 19.3 | 0.6
5250 | 19.1 | 0.63
5251 | 18.9 | 0.65
5252 | 17.7 | 0.7
5253 | 16.8 | 0.7
5254 | 16.1 | 0.78
5255 | 15.3 | 0.82
5256 | 14.7 | 0.86
5257 | 14.6 | 0.86
5258 | 13.8 | 0.86
5259 | 13 | 0.91
5260 | 12.9 | 0.89
5261 | 13.1 | 0.92
5262 | 12.7 | 0.94
5263 | 12.3 | 0.95
5264 | 14.2 | 0.87
5265 | 16 | 0.84
5266 | 17 | 0.77
5267 | 17.5 | 0.77
5268 | 17.2 | 0.81
5269 | 18.3 | 0.72
5270 | 17.8 | 0.76
5271 | 17.7 | 0.74
5272 | 16.7 | 0.81
5273 | 16.2 | 0.81
5274 | 15.3 | 0.93
5275 | 14.8 | 0.94
5276 | 14.4 | 0.97
5277 | 14.5 | 0.98
5278 | 15.1 | 0.98
5279 | 15.8 | 0.99
5280 | 17.2 | 0.99
5281 | 17.5 | 0.99
5282 | 16.5 | 0.99
5283 | 15.7 | 0.97
5284 | 15.6 | 0.96
5285 | 15.7 | 0.98
5286 | 16.1 | 0.98
5287 | 16 | 0.98
5288 | 16.1 | 0.98
5289 | 16.1 | 0.98
5290 | 16.8 | 0.96
5291 | 16.7 | 0.95
5292 | 16.3 | 0.98
5293 | 16.1 | 0.98
5294 | 16.6 | 0.98
5295 | 16.5 | 0.98
5296 | 16.3 | 0.97
5297 | 16 | 0.98
5298 | 15.9 | 0.99
5299 | 15.9 | 0.98
5300 | 16.2 | 0.98
5301 | 15.8 | 0.96
5302 | 15.4 | 0.96
5303 | 15.3 | 0.97
5304 | 15.3 | 0.97
5305 | 15.5 | 0.97
5306 | 15.1 | 0.98
5307 | 14.8 | 0.98
5308 | 14.9 | 0.99
5309 | 15.3 | 0.97
5310 | 14.9 | 0.91
5311 | 14.7 | 0.91
5312 | 15.4 | 0.9
5313 | 16.1 | 0.84
5314 | 16.1 | 0.8
5315 | 15.9 | 0.78
5316 | 16.6 | 0.73
5317 | 16.8 | 0.7
5318 | 17.7 | 0.64
5319 | 17.2 | 0.67
5320 | 16.5 | 0.7
5321 | 15.9 | 0.73
5322 | 15.6 | 0.78
5323 | 15.4 | 0.81
5324 | 14.4 | 0.9
5325 | 14.1 | 0.94
5326 | 14 | 0.94
5327 | 13.9 | 0.97
5328 | 14 | 0.95
5329 | 13.8 | 0.95
5330 | 13.6 | 0.95
5331 | 13.4 | 0.94
5332 | 13.1 | 0.94
5333 | 12.9 | 0.94
5334 | 12.7 | 0.94
5335 | 12.6 | 0.93
5336 | 13 | 0.92
5337 | 13.5 | 0.88
5338 | 13.2 | 0.9
5339 | 13.7 | 0.84
5340 | 14.4 | 0.78
5341 | 14.5 | 0.77
5342 | 15.2 | 0.73
5343 | 14.6 | 0.71
5344 | 15 | 0.68
5345 | 15.9 | 0.63
5346 | 15.2 | 0.62
5347 | 14.9 | 0.65
5348 | 14.2 | 0.65
5349 | 12.9 | 0.7
5350 | 11.9 | 0.76
5351 | 11.3 | 0.8
5352 | 10.8 | 0.82
5353 | 10.4 | 0.85
5354 | 9.7 | 0.87
5355 | 9.3 | 0.89
5356 | 9.4 | 0.88
5357 | 9.9 | 0.84
5358 | 9.7 | 0.83
5359 | 10.2 | 0.82
5360 | 10.6 | 0.84
5361 | 12 | 0.82
5362 | 13.6 | 0.82
5363 | 14.7 | 0.76
5364 | 16.9 | 0.61
5365 | 17.5 | 0.59
5366 | 17.1 | 0.64
5367 | 12.9 | 0.86
5368 | 16.3 | 0.7
5369 | 17.4 | 0.6
5370 | 17.1 | 0.53
5371 | 15.9 | 0.59
5372 | 14.8 | 0.65
5373 | 13.9 | 0.7
5374 | 13.4 | 0.72
5375 | 12.5 | 0.78
5376 | 12.4 | 0.79
5377 | 12.5 | 0.79
5378 | 12 | 0.81
5379 | 11.9 | 0.82
5380 | 11.5 | 0.88
5381 | 11.7 | 0.89
5382 | 11.3 | 0.93
5383 | 11.2 | 0.94
5384 | 12.3 | 0.95
5385 | 12.7 | 0.96
5386 | 13.4 | 0.9
5387 | 14 | 0.89
5388 | 14.2 | 0.91
5389 | 15.6 | 0.85
5390 | 15.9 | 0.83
5391 | 15.5 | 0.9
5392 | 15.8 | 0.83
5393 | 15 | 0.92
5394 | 14.4 | 0.93
5395 | 14.2 | 0.99
5396 | 14.2 | 0.98
5397 | 14.3 | 0.98
5398 | 14.1 | 0.99
5399 | 14.4 | 0.99
5400 | 14.6 | 0.99
5401 | 14.8 | 0.99
5402 | 15.1 | 1
5403 | 15.6 | 0.99
5404 | 15.6 | 1
5405 | 15.6 | 0.99
5406 | 15.4 | 0.99
5407 | 15.4 | 0.99
5408 | 15.7 | 0.98
5409 | 16.5 | 0.98
5410 | 17.3 | 0.92
5411 | 18.5 | 0.85
5412 | 18.8 | 0.84
5413 | 19.9 | 0.78
5414 | 21.2 | 0.68
5415 | 18.8 | 0.75
5416 | 17.2 | 0.73
5417 | 17.8 | 0.69
5418 | 17.5 | 0.72
5419 | 16.7 | 0.77
5420 | 16.3 | 0.81
5421 | 15.5 | 0.87
5422 | 14.8 | 0.92
5423 | 14.6 | 0.88
5424 | 13.5 | 0.92
5425 | 15.3 | 0.81
5426 | 15 | 0.83
5427 | 14.8 | 0.86
5428 | 14.2 | 0.81
5429 | 13.7 | 0.89
5430 | 13.8 | 0.87
5431 | 13.9 | 0.88
5432 | 14.2 | 0.9
5433 | 15 | 0.88
5434 | 16.5 | 0.81
5435 | 17.6 | 0.78
5436 | 17.5 | 0.75
5437 | 18.1 | 0.75
5438 | 19.3 | 0.68
5439 | 20 | 0.62
5440 | 19.5 | 0.69
5441 | 18.4 | 0.68
5442 | 17.5 | 0.72
5443 | 16.5 | 0.73
5444 | 15.4 | 0.89
5445 | 15 | 0.93
5446 | 14.9 | 0.93
5447 | 15 | 0.94
5448 | 14.5 | 0.98
5449 | 15.1 | 0.94
5450 | 15 | 0.97
5451 | 14.8 | 0.96
5452 | 14.5 | 0.97
5453 | 14.3 | 0.99
5454 | 14.8 | 0.99
5455 | 15.4 | 0.99
5456 | 16.1 | 0.99
5457 | 16.3 | 0.99
5458 | 16.3 | 0.99
5459 | 16.4 | 0.99
5460 | 16.4 | 0.99
5461 | 17.5 | 0.97
5462 | 19.4 | 0.77
5463 | 19.8 | 0.72
5464 | 18.8 | 0.65
5465 | 18.9 | 0.66
5466 | 17.4 | 0.72
5467 | 16.3 | 0.79
5468 | 15.7 | 0.8
5469 | 15.1 | 0.84
5470 | 14.3 | 0.89
5471 | 14 | 0.92
5472 | 14.1 | 0.94
5473 | 13.4 | 0.94
5474 | 12.5 | 0.92
5475 | 12 | 0.89
5476 | 11.1 | 0.91
5477 | 10.4 | 0.95
5478 | 10.3 | 0.95
5479 | 11.3 | 0.94
5480 | 12.4 | 0.9
5481 | 13.5 | 0.86
5482 | 14 | 0.82
5483 | 16.2 | 0.69
5484 | 16.7 | 0.72
5485 | 16.5 | 0.72
5486 | 16.8 | 0.63
5487 | 16.6 | 0.66
5488 | 16.5 | 0.67
5489 | 16.7 | 0.64
5490 | 16.3 | 0.71
5491 | 14.9 | 0.71
5492 | 13.9 | 0.81
5493 | 12.4 | 0.89
5494 | 11.9 | 0.9
5495 | 11.4 | 0.93
5496 | 10.9 | 0.94
5497 | 11.1 | 0.95
5498 | 10.8 | 0.96
5499 | 10.4 | 0.97
5500 | 10.2 | 0.96
5501 | 10.5 | 0.96
5502 | 10.2 | 0.96
5503 | 10.6 | 0.94
5504 | 11.7 | 0.9
5505 | 13.1 | 0.86
5506 | 14.4 | 0.72
5507 | 16.1 | 0.66
5508 | 16.3 | 0.64
5509 | 16.5 | 0.66
5510 | 18.2 | 0.57
5511 | 17.6 | 0.61
5512 | 17.7 | 0.61
5513 | 16 | 0.69
5514 | 16.2 | 0.68
5515 | 15.4 | 0.75
5516 | 14.6 | 0.78
5517 | 13.4 | 0.85
5518 | 13.1 | 0.87
5519 | 12.7 | 0.93
5520 | 12.3 | 0.9
5521 | 11.9 | 0.91
5522 | 11.3 | 0.93
5523 | 11.1 | 0.91
5524 | 10.5 | 0.91
5525 | 10.6 | 0.9
5526 | 10.1 | 0.9
5527 | 10.1 | 0.9
5528 | 11.3 | 0.86
5529 | 12.4 | 0.85
5530 | 14.3 | 0.73
5531 | 16.2 | 0.62
5532 | 15.5 | 0.69
5533 | 14 | 0.82
5534 | 16.4 | 0.63
5535 | 15.2 | 0.67
5536 | 17.5 | 0.59
5537 | 16.5 | 0.58
5538 | 16 | 0.59
5539 | 15.5 | 0.57
5540 | 14.5 | 0.62
5541 | 13.1 | 0.69
5542 | 12 | 0.76
5543 | 10.9 | 0.82
5544 | 9.5 | 0.87
5545 | 8.3 | 0.92
5546 | 9.9 | 0.87
5547 | 9.3 | 0.88
5548 | 9.7 | 0.88
5549 | 10.1 | 0.91
5550 | 10.9 | 0.91
5551 | 11.1 | 0.92
5552 | 11.7 | 0.95
5553 | 12.8 | 0.96
5554 | 13.7 | 0.97
5555 | 15 | 0.92
5556 | 16.7 | 0.78
5557 | 16.9 | 0.82
5558 | 17.1 | 0.71
5559 | 17.1 | 0.74
5560 | 17.4 | 0.65
5561 | 17 | 0.65
5562 | 15.8 | 0.74
5563 | 16.1 | 0.76
5564 | 14.7 | 0.82
5565 | 13.3 | 0.87
5566 | 12.7 | 0.92
5567 | 12.6 | 0.95
5568 | 12.5 | 0.96
5569 | 13.1 | 0.98
5570 | 12.4 | 0.98
5571 | 12.7 | 0.98
5572 | 13.3 | 0.99
5573 | 13.4 | 0.98
5574 | 13.4 | 0.98
5575 | 13.5 | 0.97
5576 | 13.9 | 0.95
5577 | 14.3 | 0.92
5578 | 15 | 0.88
5579 | 15.2 | 0.86
5580 | 15.6 | 0.85
5581 | 15.5 | 0.86
5582 | 15.5 | 0.85
5583 | 15.5 | 0.87
5584 | 15.4 | 0.85
5585 | 14.5 | 0.93
5586 | 14.3 | 0.98
5587 | 14.4 | 0.98
5588 | 14.5 | 0.98
5589 | 14.6 | 0.98
5590 | 14.6 | 0.98
5591 | 14.8 | 0.97
5592 | 14.8 | 0.97
5593 | 14.8 | 0.96
5594 | 14.9 | 0.97
5595 | 14.9 | 0.98
5596 | 14.7 | 0.98
5597 | 14.8 | 0.99
5598 | 15.1 | 0.99
5599 | 15.3 | 0.98
5600 | 15.3 | 0.98
5601 | 15.4 | 0.95
5602 | 16 | 0.93
5603 | 16.3 | 0.89
5604 | 17.1 | 0.89
5605 | 16.9 | 0.94
5606 | 17.6 | 0.91
5607 | 18.1 | 0.89
5608 | 19.4 | 0.84
5609 | 18.2 | 0.9
5610 | 17.6 | 0.93
5611 | 17.6 | 0.89
5612 | 16.4 | 0.94
5613 | 15.9 | 0.97
5614 | 15.4 | 0.98
5615 | 15.1 | 0.98
5616 | 14.9 | 0.99
5617 | 14.7 | 0.99
5618 | 14.5 | 0.99
5619 | 14.1 | 0.98
5620 | 13.6 | 0.97
5621 | 13.6 | 0.97
5622 | 13.2 | 0.98
5623 | 13.6 | 0.98
5624 | 14.2 | 0.98
5625 | 15.3 | 0.92
5626 | 16.2 | 0.89
5627 | 15.6 | 0.88
5628 | 16.1 | 0.84
5629 | 15.6 | 0.91
5630 | 18 | 0.75
5631 | 17.3 | 0.79
5632 | 17.2 | 0.75
5633 | 16.9 | 0.75
5634 | 16.5 | 0.83
5635 | 15.6 | 0.89
5636 | 15.3 | 0.93
5637 | 14.3 | 0.95
5638 | 13.7 | 0.99
5639 | 13.9 | 0.99
5640 | 14.1 | 0.98
5641 | 14 | 0.99
5642 | 14.9 | 0.99
5643 | 15.1 | 0.99
5644 | 14.6 | 1
5645 | 14.4 | 0.99
5646 | 14.5 | 0.99
5647 | 15 | 0.99
5648 | 15.5 | 0.99
5649 | 16.3 | 0.98
5650 | 17 | 0.95
5651 | 18 | 0.9
5652 | 18.7 | 0.84
5653 | 18 | 0.9
5654 | 17.8 | 0.91
5655 | 18.3 | 0.86
5656 | 18.8 | 0.83
5657 | 18.8 | 0.8
5658 | 19.3 | 0.8
5659 | 19.4 | 0.75
5660 | 17.2 | 0.93
5661 | 17.2 | 0.87
5662 | 16.5 | 0.89
5663 | 15.6 | 0.92
5664 | 15.1 | 0.93
5665 | 15.1 | 0.91
5666 | 14.8 | 0.91
5667 | 14.4 | 0.89
5668 | 14.2 | 0.87
5669 | 13.7 | 0.86
5670 | 13.2 | 0.87
5671 | 13 | 0.87
5672 | 13.4 | 0.85
5673 | 14.4 | 0.8
5674 | 16 | 0.73
5675 | 16.4 | 0.71
5676 | 17.5 | 0.68
5677 | 18.5 | 0.63
5678 | 18.7 | 0.6
5679 | 19.8 | 0.57
5680 | 19.5 | 0.58
5681 | 20 | 0.58
5682 | 18.3 | 0.61
5683 | 17.7 | 0.67
5684 | 17.1 | 0.71
5685 | 15.9 | 0.77
5686 | 14.5 | 0.82
5687 | 13.7 | 0.85
5688 | 13 | 0.87
5689 | 12.4 | 0.9
5690 | 12.1 | 0.92
5691 | 11.8 | 0.9
5692 | 11.2 | 0.94
5693 | 11 | 0.94
5694 | 11.5 | 0.93
5695 | 10.7 | 0.92
5696 | 11.7 | 0.9
5697 | 12.8 | 0.89
5698 | 14.7 | 0.79
5699 | 15.6 | 0.74
5700 | 16.7 | 0.71
5701 | 17.1 | 0.66
5702 | 18.4 | 0.68
5703 | 18.2 | 0.72
5704 | 18.1 | 0.72
5705 | 16.4 | 0.82
5706 | 15.8 | 0.83
5707 | 15.4 | 0.86
5708 | 14.8 | 0.9
5709 | 14.4 | 0.93
5710 | 13.1 | 0.95
5711 | 13 | 0.98
5712 | 13.1 | 0.98
5713 | 13.2 | 0.98
5714 | 13.2 | 0.99
5715 | 13.4 | 0.99
5716 | 13.8 | 0.99
5717 | 14 | 0.99
5718 | 14.2 | 0.99
5719 | 14 | 0.98
5720 | 14 | 0.98
5721 | 14 | 0.98
5722 | 14.3 | 0.98
5723 | 15.2 | 0.96
5724 | 14.8 | 0.98
5725 | 14.7 | 0.97
5726 | 15.3 | 0.93
5727 | 15.2 | 0.91
5728 | 16.1 | 0.86
5729 | 15.4 | 0.9
5730 | 15.5 | 0.9
5731 | 15 | 0.97
5732 | 14.4 | 0.98
5733 | 15 | 0.99
5734 | 13.9 | 0.98
5735 | 13.1 | 0.96
5736 | 13.1 | 0.95
5737 | 12.4 | 0.94
5738 | 11.8 | 0.96
5739 | 11.5 | 0.93
5740 | 10.3 | 0.92
5741 | 9.7 | 0.95
5742 | 9.5 | 0.93
5743 | 9.9 | 0.91
5744 | 10.7 | 0.89
5745 | 12.2 | 0.83
5746 | 14.3 | 0.76
5747 | 14.7 | 0.71
5748 | 16 | 0.68
5749 | 16.7 | 0.65
5750 | 16.2 | 0.7
5751 | 17 | 0.63
5752 | 16.4 | 0.68
5753 | 16.5 | 0.72
5754 | 15.6 | 0.75
5755 | 14.8 | 0.8
5756 | 14.4 | 0.84
5757 | 12.6 | 0.92
5758 | 11.7 | 0.94
5759 | 11.4 | 0.95
5760 | 10.9 | 0.97
5761 | 10.8 | 0.96
5762 | 10.5 | 0.96
5763 | 10.4 | 0.96
5764 | 10.4 | 0.96
5765 | 11.8 | 0.95
5766 | 12.3 | 0.94
5767 | 13.1 | 0.94
5768 | 13.4 | 0.93
5769 | 14.2 | 0.92
5770 | 14.9 | 0.9
5771 | 16.1 | 0.82
5772 | 16.3 | 0.81
5773 | 16.5 | 0.85
5774 | 15.7 | 0.9
5775 | 16.6 | 0.86
5776 | 17.1 | 0.82
5777 | 16.4 | 0.85
5778 | 16.6 | 0.82
5779 | 16 | 0.87
5780 | 15.2 | 0.86
5781 | 14.8 | 0.88
5782 | 14.6 | 0.93
5783 | 14.7 | 0.93
5784 | 15.1 | 0.91
5785 | 15.3 | 0.91
5786 | 15.3 | 0.93
5787 | 15.3 | 0.91
5788 | 15.3 | 0.92
5789 | 15.3 | 0.93
5790 | 15.3 | 0.92
5791 | 15.4 | 0.91
5792 | 15.3 | 0.93
5793 | 15.4 | 0.92
5794 | 15.6 | 0.92
5795 | 16.7 | 0.87
5796 | 16.3 | 0.88
5797 | 16.2 | 0.88
5798 | 16.8 | 0.87
5799 | 17.4 | 0.87
5800 | 17.3 | 0.86
5801 | 17.1 | 0.86
5802 | 16.3 | 0.89
5803 | 16 | 0.9
5804 | 15.5 | 0.93
5805 | 15.4 | 0.93
5806 | 15.3 | 0.93
5807 | 15.4 | 0.93
5808 | 15.5 | 0.92
5809 | 15.4 | 0.93
5810 | 15.1 | 0.98
5811 | 14.9 | 0.99
5812 | 14.8 | 0.98
5813 | 12.3 | 0.93
5814 | 11.6 | 0.89
5815 | 11.2 | 0.88
5816 | 11.5 | 0.86
5817 | 12.6 | 0.81
5818 | 13.7 | 0.73
5819 | 14.8 | 0.66
5820 | 15.2 | 0.63
5821 | 16.1 | 0.63
5822 | 15.3 | 0.64
5823 | 15.4 | 0.59
5824 | 16.3 | 0.57
5825 | 16 | 0.6
5826 | 14.9 | 0.56
5827 | 14.3 | 0.63
5828 | 13.1 | 0.73
5829 | 11.9 | 0.77
5830 | 11.1 | 0.85
5831 | 11.1 | 0.83
5832 | 10.9 | 0.84
5833 | 10.8 | 0.84
5834 | 10.6 | 0.84
5835 | 10.2 | 0.85
5836 | 9.8 | 0.84
5837 | 9.5 | 0.87
5838 | 9 | 0.88
5839 | 8.9 | 0.89
5840 | 10.2 | 0.82
5841 | 11.7 | 0.78
5842 | 12.9 | 0.7
5843 | 14.1 | 0.65
5844 | 14.9 | 0.66
5845 | 16.7 | 0.57
5846 | 15.4 | 0.57
5847 | 16.2 | 0.66
5848 | 16 | 0.69
5849 | 16 | 0.66
5850 | 15.6 | 0.63
5851 | 14.8 | 0.74
5852 | 14.1 | 0.8
5853 | 13 | 0.84
5854 | 12.2 | 0.89
5855 | 11.9 | 0.93
5856 | 11.6 | 0.91
5857 | 11.1 | 0.9
5858 | 11.3 | 0.9
5859 | 11.6 | 0.93
5860 | 11.8 | 0.89
5861 | 10.7 | 0.94
5862 | 11.6 | 0.91
5863 | 10.7 | 0.95
5864 | 12 | 0.95
5865 | 13.1 | 0.93
5866 | 14.6 | 0.88
5867 | 15.3 | 0.82
5868 | 16 | 0.75
5869 | 17.9 | 0.69
5870 | 17.6 | 0.67
5871 | 17.3 | 0.71
5872 | 16.8 | 0.7
5873 | 15.7 | 0.73
5874 | 15.2 | 0.75
5875 | 15.1 | 0.73
5876 | 13.2 | 0.88
5877 | 13.4 | 0.87
5878 | 12.6 | 0.92
5879 | 12.3 | 0.94
5880 | 13.1 | 0.95
5881 | 13.7 | 0.92
5882 | 13.1 | 0.93
5883 | 13.5 | 0.9
5884 | 13.5 | 0.91
5885 | 13.3 | 0.96
5886 | 13.5 | 0.98
5887 | 13.8 | 0.99
5888 | 14.2 | 0.99
5889 | 14.6 | 0.99
5890 | 15.2 | 0.98
5891 | 15.3 | 0.98
5892 | 15.6 | 0.99
5893 | 16.6 | 0.95
5894 | 16.8 | 0.96
5895 | 17.9 | 0.89
5896 | 17 | 0.94
5897 | 16.1 | 0.98
5898 | 16.6 | 0.98
5899 | 16.4 | 0.95
5900 | 16 | 0.97
5901 | 15.4 | 0.95
5902 | 14.6 | 0.98
5903 | 14.7 | 0.97
5904 | 13.8 | 0.85
5905 | 12.1 | 0.89
5906 | 11.5 | 0.86
5907 | 10.8 | 0.81
5908 | 10.1 | 0.84
5909 | 10.3 | 0.86
5910 | 9.5 | 0.89
5911 | 9.4 | 0.88
5912 | 10.2 | 0.88
5913 | 12.3 | 0.83
5914 | 13.2 | 0.82
5915 | 13.5 | 0.87
5916 | 16.1 | 0.7
5917 | 15.7 | 0.64
5918 | 14.6 | 0.65
5919 | 15.7 | 0.59
5920 | 15.9 | 0.58
5921 | 15.4 | 0.58
5922 | 14.8 | 0.58
5923 | 14 | 0.65
5924 | 12.2 | 0.72
5925 | 11.7 | 0.72
5926 | 10.9 | 0.76
5927 | 10.5 | 0.74
5928 | 9.6 | 0.74
5929 | 8 | 0.8
5930 | 8.4 | 0.78
5931 | 8.4 | 0.79
5932 | 8.1 | 0.83
5933 | 8.8 | 0.86
5934 | 9.6 | 0.83
5935 | 9.7 | 0.83
5936 | 10.9 | 0.8
5937 | 11.7 | 0.78
5938 | 12.9 | 0.76
5939 | 13.9 | 0.66
5940 | 14.8 | 0.66
5941 | 15.3 | 0.65
5942 | 16.6 | 0.59
5943 | 17 | 0.59
5944 | 17.4 | 0.59
5945 | 18 | 0.59
5946 | 17.2 | 0.57
5947 | 16 | 0.64
5948 | 14 | 0.73
5949 | 12.3 | 0.78
5950 | 10.2 | 0.87
5951 | 10.4 | 0.88
5952 | 10.1 | 0.91
5953 | 12 | 0.81
5954 | 11.8 | 0.84
5955 | 12 | 0.84
5956 | 12.3 | 0.84
5957 | 12.6 | 0.86
5958 | 12.5 | 0.9
5959 | 12.6 | 0.92
5960 | 13.1 | 0.92
5961 | 14.3 | 0.9
5962 | 14.7 | 0.91
5963 | 16.2 | 0.83
5964 | 16.8 | 0.79
5965 | 17.2 | 0.61
5966 | 16.4 | 0.65
5967 | 16.6 | 0.61
5968 | 16.7 | 0.58
5969 | 16.9 | 0.53
5970 | 16.4 | 0.52
5971 | 15.2 | 0.61
5972 | 13.6 | 0.67
5973 | 12.5 | 0.77
5974 | 12 | 0.8
5975 | 11.4 | 0.83
5976 | 11.3 | 0.84
5977 | 10.9 | 0.85
5978 | 11.1 | 0.85
5979 | 11.6 | 0.79
5980 | 11.4 | 0.79
5981 | 11.4 | 0.78
5982 | 11.3 | 0.8
5983 | 11.6 | 0.81
5984 | 11.4 | 0.85
5985 | 11.7 | 0.85
5986 | 12.4 | 0.82
5987 | 13.5 | 0.75
5988 | 13.8 | 0.69
5989 | 15.3 | 0.59
5990 | 15.6 | 0.58
5991 | 15.4 | 0.6
5992 | 15.6 | 0.57
5993 | 15.8 | 0.57
5994 | 15.7 | 0.57
5995 | 15.1 | 0.6
5996 | 15 | 0.61
5997 | 14 | 0.67
5998 | 13.1 | 0.7
5999 | 12.2 | 0.76
6000 | 11.3 | 0.82
6001 | 10.7 | 0.85
6002 | 10.4 | 0.86
6003 | 10.1 | 0.88
6004 | 10 | 0.87
6005 | 9.8 | 0.88
6006 | 9.1 | 0.91
6007 | 9 | 0.93
6008 | 9.4 | 0.92
6009 | 11.4 | 0.89
6010 | 12.8 | 0.88
6011 | 14.6 | 0.79
6012 | 15.4 | 0.75
6013 | 15.5 | 0.77
6014 | 15.6 | 0.81
6015 | 15.1 | 0.86
6016 | 14.3 | 0.86
6017 | 14.4 | 0.87
6018 | 13.1 | 0.99
6019 | 13.3 | 1
6020 | 13 | 0.98
6021 | 12.7 | 0.98
6022 | 12.6 | 0.99
6023 | 12.6 | 1
6024 | 12.6 | 0.99
6025 | 12.6 | 0.98
6026 | 12.7 | 0.82
6027 | 11.8 | 0.94
6028 | 11.3 | 0.89
6029 | 10.5 | 0.9
6030 | 10.6 | 0.89
6031 | 10.7 | 0.87
6032 | 10.8 | 0.85
6033 | 11.9 | 0.83
6034 | 12.8 | 0.79
6035 | 13.8 | 0.7
6036 | 14.1 | 0.68
6037 | 15.6 | 0.57
6038 | 15.3 | 0.59
6039 | 15.8 | 0.6
6040 | 14.7 | 0.58
6041 | 13 | 0.76
6042 | 14.2 | 0.7
6043 | 14.2 | 0.66
6044 | 12.5 | 0.7
6045 | 11.4 | 0.76
6046 | 10.6 | 0.81
6047 | 10 | 0.83
6048 | 9.3 | 0.87
6049 | 9.4 | 0.85
6050 | 8.7 | 0.88
6051 | 8.5 | 0.9
6052 | 8.5 | 0.9
6053 | 8.2 | 0.92
6054 | 8.5 | 0.9
6055 | 8.6 | 0.9
6056 | 10.1 | 0.86
6057 | 11.1 | 0.81
6058 | 13.2 | 0.74
6059 | 14 | 0.66
6060 | 14.9 | 0.65
6061 | 14.4 | 0.7
6062 | 14.6 | 0.71
6063 | 15.1 | 0.73
6064 | 14.9 | 0.75
6065 | 14.7 | 0.81
6066 | 14.3 | 0.89
6067 | 13.6 | 0.95
6068 | 13.9 | 0.98
6069 | 14.2 | 0.99
6070 | 14.5 | 0.98
6071 | 14.8 | 0.98
6072 | 15 | 0.98
6073 | 15.1 | 0.98
6074 | 15.7 | 0.97
6075 | 15.7 | 0.97
6076 | 15.7 | 0.94
6077 | 15.9 | 0.94
6078 | 15.7 | 0.95
6079 | 15.7 | 0.97
6080 | 16 | 0.95
6081 | 15.6 | 0.9
6082 | 15.7 | 0.87
6083 | 16 | 0.79
6084 | 17.7 | 0.71
6085 | 18.2 | 0.65
6086 | 17.7 | 0.66
6087 | 18.9 | 0.56
6088 | 18.5 | 0.6
6089 | 18.6 | 0.58
6090 | 18.4 | 0.62
6091 | 17.2 | 0.67
6092 | 15.1 | 0.8
6093 | 14.6 | 0.83
6094 | 13.8 | 0.9
6095 | 13.8 | 0.86
6096 | 13.3 | 0.94
6097 | 13.5 | 0.99
6098 | 14.1 | 1
6099 | 14.9 | 0.99
6100 | 15.1 | 0.99
6101 | 15.1 | 0.99
6102 | 15.1 | 0.99
6103 | 14.7 | 0.98
6104 | 14.9 | 0.97
6105 | 15.1 | 0.99
6106 | 15.4 | 0.98
6107 | 15.8 | 0.99
6108 | 16.6 | 0.99
6109 | 17.6 | 0.93
6110 | 18.2 | 0.93
6111 | 17.5 | 0.83
6112 | 16.5 | 0.8
6113 | 16.2 | 0.74
6114 | 15.3 | 0.73
6115 | 14.5 | 0.69
6116 | 12.9 | 0.75
6117 | 11.9 | 0.75
6118 | 11.2 | 0.79
6119 | 10.5 | 0.83
6120 | 10.2 | 0.86
6121 | 9.7 | 0.87
6122 | 9.4 | 0.88
6123 | 8.2 | 0.92
6124 | 8.1 | 0.93
6125 | 8.5 | 0.9
6126 | 8.4 | 0.92
6127 | 8.6 | 0.9
6128 | 8.7 | 0.9
6129 | 10.5 | 0.87
6130 | 12.5 | 0.78
6131 | 14.3 | 0.73
6132 | 15.3 | 0.64
6133 | 16.1 | 0.54
6134 | 16.7 | 0.5
6135 | 17.2 | 0.53
6136 | 17.7 | 0.5
6137 | 16.1 | 0.65
6138 | 15.2 | 0.66
6139 | 13.7 | 0.73
6140 | 11.3 | 0.82
6141 | 11.4 | 0.82
6142 | 11.6 | 0.82
6143 | 11.3 | 0.84
6144 | 10.6 | 0.87
6145 | 10 | 0.88
6146 | 9.9 | 0.91
6147 | 9.1 | 0.92
6148 | 9.5 | 0.92
6149 | 9.1 | 0.93
6150 | 8.4 | 0.96
6151 | 8.3 | 0.96
6152 | 9.2 | 0.93
6153 | 11.7 | 0.93
6154 | 13.6 | 0.87
6155 | 14.4 | 0.82
6156 | 15.6 | 0.75
6157 | 17.1 | 0.68
6158 | 17.5 | 0.6
6159 | 17.9 | 0.66
6160 | 18.2 | 0.61
6161 | 18.2 | 0.63
6162 | 17.3 | 0.63
6163 | 16.3 | 0.71
6164 | 13.7 | 0.85
6165 | 13.1 | 0.88
6166 | 12.9 | 0.89
6167 | 12.1 | 0.9
6168 | 10.7 | 0.96
6169 | 10.7 | 0.95
6170 | 11.2 | 0.96
6171 | 11.1 | 0.97
6172 | 12.5 | 0.96
6173 | 12.7 | 0.98
6174 | 12.6 | 0.99
6175 | 13 | 0.99
6176 | 13.5 | 0.98
6177 | 13.7 | 0.99
6178 | 14.3 | 0.98
6179 | 15.3 | 0.97
6180 | 16.6 | 0.89
6181 | 16.9 | 0.88
6182 | 18.9 | 0.8
6183 | 19.3 | 0.78
6184 | 18.5 | 0.81
6185 | 18.4 | 0.79
6186 | 17.5 | 0.83
6187 | 16.8 | 0.86
6188 | 15.8 | 0.9
6189 | 15.2 | 0.92
6190 | 14.8 | 0.94
6191 | 14.7 | 0.94
6192 | 14.5 | 0.97
6193 | 14.6 | 0.97
6194 | 14.8 | 0.96
6195 | 14.9 | 0.97
6196 | 15 | 0.98
6197 | 15.1 | 0.97
6198 | 15.1 | 0.97
6199 | 15.1 | 0.97
6200 | 15.4 | 0.96
6201 | 15.9 | 0.94
6202 | 16.9 | 0.9
6203 | 17.3 | 0.87
6204 | 18.1 | 0.82
6205 | 18.7 | 0.8
6206 | 18.7 | 0.79
6207 | 17.3 | 0.9
6208 | 17.9 | 0.84
6209 | 18.3 | 0.78
6210 | 17.4 | 0.81
6211 | 14.8 | 0.96
6212 | 14.4 | 0.98
6213 | 13.9 | 0.98
6214 | 13.6 | 0.98
6215 | 13.2 | 0.98
6216 | 13.1 | 0.98
6217 | 12.8 | 0.98
6218 | 12.7 | 0.99
6219 | 12.6 | 0.96
6220 | 12.6 | 0.98
6221 | 12.2 | 0.96
6222 | 10.2 | 0.95
6223 | 9.2 | 0.96
6224 | 9.4 | 0.96
6225 | 10.7 | 0.89
6226 | 12.2 | 0.81
6227 | 13.8 | 0.75
6228 | 14.4 | 0.73
6229 | 15.5 | 0.67
6230 | 16.3 | 0.67
6231 | 16.7 | 0.65
6232 | 16.2 | 0.68
6233 | 15.3 | 0.67
6234 | 15 | 0.67
6235 | 13.6 | 0.77
6236 | 11.4 | 0.84
6237 | 11.1 | 0.85
6238 | 11.5 | 0.85
6239 | 11 | 0.87
6240 | 10.6 | 0.9
6241 | 10.4 | 0.91
6242 | 10.1 | 0.92
6243 | 9.7 | 0.93
6244 | 8.9 | 0.95
6245 | 8.7 | 0.96
6246 | 8.3 | 0.96
6247 | 8.3 | 0.93
6248 | 9 | 0.89
6249 | 10.7 | 0.86
6250 | 12.5 | 0.87
6251 | 13.7 | 0.86
6252 | 14.8 | 0.84
6253 | 16.3 | 0.75
6254 | 16.7 | 0.72
6255 | 17.3 | 0.68
6256 | 17.9 | 0.66
6257 | 17.8 | 0.64
6258 | 16.6 | 0.74
6259 | 14.9 | 0.82
6260 | 12.4 | 0.92
6261 | 11.7 | 0.96
6262 | 11.7 | 0.96
6263 | 12.1 | 0.98
6264 | 12.1 | 0.98
6265 | 11.8 | 0.98
6266 | 11 | 1
6267 | 10.4 | 1
6268 | 10.1 | 1
6269 | 9.8 | 1
6270 | 10.1 | 1
6271 | 10.2 | 1
6272 | 10.8 | 1
6273 | 11.8 | 1
6274 | 13.5 | 0.99
6275 | 14.7 | 0.9
6276 | 16.3 | 0.76
6277 | 17.7 | 0.64
6278 | 17.5 | 0.73
6279 | 17.6 | 0.7
6280 | 17.6 | 0.67
6281 | 17.1 | 0.73
6282 | 16.4 | 0.75
6283 | 15.2 | 0.8
6284 | 13.6 | 0.95
6285 | 13.1 | 0.94
6286 | 13.1 | 0.96
6287 | 12.9 | 1
6288 | 12.7 | 1
6289 | 12.5 | 0.96
6290 | 12.6 | 0.96
6291 | 12.5 | 0.96
6292 | 12.6 | 0.96
6293 | 12.6 | 0.98
6294 | 13.6 | 0.98
6295 | 13.4 | 0.94
6296 | 13.6 | 0.94
6297 | 14.4 | 0.9
6298 | 14.8 | 0.9
6299 | 15 | 0.86
6300 | 16 | 0.8
6301 | 16.1 | 0.79
6302 | 16.1 | 0.76
6303 | 16.2 | 0.76
6304 | 15.6 | 0.81
6305 | 15.8 | 0.77
6306 | 15.5 | 0.79
6307 | 14.9 | 0.83
6308 | 14.1 | 0.8
6309 | 14 | 0.79
6310 | 13.7 | 0.83
6311 | 13.9 | 0.84
6312 | 14.1 | 0.87
6313 | 14.7 | 0.85
6314 | 14.9 | 0.85
6315 | 15.2 | 0.84
6316 | 15.3 | 0.84
6317 | 15 | 0.85
6318 | 14.9 | 0.86
6319 | 15.3 | 0.86
6320 | 15.5 | 0.86
6321 | 15.4 | 0.89
6322 | 15.1 | 0.93
6323 | 15 | 0.98
6324 | 15.4 | 0.98
6325 | 15.7 | 0.98
6326 | 15.9 | 0.97
6327 | 15.9 | 0.98
6328 | 15.9 | 0.98
6329 | 15.7 | 0.99
6330 | 15.7 | 0.99
6331 | 15.6 | 0.99
6332 | 15.6 | 0.99
6333 | 15.6 | 0.99
6334 | 15.6 | 0.98
6335 | 14.3 | 0.98
6336 | 14.5 | 0.99
6337 | 14.7 | 0.99
6338 | 14.7 | 1
6339 | 14.8 | 0.99
6340 | 14.3 | 1
6341 | 14.1 | 1
6342 | 14 | 0.99
6343 | 13.6 | 0.99
6344 | 13 | 0.98
6345 | 13.2 | 0.99
6346 | 14 | 0.97
6347 | 14.7 | 0.89
6348 | 15.9 | 0.78
6349 | 15.9 | 0.77
6350 | 14.4 | 0.84
6351 | 16.2 | 0.69
6352 | 16.4 | 0.65
6353 | 16.1 | 0.66
6354 | 15.2 | 0.7
6355 | 14.5 | 0.75
6356 | 12.9 | 0.84
6357 | 11.6 | 0.85
6358 | 10.7 | 0.9
6359 | 9.9 | 0.92
6360 | 8.8 | 0.97
6361 | 8.4 | 0.97
6362 | 8.9 | 0.99
6363 | 10.2 | 0.97
6364 | 10.6 | 0.99
6365 | 12 | 0.98
6366 | 13.1 | 0.96
6367 | 13.8 | 0.98
6368 | 14.2 | 0.97
6369 | 13.6 | 0.97
6370 | 13.8 | 0.97
6371 | 14.1 | 0.99
6372 | 14.5 | 0.99
6373 | 15.9 | 0.98
6374 | 17.2 | 0.95
6375 | 16.9 | 0.96
6376 | 17.2 | 0.93
6377 | 16.3 | 0.98
6378 | 16.1 | 0.98
6379 | 16 | 0.97
6380 | 15.7 | 0.98
6381 | 15.6 | 0.99
6382 | 15.7 | 0.99
6383 | 15.5 | 0.98
6384 | 15.2 | 0.98
6385 | 14.6 | 0.97
6386 | 14.4 | 0.98
6387 | 14.3 | 0.99
6388 | 14.5 | 0.98
6389 | 14.2 | 0.98
6390 | 14 | 0.97
6391 | 13.3 | 0.96
6392 | 13.6 | 0.94
6393 | 14.3 | 0.92
6394 | 14.1 | 0.95
6395 | 14.3 | 0.99
6396 | 14.9 | 0.97
6397 | 15.2 | 0.95
6398 | 15 | 0.94
6399 | 14.1 | 0.95
6400 | 14 | 0.98
6401 | 14.1 | 0.99
6402 | 14.8 | 0.99
6403 | 14.9 | 0.98
6404 | 14.9 | 0.97
6405 | 14.4 | 0.97
6406 | 14.3 | 0.97
6407 | 14.4 | 0.93
6408 | 14.2 | 0.92
6409 | 14.4 | 0.92
6410 | 14.1 | 0.91
6411 | 13.8 | 0.92
6412 | 13.4 | 0.91
6413 | 13.6 | 0.97
6414 | 13.4 | 0.95
6415 | 13.1 | 0.92
6416 | 12.1 | 0.98
6417 | 12.8 | 0.91
6418 | 13 | 0.92
6419 | 13.7 | 0.94
6420 | 14.6 | 0.97
6421 | 16 | 0.95
6422 | 16.1 | 0.94
6423 | 16.3 | 0.94
6424 | 16.5 | 0.9
6425 | 15.6 | 0.96
6426 | 15.1 | 0.97
6427 | 14.9 | 0.98
6428 | 15.3 | 0.99
6429 | 15.3 | 0.98
6430 | 14.6 | 0.96
6431 | 14 | 0.93
6432 | 12.8 | 0.93
6433 | 12.1 | 0.95
6434 | 12.6 | 0.95
6435 | 12.2 | 0.89
6436 | 11.8 | 0.95
6437 | 11.9 | 0.9
6438 | 11.8 | 0.91
6439 | 11 | 0.91
6440 | 11.1 | 0.92
6441 | 12 | 0.89
6442 | 12.8 | 0.87
6443 | 13.9 | 0.83
6444 | 14.3 | 0.81
6445 | 13.8 | 0.87
6446 | 14.5 | 0.81
6447 | 14.8 | 0.83
6448 | 13.5 | 0.93
6449 | 14.3 | 0.82
6450 | 14 | 0.82
6451 | 12.9 | 0.85
6452 | 12.1 | 0.88
6453 | 12.1 | 0.94
6454 | 11.8 | 0.91
6455 | 11.4 | 0.93
6456 | 11.5 | 0.94
6457 | 11.8 | 0.94
6458 | 12.1 | 0.93
6459 | 12.3 | 0.94
6460 | 12.2 | 0.92
6461 | 12.3 | 0.93
6462 | 12.3 | 0.94
6463 | 12.3 | 0.94
6464 | 12.2 | 0.94
6465 | 11.5 | 0.9
6466 | 12.3 | 0.93
6467 | 13.7 | 0.82
6468 | 14.8 | 0.7
6469 | 15.2 | 0.64
6470 | 14.4 | 0.65
6471 | 15.1 | 0.64
6472 | 16.1 | 0.63
6473 | 15.8 | 0.61
6474 | 14.5 | 0.72
6475 | 13.1 | 0.78
6476 | 11.1 | 0.89
6477 | 11.6 | 0.9
6478 | 11.9 | 0.95
6479 | 12.5 | 0.95
6480 | 12.9 | 0.93
6481 | 12.7 | 0.96
6482 | 12.5 | 0.95
6483 | 12.7 | 0.92
6484 | 12.4 | 0.95
6485 | 12.1 | 0.93
6486 | 11.8 | 0.94
6487 | 11.4 | 0.94
6488 | 11.4 | 0.94
6489 | 11.9 | 0.93
6490 | 12.8 | 0.88
6491 | 12.8 | 0.84
6492 | 13.3 | 0.78
6493 | 13.3 | 0.78
6494 | 13.5 | 0.85
6495 | 13.3 | 0.9
6496 | 12.6 | 0.95
6497 | 12.1 | 0.98
6498 | 12.4 | 0.98
6499 | 13 | 0.99
6500 | 13.7 | 0.99
6501 | 15.4 | 0.99
6502 | 15.3 | 0.99
6503 | 14.9 | 0.99
6504 | 14.9 | 0.98
6505 | 14.9 | 0.99
6506 | 14.8 | 0.99
6507 | 11.2 | 0.96
6508 | 10.7 | 0.99
6509 | 10.9 | 0.96
6510 | 10.9 | 0.96
6511 | 11.2 | 0.91
6512 | 11.3 | 0.91
6513 | 12 | 0.88
6514 | 13.6 | 0.84
6515 | 14.2 | 0.83
6516 | 14.8 | 0.81
6517 | 15.6 | 0.74
6518 | 16.3 | 0.65
6519 | 15.7 | 0.72
6520 | 16.4 | 0.7
6521 | 15.7 | 0.72
6522 | 15.4 | 0.74
6523 | 13.5 | 0.78
6524 | 11.9 | 0.82
6525 | 11.3 | 0.86
6526 | 10.9 | 0.87
6527 | 10.4 | 0.91
6528 | 10.2 | 0.91
6529 | 9.6 | 0.95
6530 | 10.2 | 0.93
6531 | 9.6 | 0.95
6532 | 9.3 | 0.96
6533 | 9.5 | 0.96
6534 | 10.5 | 0.92
6535 | 10.4 | 0.97
6536 | 11 | 0.97
6537 | 11.5 | 0.99
6538 | 11.2 | 0.97
6539 | 11.6 | 0.98
6540 | 12.9 | 1
6541 | 13.6 | 0.99
6542 | 15.8 | 0.99
6543 | 15.8 | 0.99
6544 | 16 | 0.94
6545 | 15.9 | 0.84
6546 | 14.9 | 0.87
6547 | 14.1 | 0.93
6548 | 14 | 0.94
6549 | 14.1 | 0.98
6550 | 14.2 | 0.98
6551 | 13.3 | 0.96
6552 | 13.6 | 0.99
6553 | 14 | 0.98
6554 | 13.7 | 0.98
6555 | 13.8 | 0.98
6556 | 13.5 | 0.99
6557 | 13.4 | 0.98
6558 | 13.5 | 0.99
6559 | 13.3 | 0.98
6560 | 12.9 | 0.98
6561 | 12.7 | 0.96
6562 | 12.6 | 0.94
6563 | 12.5 | 0.9
6564 | 12.1 | 0.88
6565 | 12.6 | 0.79
6566 | 11.8 | 0.81
6567 | 12.1 | 0.75
6568 | 11.9 | 0.76
6569 | 12.3 | 0.72
6570 | 12 | 0.69
6571 | 11.5 | 0.72
6572 | 10.5 | 0.71
6573 | 9.4 | 0.75
6574 | 8.5 | 0.81
6575 | 8 | 0.8
6576 | 7.6 | 0.8
6577 | 6.8 | 0.82
6578 | 6.6 | 0.87
6579 | 5.7 | 0.85
6580 | 5.2 | 0.92
6581 | 4.8 | 0.92
6582 | 4.7 | 0.89
6583 | 4.7 | 0.89
6584 | 4.5 | 0.89
6585 | 5.2 | 0.86
6586 | 6.5 | 0.84
6587 | 8.9 | 0.76
6588 | 10.5 | 0.7
6589 | 11.4 | 0.58
6590 | 11.6 | 0.56
6591 | 12.3 | 0.6
6592 | 12 | 0.63
6593 | 11.2 | 0.67
6594 | 10.2 | 0.73
6595 | 9.1 | 0.81
6596 | 8.4 | 0.82
6597 | 8.5 | 0.79
6598 | 8.2 | 0.82
6599 | 9.2 | 0.83
6600 | 9.3 | 0.84
6601 | 9.5 | 0.84
6602 | 9.5 | 0.85
6603 | 10.4 | 0.8
6604 | 10.9 | 0.81
6605 | 11.2 | 0.81
6606 | 11.7 | 0.83
6607 | 12.4 | 0.83
6608 | 12.7 | 0.88
6609 | 13.3 | 0.82
6610 | 12.6 | 0.96
6611 | 12.6 | 0.99
6612 | 13.3 | 0.99
6613 | 14.4 | 0.99
6614 | 15.2 | 0.98
6615 | 14.8 | 0.98
6616 | 14.7 | 0.94
6617 | 14.2 | 0.91
6618 | 14 | 0.83
6619 | 12.7 | 0.77
6620 | 12.3 | 0.76
6621 | 11.5 | 0.84
6622 | 12.2 | 0.76
6623 | 12.2 | 0.8
6624 | 12.2 | 0.74
6625 | 12.1 | 0.76
6626 | 11.9 | 0.78
6627 | 11.9 | 0.77
6628 | 11.9 | 0.76
6629 | 12.3 | 0.73
6630 | 11.2 | 0.79
6631 | 11.5 | 0.78
6632 | 12.2 | 0.74
6633 | 12.7 | 0.71
6634 | 13.9 | 0.68
6635 | 14 | 0.68
6636 | 14.7 | 0.66
6637 | 14.8 | 0.68
6638 | 15.5 | 0.65
6639 | 16.1 | 0.63
6640 | 15.4 | 0.62
6641 | 15.1 | 0.63
6642 | 14.1 | 0.68
6643 | 13.4 | 0.72
6644 | 12.8 | 0.72
6645 | 12.6 | 0.82
6646 | 11.5 | 0.85
6647 | 11.4 | 0.93
6648 | 12 | 0.95
6649 | 12.4 | 0.99
6650 | 13.1 | 1
6651 | 13.5 | 0.99
6652 | 13.8 | 0.99
6653 | 13.6 | 0.99
6654 | 13.6 | 0.99
6655 | 13.8 | 0.99
6656 | 13.9 | 0.99
6657 | 14 | 0.99
6658 | 14.1 | 0.99
6659 | 14.1 | 0.99
6660 | 14.4 | 0.99
6661 | 14.6 | 0.99
6662 | 14.8 | 0.99
6663 | 15 | 0.99
6664 | 15.8 | 0.99
6665 | 16.5 | 0.83
6666 | 15.6 | 0.84
6667 | 14 | 0.88
6668 | 13 | 0.86
6669 | 12.2 | 0.86
6670 | 11.3 | 0.88
6671 | 10.5 | 0.87
6672 | 10.1 | 0.88
6673 | 10 | 0.9
6674 | 9.3 | 0.92
6675 | 9.6 | 0.91
6676 | 9.9 | 0.87
6677 | 9.9 | 0.87
6678 | 9.8 | 0.87
6679 | 9.9 | 0.86
6680 | 10 | 0.86
6681 | 10.4 | 0.85
6682 | 11.8 | 0.81
6683 | 12.6 | 0.77
6684 | 13.1 | 0.73
6685 | 13.6 | 0.67
6686 | 14.1 | 0.71
6687 | 13.8 | 0.69
6688 | 13.4 | 0.73
6689 | 12.7 | 0.77
6690 | 11.9 | 0.85
6691 | 11.8 | 0.88
6692 | 11.5 | 0.93
6693 | 11.2 | 0.94
6694 | 10.4 | 0.97
6695 | 10.8 | 0.97
6696 | 10.9 | 0.97
6697 | 11.7 | 0.98
6698 | 12.2 | 1
6699 | 13.1 | 0.99
6700 | 13.7 | 0.99
6701 | 14.3 | 0.99
6702 | 13.8 | 0.99
6703 | 13.3 | 0.98
6704 | 12.7 | 0.98
6705 | 12.8 | 0.98
6706 | 13.5 | 0.93
6707 | 14.5 | 0.88
6708 | 15.1 | 0.75
6709 | 15.4 | 0.79
6710 | 14 | 0.86
6711 | 14.9 | 0.83
6712 | 14.9 | 0.8
6713 | 15 | 0.72
6714 | 13.8 | 0.74
6715 | 12.5 | 0.86
6716 | 11.8 | 0.88
6717 | 11.2 | 0.91
6718 | 10.8 | 0.94
6719 | 10.9 | 0.92
6720 | 10.6 | 0.91
6721 | 11.1 | 0.9
6722 | 10.8 | 0.91
6723 | 10.9 | 0.91
6724 | 10.9 | 0.94
6725 | 10.1 | 0.92
6726 | 9.7 | 0.93
6727 | 9.5 | 0.95
6728 | 9.3 | 0.96
6729 | 9.9 | 0.86
6730 | 10.6 | 0.81
6731 | 11.1 | 0.81
6732 | 11.4 | 0.82
6733 | 12.5 | 0.71
6734 | 12.9 | 0.72
6735 | 11.7 | 0.82
6736 | 12.4 | 0.78
6737 | 12.4 | 0.73
6738 | 11.6 | 0.76
6739 | 10.2 | 0.83
6740 | 9.9 | 0.83
6741 | 9.7 | 0.88
6742 | 9.1 | 0.92
6743 | 9.5 | 0.88
6744 | 9.4 | 0.91
6745 | 8.9 | 0.93
6746 | 8.8 | 0.89
6747 | 8.2 | 0.86
6748 | 7.3 | 0.84
6749 | 7.8 | 0.84
6750 | 7.7 | 0.89
6751 | 7.8 | 0.89
6752 | 7.9 | 0.89
6753 | 8.4 | 0.88
6754 | 10.2 | 0.82
6755 | 11 | 0.8
6756 | 12.6 | 0.76
6757 | 10.6 | 0.86
6758 | 11.9 | 0.77
6759 | 12.9 | 0.74
6760 | 12.9 | 0.63
6761 | 12 | 0.74
6762 | 11.9 | 0.68
6763 | 9.9 | 0.79
6764 | 8.8 | 0.84
6765 | 8.8 | 0.82
6766 | 7.3 | 0.88
6767 | 8.6 | 0.86
6768 | 9.1 | 0.87
6769 | 8.2 | 0.89
6770 | 9.1 | 0.87
6771 | 8.3 | 0.9
6772 | 9 | 0.92
6773 | 9.5 | 0.91
6774 | 10.2 | 0.91
6775 | 10.7 | 0.9
6776 | 10.4 | 0.96
6777 | 11.5 | 1
6778 | 12.7 | 0.96
6779 | 13.5 | 0.92
6780 | 13.4 | 0.91
6781 | 14.3 | 0.91
6782 | 14.8 | 0.86
6783 | 13.7 | 0.98
6784 | 13.9 | 0.95
6785 | 13.4 | 0.86
6786 | 13.1 | 0.85
6787 | 13 | 0.89
6788 | 12.8 | 0.95
6789 | 12.6 | 0.94
6790 | 11.6 | 0.94
6791 | 12.5 | 0.94
6792 | 12.6 | 0.94
6793 | 12.3 | 0.96
6794 | 12.3 | 0.98
6795 | 12.1 | 0.98
6796 | 11.6 | 0.98
6797 | 11.3 | 0.99
6798 | 10.5 | 0.97
6799 | 10.1 | 0.96
6800 | 9.5 | 0.97
6801 | 8.8 | 0.99
6802 | 10.7 | 0.96
6803 | 12.3 | 0.87
6804 | 13.3 | 0.76
6805 | 14 | 0.7
6806 | 12.9 | 0.72
6807 | 12.7 | 0.77
6808 | 12.3 | 0.76
6809 | 11.7 | 0.76
6810 | 11 | 0.86
6811 | 10.4 | 0.91
6812 | 10.1 | 0.91
6813 | 9.4 | 0.92
6814 | 9.1 | 0.92
6815 | 8.3 | 0.94
6816 | 8.3 | 0.94
6817 | 7.9 | 0.96
6818 | 7.3 | 0.97
6819 | 7.2 | 0.97
6820 | 6.9 | 0.97
6821 | 6.7 | 0.98
6822 | 6.4 | 0.98
6823 | 6.1 | 0.98
6824 | 5.8 | 0.98
6825 | 8 | 0.99
6826 | 10.4 | 0.94
6827 | 12.6 | 0.87
6828 | 13.1 | 0.8
6829 | 13.4 | 0.76
6830 | 14.1 | 0.7
6831 | 13.9 | 0.68
6832 | 12.9 | 0.74
6833 | 12.3 | 0.8
6834 | 11.3 | 0.89
6835 | 10.2 | 0.92
6836 | 9.5 | 0.93
6837 | 8.4 | 0.94
6838 | 8.9 | 0.95
6839 | 8.8 | 0.97
6840 | 9.2 | 0.96
6841 | 9.4 | 0.96
6842 | 9.3 | 0.97
6843 | 9.2 | 0.97
6844 | 9 | 0.97
6845 | 8.4 | 0.97
6846 | 8.4 | 0.97
6847 | 8.3 | 0.99
6848 | 8.2 | 0.99
6849 | 8.5 | 0.97
6850 | 9.5 | 0.96
6851 | 10 | 0.96
6852 | 11.6 | 0.89
6853 | 12.3 | 0.81
6854 | 12.1 | 0.74
6855 | 13.4 | 0.7
6856 | 11.4 | 0.78
6857 | 12.3 | 0.75
6858 | 11 | 0.78
6859 | 8.1 | 0.86
6860 | 7.8 | 0.9
6861 | 7.6 | 0.9
6862 | 8.4 | 0.9
6863 | 9 | 0.9
6864 | 9.6 | 0.92
6865 | 10.5 | 0.92
6866 | 10.8 | 0.92
6867 | 11.4 | 0.94
6868 | 12 | 0.94
6869 | 12.2 | 0.95
6870 | 12.3 | 0.95
6871 | 12.6 | 0.94
6872 | 12.5 | 0.93
6873 | 12.6 | 0.92
6874 | 13 | 0.95
6875 | 12.9 | 0.98
6876 | 12.8 | 0.96
6877 | 11.8 | 0.96
6878 | 12 | 0.98
6879 | 11.9 | 0.96
6880 | 12.3 | 0.98
6881 | 12.1 | 0.96
6882 | 12.1 | 0.98
6883 | 11.6 | 0.98
6884 | 11.6 | 0.96
6885 | 11.6 | 0.96
6886 | 10.2 | 0.97
6887 | 10 | 0.96
6888 | 9.9 | 0.97
6889 | 9.8 | 0.97
6890 | 9.8 | 0.97
6891 | 9.6 | 0.97
6892 | 8.9 | 0.96
6893 | 8.3 | 0.94
6894 | 8.7 | 0.94
6895 | 8.7 | 0.94
6896 | 7.2 | 0.9
6897 | 7.5 | 0.94
6898 | 9.8 | 0.86
6899 | 10.9 | 0.86
6900 | 11.7 | 0.85
6901 | 11.8 | 0.87
6902 | 12.4 | 0.88
6903 | 12.6 | 0.89
6904 | 12.1 | 0.92
6905 | 11.7 | 0.96
6906 | 11.8 | 0.98
6907 | 12.5 | 0.98
6908 | 12.8 | 0.98
6909 | 13.2 | 0.98
6910 | 10.8 | 0.97
6911 | 9.8 | 0.91
6912 | 8.6 | 0.89
6913 | 7.4 | 0.9
6914 | 7.4 | 0.88
6915 | 7.1 | 0.88
6916 | 6.6 | 0.9
6917 | 6.1 | 0.91
6918 | 6 | 0.92
6919 | 6.6 | 0.9
6920 | 6.1 | 0.92
6921 | 7.3 | 0.88
6922 | 9.2 | 0.85
6923 | 10.7 | 0.81
6924 | 11.9 | 0.76
6925 | 12.5 | 0.68
6926 | 12.2 | 0.72
6927 | 11.5 | 0.75
6928 | 11.9 | 0.7
6929 | 11 | 0.74
6930 | 10.2 | 0.78
6931 | 9 | 0.84
6932 | 9.6 | 0.82
6933 | 9.9 | 0.87
6934 | 8.8 | 0.88
6935 | 8.6 | 0.89
6936 | 8.3 | 0.92
6937 | 8.6 | 0.9
6938 | 9.4 | 0.89
6939 | 8.9 | 0.9
6940 | 9.1 | 0.89
6941 | 9.6 | 0.88
6942 | 9.3 | 0.91
6943 | 9.8 | 0.87
6944 | 9.5 | 0.93
6945 | 9 | 0.92
6946 | 9.3 | 0.93
6947 | 10.4 | 0.88
6948 | 11.2 | 0.85
6949 | 11.4 | 0.8
6950 | 8.6 | 0.93
6951 | 10.2 | 0.78
6952 | 10.2 | 0.83
6953 | 9.3 | 0.83
6954 | 7.5 | 0.88
6955 | 7.1 | 0.93
6956 | 6.8 | 0.96
6957 | 7.4 | 0.9
6958 | 7.9 | 0.91
6959 | 8 | 0.9
6960 | 8.1 | 0.89
6961 | 8.1 | 0.93
6962 | 9.4 | 0.88
6963 | 8.8 | 0.89
6964 | 8.1 | 0.92
6965 | 7.6 | 0.93
6966 | 8 | 0.93
6967 | 8.4 | 0.92
6968 | 8.9 | 0.93
6969 | 8.2 | 0.92
6970 | 9.5 | 0.91
6971 | 10.4 | 0.87
6972 | 10.4 | 0.86
6973 | 11 | 0.8
6974 | 11.3 | 0.79
6975 | 11.5 | 0.75
6976 | 11.6 | 0.73
6977 | 10.8 | 0.78
6978 | 10.5 | 0.8
6979 | 9.5 | 0.85
6980 | 8.5 | 0.9
6981 | 8.1 | 0.9
6982 | 8 | 0.92
6983 | 7.8 | 0.91
6984 | 7.8 | 0.9
6985 | 7.6 | 0.91
6986 | 7.5 | 0.91
6987 | 7.3 | 0.93
6988 | 7.3 | 0.93
6989 | 7.4 | 0.93
6990 | 7.3 | 0.93
6991 | 6.6 | 0.94
6992 | 6.5 | 0.94
6993 | 6.8 | 0.94
6994 | 7.9 | 0.89
6995 | 9.9 | 0.83
6996 | 11.2 | 0.81
6997 | 11 | 0.78
6998 | 10.6 | 0.82
6999 | 12.1 | 0.74
7000 | 11 | 0.84
7001 | 11.2 | 0.8
7002 | 10.8 | 0.82
7003 | 10 | 0.87
7004 | 9.6 | 0.89
7005 | 9 | 0.89
7006 | 8.3 | 0.87
7007 | 7.4 | 0.9
7008 | 7 | 0.91
7009 | 6.9 | 0.93
7010 | 7 | 0.94
7011 | 7.7 | 0.93
7012 | 7.6 | 0.93
7013 | 7.6 | 0.91
7014 | 7.3 | 0.88
7015 | 6.9 | 0.91
7016 | 6.9 | 0.91
7017 | 7.6 | 0.91
7018 | 8.9 | 0.88
7019 | 10.2 | 0.8
7020 | 10.7 | 0.74
7021 | 11.2 | 0.7
7022 | 11.5 | 0.6
7023 | 10.5 | 0.6
7024 | 10.3 | 0.54
7025 | 9.7 | 0.58
7026 | 9.3 | 0.61
7027 | 8.4 | 0.69
7028 | 7.8 | 0.72
7029 | 7.2 | 0.76
7030 | 6.4 | 0.81
7031 | 6.9 | 0.8
7032 | 6 | 0.83
7033 | 5.1 | 0.87
7034 | 4.8 | 0.89
7035 | 5.1 | 0.87
7036 | 4.7 | 0.87
7037 | 4 | 0.9
7038 | 3.7 | 0.9
7039 | 3.6 | 0.9
7040 | 3.6 | 0.9
7041 | 3.6 | 0.88
7042 | 4.9 | 0.86
7043 | 7 | 0.78
7044 | 9.1 | 0.73
7045 | 10.3 | 0.69
7046 | 11 | 0.67
7047 | 11.6 | 0.59
7048 | 11.9 | 0.58
7049 | 11.4 | 0.55
7050 | 10.8 | 0.6
7051 | 9.1 | 0.65
7052 | 8.7 | 0.65
7053 | 7.2 | 0.74
7054 | 7 | 0.75
7055 | 6.8 | 0.77
7056 | 6.6 | 0.69
7057 | 4.7 | 0.79
7058 | 5.6 | 0.8
7059 | 5.3 | 0.83
7060 | 6.1 | 0.79
7061 | 6.4 | 0.84
7062 | 6.3 | 0.83
7063 | 6.6 | 0.82
7064 | 6.8 | 0.85
7065 | 7.2 | 0.84
7066 | 8 | 0.85
7067 | 8.6 | 0.82
7068 | 9 | 0.84
7069 | 9.8 | 0.8
7070 | 10.4 | 0.8
7071 | 10.6 | 0.77
7072 | 10.4 | 0.8
7073 | 10.1 | 0.83
7074 | 10.1 | 0.84
7075 | 9.8 | 0.87
7076 | 9.9 | 0.87
7077 | 9.9 | 0.9
7078 | 10.1 | 0.91
7079 | 10.8 | 0.9
7080 | 10.3 | 0.92
7081 | 10.7 | 0.9
7082 | 10.6 | 0.89
7083 | 10.6 | 0.89
7084 | 10.5 | 0.9
7085 | 10.8 | 0.87
7086 | 10.7 | 0.89
7087 | 10.9 | 0.86
7088 | 10.8 | 0.86
7089 | 11.1 | 0.86
7090 | 11.3 | 0.85
7091 | 12 | 0.84
7092 | 12 | 0.83
7093 | 11.8 | 0.85
7094 | 11.4 | 0.93
7095 | 11.1 | 0.97
7096 | 11.3 | 0.97
7097 | 11.4 | 0.97
7098 | 11.7 | 0.98
7099 | 11.7 | 0.98
7100 | 11.9 | 0.99
7101 | 10.8 | 0.99
7102 | 9.2 | 0.99
7103 | 8.8 | 0.99
7104 | 8.9 | 0.99
7105 | 9.5 | 0.99
7106 | 8.7 | 0.99
7107 | 6.9 | 1
7108 | 7.4 | 1
7109 | 7.5 | 0.99
7110 | 7.1 | 0.99
7111 | 5.6 | 0.98
7112 | 5.9 | 0.97
7113 | 6.3 | 0.98
7114 | 8.9 | 0.97
7115 | 10.4 | 0.87
7116 | 11.4 | 0.84
7117 | 11.6 | 0.76
7118 | 12.6 | 0.72
7119 | 11.3 | 0.7
7120 | 11.7 | 0.72
7121 | 9.5 | 0.87
7122 | 9.4 | 0.84
7123 | 8.9 | 0.86
7124 | 8.3 | 0.86
7125 | 8.2 | 0.85
7126 | 8.2 | 0.83
7127 | 7.7 | 0.87
7128 | 7.9 | 0.86
7129 | 7.7 | 0.83
7130 | 7.4 | 0.84
7131 | 7 | 0.91
7132 | 7.3 | 0.86
7133 | 7.6 | 0.9
7134 | 7.3 | 0.96
7135 | 7.5 | 0.97
7136 | 7.6 | 0.99
7137 | 7.5 | 0.97
7138 | 7.2 | 0.99
7139 | 7 | 0.97
7140 | 7 | 0.99
7141 | 6.6 | 0.95
7142 | 6.9 | 0.96
7143 | 6.8 | 0.96
7144 | 6.5 | 0.94
7145 | 6.4 | 0.94
7146 | 6.4 | 0.92
7147 | 6.2 | 0.94
7148 | 6.1 | 0.95
7149 | 5.9 | 0.95
7150 | 5.9 | 0.95
7151 | 5.8 | 0.95
7152 | 5.7 | 0.95
7153 | 5.5 | 0.97
7154 | 5.4 | 0.97
7155 | 5.3 | 0.95
7156 | 5.1 | 0.97
7157 | 5 | 0.98
7158 | 4.8 | 0.98
7159 | 4.7 | 0.97
7160 | 4.5 | 0.95
7161 | 4.6 | 0.93
7162 | 4.5 | 0.93
7163 | 5.2 | 0.92
7164 | 6.9 | 0.87
7165 | 7.8 | 0.75
7166 | 8.4 | 0.65
7167 | 8.6 | 0.6
7168 | 8.3 | 0.62
7169 | 8.1 | 0.64
7170 | 7.2 | 0.64
7171 | 5.9 | 0.7
7172 | 5.3 | 0.72
7173 | 4.8 | 0.73
7174 | 4.4 | 0.74
7175 | 3.8 | 0.78
7176 | 4.1 | 0.79
7177 | 4.1 | 0.79
7178 | 3.6 | 0.81
7179 | 2.4 | 0.87
7180 | 3.3 | 0.83
7181 | 3.3 | 0.83
7182 | 2.3 | 0.87
7183 | 3.4 | 0.83
7184 | 2.4 | 0.89
7185 | 3.6 | 0.86
7186 | 4.4 | 0.84
7187 | 6.9 | 0.75
7188 | 7.7 | 0.76
7189 | 8.7 | 0.7
7190 | 9.3 | 0.61
7191 | 9.7 | 0.57
7192 | 9.7 | 0.57
7193 | 9.4 | 0.56
7194 | 7.9 | 0.64
7195 | 6.4 | 0.72
7196 | 5.6 | 0.77
7197 | 5.6 | 0.75
7198 | 4.8 | 0.79
7199 | 4.3 | 0.82
7200 | 4.3 | 0.8
7201 | 4.2 | 0.82
7202 | 3.4 | 0.86
7203 | 3.8 | 0.85
7204 | 4.1 | 0.85
7205 | 4 | 0.85
7206 | 4.1 | 0.85
7207 | 4.5 | 0.82
7208 | 4.6 | 0.81
7209 | 5.2 | 0.8
7210 | 6.1 | 0.79
7211 | 7.8 | 0.72
7212 | 8.5 | 0.66
7213 | 8.4 | 0.71
7214 | 8.7 | 0.77
7215 | 8.2 | 0.78
7216 | 8.5 | 0.77
7217 | 8.4 | 0.73
7218 | 7.8 | 0.75
7219 | 7.4 | 0.72
7220 | 6.7 | 0.74
7221 | 5.8 | 0.79
7222 | 5.8 | 0.76
7223 | 6 | 0.74
7224 | 6.4 | 0.75
7225 | 6.5 | 0.75
7226 | 6.7 | 0.75
7227 | 6.7 | 0.76
7228 | 6.6 | 0.78
7229 | 6.7 | 0.79
7230 | 6.8 | 0.79
7231 | 6.9 | 0.8
7232 | 7 | 0.82
7233 | 7.1 | 0.84
7234 | 7.4 | 0.84
7235 | 7.7 | 0.82
7236 | 8.5 | 0.79
7237 | 9.4 | 0.75
7238 | 10 | 0.73
7239 | 9.3 | 0.76
7240 | 8.9 | 0.77
7241 | 8.8 | 0.78
7242 | 8.9 | 0.77
7243 | 9.1 | 0.79
7244 | 9.3 | 0.8
7245 | 9.5 | 0.82
7246 | 9.6 | 0.82
7247 | 9.8 | 0.8
7248 | 9.7 | 0.82
7249 | 9.6 | 0.82
7250 | 9.6 | 0.83
7251 | 9.5 | 0.87
7252 | 9.5 | 0.87
7253 | 9.4 | 0.88
7254 | 9.4 | 0.91
7255 | 10.1 | 0.87
7256 | 9.7 | 0.93
7257 | 9.5 | 0.96
7258 | 9.6 | 0.97
7259 | 9.7 | 0.96
7260 | 9.8 | 0.95
7261 | 9.8 | 0.96
7262 | 9.8 | 0.97
7263 | 9.8 | 0.97
7264 | 10 | 0.97
7265 | 10.1 | 0.97
7266 | 10.2 | 0.97
7267 | 10.3 | 0.97
7268 | 10.3 | 0.99
7269 | 10.2 | 0.97
7270 | 10.1 | 0.99
7271 | 10.1 | 0.99
7272 | 10 | 0.99
7273 | 10.1 | 0.97
7274 | 10 | 0.97
7275 | 10.2 | 0.99
7276 | 10.2 | 0.97
7277 | 10.2 | 0.99
7278 | 10.4 | 0.99
7279 | 10.5 | 1
7280 | 10.7 | 1
7281 | 10.8 | 0.99
7282 | 11.1 | 1
7283 | 11.6 | 0.99
7284 | 11.9 | 0.99
7285 | 12.2 | 0.98
7286 | 12.3 | 0.99
7287 | 12.3 | 0.98
7288 | 12 | 0.98
7289 | 11.8 | 0.98
7290 | 11.9 | 0.99
7291 | 12.1 | 0.99
7292 | 12.2 | 0.99
7293 | 12.5 | 1
7294 | 12.5 | 1
7295 | 12.6 | 0.99
7296 | 13 | 1
7297 | 13 | 1
7298 | 12.6 | 0.99
7299 | 12.4 | 0.99
7300 | 12.4 | 0.98
7301 | 12.4 | 0.96
7302 | 12.5 | 0.96
7303 | 12.2 | 0.96
7304 | 12.1 | 0.96
7305 | 12.2 | 0.95
7306 | 12.5 | 0.98
7307 | 12.9 | 0.98
7308 | 12.6 | 0.98
7309 | 12.8 | 0.99
7310 | 12.9 | 0.98
7311 | 13.2 | 1
7312 | 13.1 | 0.98
7313 | 12.6 | 0.96
7314 | 12.4 | 0.98
7315 | 12.2 | 0.96
7316 | 11.1 | 0.91
7317 | 10.6 | 0.94
7318 | 9.3 | 0.92
7319 | 8.5 | 0.93
7320 | 8.2 | 0.96
7321 | 8.2 | 0.96
7322 | 8 | 0.93
7323 | 8.7 | 0.96
7324 | 8.9 | 0.97
7325 | 8.4 | 0.97
7326 | 8 | 0.96
7327 | 8.6 | 0.96
7328 | 9.9 | 0.95
7329 | 10.3 | 0.85
7330 | 10.3 | 0.88
7331 | 10.6 | 0.91
7332 | 10.3 | 0.9
7333 | 10 | 0.83
7334 | 9.6 | 0.82
7335 | 9.5 | 0.84
7336 | 9.5 | 0.82
7337 | 9.2 | 0.85
7338 | 8.9 | 0.81
7339 | 8.2 | 0.83
7340 | 7.1 | 0.87
7341 | 7.7 | 0.87
7342 | 7.8 | 0.9
7343 | 8.1 | 0.92
7344 | 8.6 | 0.9
7345 | 9.2 | 0.88
7346 | 8.8 | 0.92
7347 | 9.2 | 0.92
7348 | 9.4 | 0.96
7349 | 10 | 0.96
7350 | 10.4 | 0.94
7351 | 10.3 | 0.94
7352 | 10.2 | 0.95
7353 | 10.2 | 0.97
7354 | 10.5 | 0.92
7355 | 10.4 | 0.92
7356 | 10.7 | 0.9
7357 | 10.7 | 0.84
7358 | 11 | 0.74
7359 | 10.6 | 0.69
7360 | 10 | 0.72
7361 | 9.6 | 0.78
7362 | 8.8 | 0.86
7363 | 8.5 | 0.99
7364 | 7.8 | 0.93
7365 | 6.9 | 0.91
7366 | 6.2 | 0.95
7367 | 6.2 | 0.95
7368 | 6.2 | 0.95
7369 | 5.3 | 0.95
7370 | 5.5 | 0.95
7371 | 6.3 | 0.95
7372 | 6.2 | 0.95
7373 | 5.6 | 0.97
7374 | 5.8 | 0.97
7375 | 5.6 | 1
7376 | 5.5 | 0.98
7377 | 5.9 | 0.98
7378 | 5.9 | 0.95
7379 | 5.9 | 0.94
7380 | 7.3 | 0.88
7381 | 7.7 | 0.87
7382 | 8.2 | 0.83
7383 | 7.8 | 0.89
7384 | 7.8 | 0.93
7385 | 8.7 | 0.89
7386 | 9 | 0.89
7387 | 8.9 | 0.88
7388 | 8.9 | 0.85
7389 | 8.6 | 0.88
7390 | 8.2 | 0.89
7391 | 8.4 | 0.85
7392 | 8.1 | 0.87
7393 | 8.4 | 0.86
7394 | 8.5 | 0.86
7395 | 8.8 | 0.82
7396 | 8.9 | 0.84
7397 | 8.7 | 0.84
7398 | 8.6 | 0.82
7399 | 8.2 | 0.83
7400 | 7.8 | 0.83
7401 | 7.3 | 0.88
7402 | 8.1 | 0.87
7403 | 9.3 | 0.83
7404 | 9.8 | 0.8
7405 | 9.9 | 0.81
7406 | 11 | 0.73
7407 | 10.7 | 0.71
7408 | 10.5 | 0.68
7409 | 10.1 | 0.7
7410 | 9 | 0.75
7411 | 8.1 | 0.76
7412 | 7.2 | 0.77
7413 | 6.4 | 0.81
7414 | 6.5 | 0.87
7415 | 6.8 | 0.88
7416 | 6.6 | 0.9
7417 | 6.9 | 0.85
7418 | 6.6 | 0.84
7419 | 6.7 | 0.82
7420 | 6.3 | 0.88
7421 | 6.3 | 0.86
7422 | 6 | 0.89
7423 | 5.8 | 0.92
7424 | 5.8 | 0.95
7425 | 5.7 | 0.95
7426 | 6 | 0.95
7427 | 6.7 | 0.97
7428 | 7.5 | 0.96
7429 | 8.2 | 0.97
7430 | 8.5 | 0.99
7431 | 8.2 | 0.97
7432 | 8.4 | 0.79
7433 | 7.6 | 0.82
7434 | 6.6 | 0.87
7435 | 6 | 0.83
7436 | 5.5 | 0.81
7437 | 4.9 | 0.84
7438 | 4.7 | 0.84
7439 | 4.7 | 0.85
7440 | 2.7 | 0.91
7441 | 3.6 | 0.86
7442 | 2.6 | 0.89
7443 | 2.8 | 0.89
7444 | 3.7 | 0.88
7445 | 3.8 | 0.9
7446 | 3.6 | 0.91
7447 | 3.9 | 0.93
7448 | 4.3 | 0.93
7449 | 4.4 | 0.95
7450 | 4.3 | 0.95
7451 | 5.2 | 0.89
7452 | 5.5 | 0.87
7453 | 5 | 0.92
7454 | 5.9 | 0.88
7455 | 6.4 | 0.84
7456 | 6.4 | 0.79
7457 | 6.6 | 0.76
7458 | 6.5 | 0.78
7459 | 6.2 | 0.8
7460 | 6.4 | 0.81
7461 | 6.4 | 0.84
7462 | 6.3 | 0.85
7463 | 6.4 | 0.85
7464 | 6.3 | 0.86
7465 | 6 | 0.88
7466 | 5.3 | 0.91
7467 | 4.6 | 0.93
7468 | 4.2 | 0.93
7469 | 3.8 | 0.95
7470 | 3.5 | 0.97
7471 | 3.3 | 0.95
7472 | 3.2 | 0.95
7473 | 2.7 | 0.96
7474 | 3.6 | 0.93
7475 | 4.5 | 0.92
7476 | 5.9 | 0.83
7477 | 7.1 | 0.78
7478 | 8.9 | 0.69
7479 | 9.5 | 0.63
7480 | 9.8 | 0.64
7481 | 8 | 0.75
7482 | 5.6 | 0.86
7483 | 5 | 0.9
7484 | 5.1 | 0.9
7485 | 6 | 0.92
7486 | 5.8 | 0.94
7487 | 6.4 | 0.92
7488 | 6.8 | 0.93
7489 | 7.3 | 0.93
7490 | 7.7 | 0.94
7491 | 8.1 | 0.99
7492 | 8.1 | 0.92
7493 | 7.6 | 0.93
7494 | 6.6 | 0.81
7495 | 5.8 | 0.79
7496 | 5.1 | 0.9
7497 | 4.9 | 0.92
7498 | 4.4 | 0.9
7499 | 5.7 | 0.88
7500 | 7.6 | 0.77
7501 | 7.7 | 0.75
7502 | 8.1 | 0.72
7503 | 8.9 | 0.68
7504 | 8.2 | 0.7
7505 | 7.6 | 0.73
7506 | 7.2 | 0.77
7507 | 6.5 | 0.81
7508 | 5.9 | 0.88
7509 | 5.8 | 0.88
7510 | 5.8 | 0.85
7511 | 5.7 | 0.85
7512 | 5.5 | 0.83
7513 | 5.8 | 0.85
7514 | 5.2 | 0.87
7515 | 5.3 | 0.86
7516 | 4.8 | 0.87
7517 | 4.5 | 0.89
7518 | 3.7 | 0.9
7519 | 3.2 | 0.91
7520 | 3.1 | 0.93
7521 | 2.5 | 0.95
7522 | 3.4 | 0.91
7523 | 4.8 | 0.84
7524 | 6.4 | 0.78
7525 | 6.1 | 0.85
7526 | 6.3 | 0.91
7527 | 6.4 | 0.88
7528 | 6.8 | 0.82
7529 | 7.1 | 0.83
7530 | 7.1 | 0.88
7531 | 7.4 | 0.88
7532 | 7.1 | 0.94
7533 | 7.8 | 0.97
7534 | 8.3 | 1
7535 | 7.5 | 0.81
7536 | 6.9 | 0.77
7537 | 6.4 | 0.7
7538 | 5.8 | 0.71
7539 | 4.8 | 0.78
7540 | 4.6 | 0.82
7541 | 4.1 | 0.83
7542 | 4.7 | 0.79
7543 | 4.1 | 0.85
7544 | 4.5 | 0.82
7545 | 4.7 | 0.81
7546 | 4.9 | 0.84
7547 | 6.4 | 0.75
7548 | 5.5 | 0.83
7549 | 5.6 | 0.84
7550 | 6.5 | 0.84
7551 | 6.6 | 0.81
7552 | 6 | 0.86
7553 | 5.4 | 0.8
7554 | 5.1 | 0.83
7555 | 4.8 | 0.84
7556 | 4.6 | 0.82
7557 | 4.2 | 0.85
7558 | 4.9 | 0.81
7559 | 3.3 | 0.9
7560 | 3.9 | 0.85
7561 | 3.8 | 0.85
7562 | 3.8 | 0.83
7563 | 3.5 | 0.88
7564 | 3.6 | 0.85
7565 | 3.4 | 0.86
7566 | 3.6 | 0.83
7567 | 3.8 | 0.82
7568 | 3.5 | 0.83
7569 | 3.6 | 0.85
7570 | 4.3 | 0.8
7571 | 5.4 | 0.78
7572 | 6.6 | 0.75
7573 | 7.2 | 0.7
7574 | 7.7 | 0.64
7575 | 8.2 | 0.67
7576 | 7.7 | 0.71
7577 | 6.2 | 0.76
7578 | 5.4 | 0.8
7579 | 5.2 | 0.8
7580 | 4.9 | 0.81
7581 | 4.4 | 0.82
7582 | 5 | 0.79
7583 | 4.4 | 0.84
7584 | 4.2 | 0.84
7585 | 3.6 | 0.85
7586 | 4 | 0.85
7587 | 4.4 | 0.82
7588 | 4.1 | 0.83
7589 | 4.1 | 0.87
7590 | 3.7 | 0.9
7591 | 4.1 | 0.9
7592 | 3.7 | 0.92
7593 | 4.5 | 0.93
7594 | 5.3 | 0.94
7595 | 5.6 | 0.92
7596 | 3.1 | 0.95
7597 | 3.2 | 0.93
7598 | 5.3 | 0.81
7599 | 5.4 | 0.83
7600 | 3.1 | 0.88
7601 | 2.9 | 0.91
7602 | 2.9 | 0.91
7603 | 3.2 | 0.9
7604 | 3.5 | 0.9
7605 | 3.5 | 0.88
7606 | 3.2 | 0.9
7607 | 3.1 | 0.93
7608 | 2.5 | 0.95
7609 | 2.3 | 0.95
7610 | 1.8 | 0.94
7611 | 2.2 | 0.95
7612 | 4.5 | 0.89
7613 | 5.4 | 0.81
7614 | 4.8 | 0.82
7615 | 4 | 0.85
7616 | 3.7 | 0.85
7617 | 3.8 | 0.83
7618 | 3.8 | 0.82
7619 | 4.2 | 0.79
7620 | 4.9 | 0.75
7621 | 5.3 | 0.72
7622 | 5.7 | 0.67
7623 | 6 | 0.63
7624 | 6 | 0.61
7625 | 5.6 | 0.65
7626 | 4.8 | 0.7
7627 | 4.5 | 0.74
7628 | 4 | 0.75
7629 | 3.2 | 0.81
7630 | 2.8 | 0.82
7631 | 2.3 | 0.86
7632 | 2 | 0.85
7633 | 1.9 | 0.87
7634 | 1.8 | 0.87
7635 | 1.4 | 0.89
7636 | 1.4 | 0.89
7637 | 1.6 | 0.87
7638 | 1.6 | 0.85
7639 | 1.2 | 0.89
7640 | 1.4 | 0.87
7641 | 1.2 | 0.89
7642 | 2 | 0.85
7643 | 2.8 | 0.84
7644 | 3.9 | 0.8
7645 | 5 | 0.73
7646 | 6.1 | 0.67
7647 | 6.7 | 0.67
7648 | 6.6 | 0.66
7649 | 6.2 | 0.7
7650 | 5.2 | 0.76
7651 | 4.4 | 0.79
7652 | 4 | 0.78
7653 | 4.2 | 0.75
7654 | 3.5 | 0.78
7655 | 2.9 | 0.81
7656 | 2.6 | 0.82
7657 | 1.9 | 0.87
7658 | 1.8 | 0.89
7659 | 2.1 | 0.89
7660 | 2.1 | 0.89
7661 | 2 | 0.89
7662 | 1.7 | 0.91
7663 | 1.4 | 0.92
7664 | 1.4 | 0.92
7665 | 1.6 | 0.91
7666 | 1.7 | 0.93
7667 | 2.6 | 0.89
7668 | 3.9 | 0.85
7669 | 4.5 | 0.82
7670 | 5.1 | 0.83
7671 | 5.2 | 0.84
7672 | 5.3 | 0.84
7673 | 5.3 | 0.83
7674 | 5.3 | 0.64
7675 | 4.8 | 0.65
7676 | 5 | 0.69
7677 | 5 | 0.72
7678 | 4.2 | 0.87
7679 | 3.7 | 0.88
7680 | 3.4 | 0.81
7681 | 3.6 | 0.8
7682 | 3.5 | 0.8
7683 | 3.1 | 0.9
7684 | 3 | 0.89
7685 | 3.5 | 0.86
7686 | 3.3 | 0.86
7687 | 3.7 | 0.85
7688 | 3.9 | 0.92
7689 | 4.6 | 0.93
7690 | 5.1 | 0.95
7691 | 5.8 | 0.89
7692 | 6.4 | 0.86
7693 | 6.8 | 0.82
7694 | 5.9 | 0.83
7695 | 6.7 | 0.75
7696 | 6.6 | 0.78
7697 | 6.2 | 0.83
7698 | 6.3 | 0.8
7699 | 6.4 | 0.79
7700 | 6.3 | 0.79
7701 | 6 | 0.79
7702 | 5.8 | 0.77
7703 | 4.8 | 0.81
7704 | 3.3 | 0.88
7705 | 2.6 | 0.91
7706 | 2.7 | 0.89
7707 | 1.9 | 0.93
7708 | 1.8 | 0.93
7709 | 1.8 | 0.91
7710 | 1.6 | 0.93
7711 | 1.7 | 0.93
7712 | 1.2 | 0.92
7713 | 1.3 | 0.92
7714 | 3.5 | 0.85
7715 | 6.1 | 0.76
7716 | 6.1 | 0.85
7717 | 6.3 | 0.89
7718 | 6.3 | 0.91
7719 | 7.1 | 0.9
7720 | 7.4 | 0.9
7721 | 7 | 0.91
7722 | 7 | 0.93
7723 | 7.4 | 0.86
7724 | 7.6 | 0.87
7725 | 8 | 0.86
7726 | 8.1 | 0.81
7727 | 8 | 0.83
7728 | 8.3 | 0.81
7729 | 8.6 | 0.8
7730 | 8.6 | 0.78
7731 | 8.6 | 0.78
7732 | 8.9 | 0.86
7733 | 8.6 | 0.93
7734 | 8.7 | 0.93
7735 | 8.9 | 0.96
7736 | 8.2 | 0.99
7737 | 6.8 | 0.97
7738 | 5.4 | 0.95
7739 | 6.8 | 0.88
7740 | 8.8 | 0.81
7741 | 9.4 | 0.79
7742 | 9.4 | 0.78
7743 | 9.5 | 0.75
7744 | 9 | 0.8
7745 | 8.1 | 0.85
7746 | 7.3 | 0.9
7747 | 6.9 | 0.91
7748 | 7.4 | 0.88
7749 | 7 | 0.88
7750 | 6.8 | 0.91
7751 | 7.9 | 0.89
7752 | 7.9 | 0.89
7753 | 7.8 | 0.89
7754 | 7.7 | 0.89
7755 | 8 | 0.89
7756 | 8.2 | 0.9
7757 | 8.1 | 0.93
7758 | 8.5 | 0.9
7759 | 7.6 | 0.93
7760 | 8.3 | 0.96
7761 | 9 | 0.95
7762 | 7.1 | 0.97
7763 | 7.3 | 0.99
7764 | 7.7 | 0.96
7765 | 7.8 | 0.96
7766 | 7.5 | 0.97
7767 | 7.9 | 0.96
7768 | 7.6 | 0.99
7769 | 8.5 | 0.97
7770 | 7 | 0.99
7771 | 7.4 | 0.97
7772 | 7.4 | 0.97
7773 | 7.9 | 0.99
7774 | 8.4 | 0.99
7775 | 8.1 | 0.96
7776 | 7.9 | 0.96
7777 | 6.9 | 0.96
7778 | 6.8 | 0.99
7779 | 6.7 | 0.97
7780 | 7.1 | 0.97
7781 | 7 | 0.94
7782 | 7 | 0.94
7783 | 6.9 | 0.94
7784 | 6.8 | 0.96
7785 | 7.6 | 0.93
7786 | 7.9 | 0.91
7787 | 7.3 | 0.96
7788 | 7.6 | 0.96
7789 | 7.9 | 0.96
7790 | 7.7 | 0.96
7791 | 8.1 | 0.94
7792 | 7.8 | 0.91
7793 | 7.8 | 0.96
7794 | 7.5 | 0.97
7795 | 7.3 | 0.97
7796 | 6.9 | 0.93
7797 | 6.4 | 0.94
7798 | 6.2 | 0.95
7799 | 6.3 | 0.95
7800 | 6.4 | 0.95
7801 | 5.1 | 0.92
7802 | 6.1 | 0.97
7803 | 5.6 | 0.97
7804 | 5.5 | 0.97
7805 | 5.5 | 0.98
7806 | 5.3 | 0.98
7807 | 5 | 0.98
7808 | 4.3 | 0.98
7809 | 4 | 0.98
7810 | 4.3 | 0.98
7811 | 4.4 | 0.97
7812 | 4.6 | 0.97
7813 | 5.3 | 0.98
7814 | 6.4 | 0.95
7815 | 7.5 | 0.84
7816 | 6.9 | 0.84
7817 | 6.9 | 0.9
7818 | 6.3 | 0.92
7819 | 5.8 | 0.94
7820 | 5.8 | 0.94
7821 | 5.4 | 0.94
7822 | 5.4 | 0.95
7823 | 5.5 | 0.95
7824 | 5.4 | 0.95
7825 | 4.4 | 0.93
7826 | 4.1 | 0.97
7827 | 3.9 | 0.97
7828 | 4 | 0.97
7829 | 4 | 0.97
7830 | 4.1 | 0.97
7831 | 4.5 | 0.97
7832 | 4.6 | 0.93
7833 | 4.7 | 0.95
7834 | 5.1 | 0.94
7835 | 5.5 | 0.94
7836 | 6.1 | 0.95
7837 | 6.9 | 0.94
7838 | 7.1 | 0.94
7839 | 7.2 | 0.93
7840 | 7.4 | 0.93
7841 | 7.5 | 0.93
7842 | 7.4 | 0.93
7843 | 7.4 | 0.93
7844 | 7.2 | 0.93
7845 | 7.1 | 0.93
7846 | 6.9 | 0.93
7847 | 6.7 | 0.91
7848 | 6.1 | 0.92
7849 | 6 | 0.94
7850 | 6.2 | 0.91
7851 | 5.8 | 0.92
7852 | 5.6 | 0.92
7853 | 4.5 | 0.93
7854 | 4.2 | 0.97
7855 | 4.8 | 0.95
7856 | 5.5 | 0.95
7857 | 5.9 | 0.95
7858 | 6.4 | 0.94
7859 | 6.7 | 0.96
7860 | 7.9 | 0.93
7861 | 8.6 | 0.93
7862 | 8.4 | 0.96
7863 | 8.1 | 0.93
7864 | 8.3 | 0.96
7865 | 8.3 | 0.94
7866 | 8.3 | 0.96
7867 | 8.8 | 0.96
7868 | 9.1 | 0.97
7869 | 9.6 | 0.99
7870 | 9.9 | 0.99
7871 | 10.1 | 1
7872 | 10.3 | 1
7873 | 10.4 | 1
7874 | 10.3 | 0.99
7875 | 10.3 | 1
7876 | 10.1 | 0.99
7877 | 10.1 | 0.99
7878 | 10.1 | 0.99
7879 | 10.1 | 0.99
7880 | 10.1 | 1
7881 | 10 | 1
7882 | 10 | 0.99
7883 | 10.2 | 0.99
7884 | 10.2 | 0.99
7885 | 10.4 | 0.99
7886 | 10.7 | 0.95
7887 | 10.9 | 0.91
7888 | 10.3 | 0.88
7889 | 9.3 | 0.91
7890 | 8.4 | 0.96
7891 | 8.4 | 0.97
7892 | 7 | 0.97
7893 | 7.2 | 0.97
7894 | 7.9 | 0.97
7895 | 7.4 | 0.96
7896 | 7.7 | 0.96
7897 | 8.7 | 0.97
7898 | 8.8 | 0.97
7899 | 8.9 | 0.97
7900 | 8.6 | 0.97
7901 | 8.3 | 0.97
7902 | 8.3 | 0.97
7903 | 8.9 | 0.97
7904 | 10.3 | 0.99
7905 | 10.6 | 0.99
7906 | 10.4 | 0.99
7907 | 10.1 | 0.99
7908 | 9.8 | 0.96
7909 | 9.6 | 0.91
7910 | 9.5 | 0.91
7911 | 9.3 | 0.89
7912 | 8.6 | 0.94
7913 | 8.4 | 0.94
7914 | 8.1 | 0.96
7915 | 8.1 | 0.97
7916 | 8.3 | 0.99
7917 | 8.4 | 0.99
7918 | 8.5 | 0.99
7919 | 8.8 | 1
7920 | 8.9 | 0.99
7921 | 8.9 | 0.99
7922 | 8.9 | 0.99
7923 | 8.4 | 0.99
7924 | 8.1 | 1
7925 | 7.6 | 0.99
7926 | 7.2 | 0.99
7927 | 7 | 0.97
7928 | 6.9 | 0.99
7929 | 6.9 | 0.97
7930 | 7.1 | 0.93
7931 | 7.5 | 0.91
7932 | 7.9 | 0.83
7933 | 7.6 | 0.87
7934 | 8.1 | 0.87
7935 | 8 | 0.87
7936 | 8.1 | 0.89
7937 | 8.1 | 0.89
7938 | 7.7 | 0.9
7939 | 7.3 | 0.93
7940 | 6.9 | 0.94
7941 | 6.6 | 0.94
7942 | 6.1 | 0.94
7943 | 6.3 | 0.91
7944 | 6.6 | 0.95
7945 | 7 | 0.96
7946 | 7.1 | 0.97
7947 | 7.3 | 0.99
7948 | 7.6 | 0.99
7949 | 7.6 | 0.97
7950 | 7.6 | 0.96
7951 | 7.5 | 0.94
7952 | 7.6 | 0.93
7953 | 7.4 | 0.94
7954 | 7.9 | 0.91
7955 | 8.2 | 0.92
7956 | 8.6 | 0.9
7957 | 9.1 | 0.88
7958 | 9.2 | 0.91
7959 | 9.4 | 0.88
7960 | 9.4 | 0.83
7961 | 8.4 | 0.9
7962 | 8 | 0.92
7963 | 8 | 0.9
7964 | 7.9 | 0.91
7965 | 7.3 | 0.94
7966 | 6.8 | 0.97
7967 | 7.1 | 0.96
7968 | 7.2 | 0.96
7969 | 7.1 | 0.94
7970 | 7.2 | 0.94
7971 | 7 | 0.94
7972 | 7 | 0.91
7973 | 6.9 | 0.91
7974 | 6.8 | 0.91
7975 | 6.7 | 0.9
7976 | 6.7 | 0.88
7977 | 6.5 | 0.87
7978 | 6.2 | 0.83
7979 | 6.4 | 0.84
7980 | 7 | 0.85
7981 | 7.5 | 0.86
7982 | 7.4 | 0.87
7983 | 7.5 | 0.87
7984 | 7.9 | 0.84
7985 | 7.7 | 0.86
7986 | 7.6 | 0.87
7987 | 7.8 | 0.83
7988 | 7.8 | 0.79
7989 | 7.8 | 0.8
7990 | 8 | 0.86
7991 | 8 | 0.79
7992 | 7.9 | 0.82
7993 | 7.7 | 0.9
7994 | 8.2 | 0.86
7995 | 9 | 0.89
7996 | 8.8 | 0.88
7997 | 8.9 | 0.89
7998 | 9.2 | 0.89
7999 | 9.4 | 0.89
8000 | 9.5 | 0.91
8001 | 9.3 | 0.92
8002 | 9.4 | 0.89
8003 | 9.2 | 0.89
8004 | 9.2 | 0.89
8005 | 9.1 | 0.89
8006 | 8.9 | 0.89
8007 | 8.7 | 0.9
8008 | 8.8 | 0.89
8009 | 8.4 | 0.89
8010 | 8.3 | 0.87
8011 | 8 | 0.87
8012 | 7.7 | 0.89
8013 | 7.4 | 0.88
8014 | 7.4 | 0.87
8015 | 7.2 | 0.85
8016 | 7.1 | 0.84
8017 | 7 | 0.82
8018 | 6.5 | 0.87
8019 | 5.4 | 0.89
8020 | 4.3 | 0.92
8021 | 4.6 | 0.9
8022 | 4.9 | 0.89
8023 | 3.9 | 0.92
8024 | 2.9 | 0.95
8025 | 2.2 | 0.96
8026 | 2 | 0.96
8027 | 3.3 | 0.86
8028 | 4.4 | 0.82
8029 | 5 | 0.81
8030 | 5.6 | 0.75
8031 | 6.1 | 0.76
8032 | 5.6 | 0.8
8033 | 5.2 | 0.83
8034 | 4.2 | 0.85
8035 | 3.2 | 0.86
8036 | 2.7 | 0.89
8037 | 2.4 | 0.86
8038 | 2.5 | 0.84
8039 | 2.2 | 0.87
8040 | 2.2 | 0.87
8041 | 1.8 | 0.93
8042 | 1.4 | 0.94
8043 | 1.2 | 0.94
8044 | 0.9 | 0.94
8045 | 0.8 | 0.94
8046 | 0.8 | 0.92
8047 | 0.8 | 0.94
8048 | 0.8 | 0.92
8049 | 1 | 0.9
8050 | 2.1 | 0.85
8051 | 2.6 | 0.84
8052 | 4.4 | 0.77
8053 | 4.8 | 0.71
8054 | 6.2 | 0.72
8055 | 6.2 | 0.69
8056 | 6.8 | 0.71
8057 | 5 | 0.83
8058 | 4 | 0.87
8059 | 3.7 | 0.9
8060 | 2.1 | 0.91
8061 | 3.3 | 0.91
8062 | 2.7 | 0.91
8063 | 3.4 | 0.88
8064 | 4.4 | 0.87
8065 | 3 | 0.91
8066 | 2.4 | 0.91
8067 | 2.8 | 0.91
8068 | 3.2 | 0.91
8069 | 4 | 0.92
8070 | 4.1 | 0.92
8071 | 4.5 | 0.9
8072 | 5 | 0.89
8073 | 5.1 | 0.9
8074 | 5.4 | 0.89
8075 | 6.5 | 0.85
8076 | 7.1 | 0.83
8077 | 7.4 | 0.81
8078 | 7.6 | 0.79
8079 | 7.7 | 0.79
8080 | 7.7 | 0.8
8081 | 7.2 | 0.81
8082 | 6.9 | 0.82
8083 | 7.5 | 0.8
8084 | 7.7 | 0.76
8085 | 7.7 | 0.79
8086 | 7.7 | 0.8
8087 | 7.9 | 0.8
8088 | 8 | 0.8
8089 | 8.3 | 0.81
8090 | 8.3 | 0.79
8091 | 8.3 | 0.78
8092 | 8.4 | 0.82
8093 | 8.3 | 0.82
8094 | 8.3 | 0.82
8095 | 7.8 | 0.87
8096 | 8.2 | 0.85
8097 | 7.6 | 0.94
8098 | 7.8 | 0.97
8099 | 8.1 | 0.97
8100 | 8.6 | 0.99
8101 | 8.9 | 0.96
8102 | 9.2 | 0.8
8103 | 10.2 | 0.76
8104 | 9.7 | 0.77
8105 | 8.7 | 0.78
8106 | 7.5 | 0.73
8107 | 6.5 | 0.76
8108 | 5.7 | 0.82
8109 | 4.5 | 0.85
8110 | 3.4 | 0.91
8111 | 3.6 | 0.91
8112 | 3.6 | 0.93
8113 | 3.3 | 0.97
8114 | 5.1 | 0.92
8115 | 4.5 | 0.95
8116 | 4.3 | 0.93
8117 | 5.5 | 0.92
8118 | 5.5 | 0.91
8119 | 6.8 | 0.9
8120 | 7.5 | 0.9
8121 | 8.1 | 0.9
8122 | 8.2 | 0.93
8123 | 8.3 | 0.97
8124 | 8.9 | 0.97
8125 | 9.3 | 0.97
8126 | 9.9 | 0.97
8127 | 10.5 | 0.97
8128 | 10.7 | 0.97
8129 | 10.9 | 0.95
8130 | 10.8 | 0.94
8131 | 10.8 | 0.94
8132 | 10.8 | 0.95
8133 | 10.9 | 0.95
8134 | 11.1 | 0.96
8135 | 11.1 | 0.96
8136 | 11.1 | 0.97
8137 | 10.9 | 0.97
8138 | 11 | 0.97
8139 | 11.1 | 0.96
8140 | 11.1 | 0.97
8141 | 11.1 | 0.92
8142 | 10.4 | 0.95
8143 | 9.8 | 0.83
8144 | 9.9 | 0.92
8145 | 10 | 0.95
8146 | 9.9 | 0.87
8147 | 9.5 | 0.89
8148 | 10.6 | 0.74
8149 | 10 | 0.74
8150 | 10.1 | 0.73
8151 | 9.5 | 0.82
8152 | 10.1 | 0.73
8153 | 9.4 | 0.75
8154 | 9.1 | 0.73
8155 | 8.5 | 0.82
8156 | 7.3 | 0.84
8157 | 6.8 | 0.85
8158 | 6.2 | 0.86
8159 | 5.3 | 0.91
8160 | 5.3 | 0.92
8161 | 6.1 | 0.91
8162 | 6 | 0.92
8163 | 5.9 | 0.94
8164 | 6.5 | 0.92
8165 | 6.8 | 0.94
8166 | 4.9 | 0.98
8167 | 7 | 0.97
8168 | 6.7 | 0.96
8169 | 8 | 0.97
8170 | 8.1 | 0.99
8171 | 8.6 | 0.97
8172 | 8.9 | 0.96
8173 | 9.5 | 0.97
8174 | 9.4 | 0.99
8175 | 9.2 | 0.96
8176 | 9.2 | 0.96
8177 | 9.2 | 0.99
8178 | 9.3 | 0.95
8179 | 9.6 | 0.99
8180 | 10.3 | 0.99
8181 | 11.2 | 0.97
8182 | 11.7 | 0.98
8183 | 12.2 | 0.95
8184 | 11 | 0.75
8185 | 9.4 | 0.76
8186 | 8.9 | 0.72
8187 | 8.6 | 0.72
8188 | 7.9 | 0.72
8189 | 7.2 | 0.77
8190 | 6.4 | 0.85
8191 | 5.5 | 0.83
8192 | 6.1 | 0.77
8193 | 6.4 | 0.73
8194 | 5.8 | 0.8
8195 | 5.2 | 0.81
8196 | 6.3 | 0.76
8197 | 7.6 | 0.66
8198 | 7.1 | 0.68
8199 | 5.6 | 0.78
8200 | 6.4 | 0.79
8201 | 5.8 | 0.85
8202 | 6.2 | 0.85
8203 | 6.7 | 0.9
8204 | 6.7 | 0.82
8205 | 7.2 | 0.74
8206 | 7.6 | 0.76
8207 | 8.1 | 0.72
8208 | 7.8 | 0.73
8209 | 8.2 | 0.71
8210 | 8.3 | 0.67
8211 | 8 | 0.71
8212 | 8.1 | 0.7
8213 | 7.8 | 0.71
8214 | 7.2 | 0.74
8215 | 7.1 | 0.74
8216 | 7 | 0.75
8217 | 7.1 | 0.74
8218 | 7.3 | 0.74
8219 | 7 | 0.8
8220 | 7.8 | 0.75
8221 | 8.5 | 0.71
8222 | 9.1 | 0.71
8223 | 9.5 | 0.7
8224 | 8.8 | 0.73
8225 | 6.2 | 0.83
8226 | 4.4 | 0.89
8227 | 5.4 | 0.89
8228 | 5 | 0.95
8229 | 6.2 | 0.95
8230 | 7.1 | 0.93
8231 | 8.2 | 0.89
8232 | 8.5 | 0.89
8233 | 8.7 | 0.89
8234 | 8.6 | 0.96
8235 | 9 | 0.97
8236 | 9.6 | 0.99
8237 | 10.2 | 0.99
8238 | 10.8 | 1
8239 | 11.1 | 1
8240 | 11.6 | 0.99
8241 | 11.4 | 0.99
8242 | 11.4 | 1
8243 | 11.7 | 1
8244 | 11.8 | 0.98
8245 | 11.7 | 0.98
8246 | 7.8 | 0.86
8247 | 7.3 | 0.81
8248 | 6.5 | 0.84
8249 | 6.1 | 0.77
8250 | 5.2 | 0.76
8251 | 4.4 | 0.77
8252 | 4.3 | 0.82
8253 | 4.5 | 0.81
8254 | 3.4 | 0.86
8255 | 3 | 0.88
8256 | 3.2 | 0.91
8257 | 3.4 | 0.88
8258 | 3.6 | 0.85
8259 | 3.5 | 0.9
8260 | 2.9 | 0.91
8261 | 3.3 | 0.9
8262 | 2.9 | 0.91
8263 | 3 | 0.88
8264 | 2.3 | 0.93
8265 | 2.4 | 0.93
8266 | 2.2 | 0.87
8267 | 2.7 | 0.86
8268 | 3.4 | 0.83
8269 | 3.9 | 0.8
8270 | 4.5 | 0.81
8271 | 5.4 | 0.72
8272 | 4.9 | 0.76
8273 | 2.8 | 0.84
8274 | 2 | 0.87
8275 | 1.4 | 0.89
8276 | 1.7 | 0.87
8277 | 2 | 0.87
8278 | 2.5 | 0.89
8279 | 3.9 | 0.9
8280 | 4.5 | 0.97
8281 | 6.1 | 0.97
8282 | 7 | 0.97
8283 | 7.3 | 0.99
8284 | 7.2 | 0.99
8285 | 8.3 | 0.99
8286 | 8.7 | 0.99
8287 | 8.5 | 0.94
8288 | 8.1 | 0.96
8289 | 7.1 | 0.9
8290 | 7.2 | 0.94
8291 | 8 | 0.87
8292 | 8.4 | 0.88
8293 | 9.1 | 0.8
8294 | 9.4 | 0.78
8295 | 8.5 | 0.86
8296 | 8.3 | 0.92
8297 | 8.1 | 0.94
8298 | 8.2 | 0.87
8299 | 7.2 | 0.81
8300 | 6.9 | 0.82
8301 | 6.3 | 0.75
8302 | 5.9 | 0.73
8303 | 4.9 | 0.81
8304 | 5.4 | 0.69
8305 | 4.3 | 0.79
8306 | 4.3 | 0.76
8307 | 4.2 | 0.77
8308 | 4 | 0.78
8309 | 3.6 | 0.81
8310 | 3.5 | 0.83
8311 | 3.5 | 0.8
8312 | 4.1 | 0.74
8313 | 4 | 0.74
8314 | 4.3 | 0.74
8315 | 4.5 | 0.76
8316 | 6.3 | 0.67
8317 | 6.3 | 0.72
8318 | 7.2 | 0.7
8319 | 6.9 | 0.75
8320 | 5.6 | 0.89
8321 | 5.2 | 0.95
8322 | 5.1 | 0.97
8323 | 4.7 | 0.97
8324 | 4.2 | 0.93
8325 | 4.9 | 0.92
8326 | 4.7 | 0.89
8327 | 4.8 | 0.87
8328 | 3.9 | 0.85
8329 | 4.3 | 0.74
8330 | 4.6 | 0.71
8331 | 3.8 | 0.77
8332 | 4.4 | 0.72
8333 | 3.3 | 0.83
8334 | 3.5 | 0.88
8335 | 3.3 | 0.78
8336 | 1.7 | 0.85
8337 | 2.5 | 0.72
8338 | 2.7 | 0.75
8339 | 3.5 | 0.71
8340 | 5.2 | 0.66
8341 | 5.5 | 0.68
8342 | 5.1 | 0.55
8343 | 2 | 0.89
8344 | 1.2 | 0.98
8345 | 0.6 | 0.98
8346 | 0.6 | 0.96
8347 | 1.4 | 0.98
8348 | 2.3 | 0.95
8349 | 1.2 | 0.94
8350 | 1.8 | 0.93
8351 | 2.1 | 0.91
8352 | 2.4 | 0.82
8353 | 2.3 | 0.8
8354 | 2.4 | 0.82
8355 | 1.9 | 0.82
8356 | 2.6 | 0.72
8357 | 2.5 | 0.72
8358 | 1.7 | 0.8
8359 | 1.4 | 0.91
8360 | 1.3 | 0.92
8361 | 2.3 | 0.89
8362 | 2.5 | 0.91
8363 | 3.1 | 0.93
8364 | 3.7 | 0.9
8365 | 2.9 | 0.91
8366 | 3.6 | 0.86
8367 | 3.9 | 0.87
8368 | 5.1 | 0.89
8369 | 5.4 | 0.86
8370 | 5.4 | 0.71
8371 | 4.7 | 0.76
8372 | 5.1 | 0.79
8373 | 5.2 | 0.75
8374 | 4.8 | 0.78
8375 | 4.2 | 0.85
8376 | 3.8 | 0.88
8377 | 3.3 | 0.86
8378 | 2.9 | 0.84
8379 | 1.5 | 0.89
8380 | 2.3 | 0.89
8381 | 2.3 | 0.87
8382 | 2.4 | 0.86
8383 | 1.2 | 0.89
8384 | 2.7 | 0.91
8385 | 2.7 | 0.86
8386 | 2.1 | 0.89
8387 | 2.7 | 0.86
8388 | 3.9 | 0.8
8389 | 4.9 | 0.81
8390 | 5.1 | 0.75
8391 | 5.5 | 0.75
8392 | 5.3 | 0.74
8393 | 4.2 | 0.8
8394 | 3.3 | 0.85
8395 | 3.2 | 0.84
8396 | 2.6 | 0.88
8397 | 2.5 | 0.84
8398 | 2.2 | 0.86
8399 | 2.2 | 0.86
8400 | 1.7 | 0.87
8401 | 1.8 | 0.87
8402 | 1 | 0.88
8403 | 1.1 | 0.9
8404 | 1.8 | 0.89
8405 | 1.4 | 0.89
8406 | 2.1 | 0.84
8407 | 2.5 | 0.82
8408 | 1.1 | 0.89
8409 | 2.3 | 0.86
8410 | 2.8 | 0.86
8411 | 1.7 | 0.85
8412 | 4.3 | 0.82
8413 | 4.7 | 0.84
8414 | 5.9 | 0.79
8415 | 6.1 | 0.74
8416 | 6.2 | 0.79
8417 | 3 | 0.91
8418 | 3.1 | 0.91
8419 | 3.4 | 0.93
8420 | 3.6 | 0.91
8421 | 2.6 | 0.91
8422 | 2.8 | 0.86
8423 | 3.1 | 0.83
8424 | 3.8 | 0.82
8425 | 4.4 | 0.8
8426 | 5.4 | 0.81
8427 | 5.6 | 0.8
8428 | 6.4 | 0.84
8429 | 7.3 | 0.83
8430 | 7.9 | 0.84
8431 | 7.8 | 0.97
8432 | 8.6 | 0.99
8433 | 9.1 | 0.97
8434 | 9.2 | 0.99
8435 | 9.5 | 0.99
8436 | 9.6 | 0.99
8437 | 9.6 | 0.99
8438 | 9.6 | 0.99
8439 | 9.5 | 0.97
8440 | 9.6 | 0.99
8441 | 10.3 | 0.99
8442 | 11 | 0.95
8443 | 10.7 | 0.87
8444 | 8.7 | 0.94
8445 | 8.6 | 0.85
8446 | 8.3 | 0.92
8447 | 8.4 | 0.85
8448 | 8.3 | 0.87
8449 | 8.6 | 0.89
8450 | 8.6 | 0.92
8451 | 8.2 | 0.92
8452 | 8.6 | 0.94
8453 | 8.6 | 0.93
8454 | 8.7 | 0.96
8455 | 8.9 | 0.96
8456 | 8.6 | 0.93
8457 | 8.2 | 0.9
8458 | 8.4 | 0.94
8459 | 7.8 | 0.93
8460 | 8.8 | 0.96
8461 | 8.8 | 0.9
8462 | 8.1 | 0.94
8463 | 8.2 | 0.96
8464 | 8 | 0.97
8465 | 7.9 | 0.97
8466 | 7.6 | 0.99
8467 | 7.2 | 0.97
8468 | 6.4 | 0.95
8469 | 6.3 | 0.94
8470 | 6.1 | 0.97
8471 | 6.1 | 0.98
8472 | 6 | 0.98
8473 | 4.5 | 1
8474 | 4.6 | 0.97
8475 | 4.3 | 0.98
8476 | 2.9 | 0.98
8477 | 3.4 | 0.98
8478 | 1.7 | 0.98
8479 | 1.2 | 0.98
8480 | 0.9 | 0.98
8481 | 2.6 | 0.96
8482 | 2.6 | 1
8483 | 3.9 | 0.98
8484 | 6 | 0.98
8485 | 5.8 | 0.98
8486 | 6.1 | 0.97
8487 | 6.5 | 0.94
8488 | 6.1 | 0.95
8489 | 5.8 | 0.95
8490 | 4.6 | 0.97
8491 | 5.1 | 0.98
8492 | 4.6 | 0.97
8493 | 5.7 | 0.97
8494 | 5.5 | 0.95
8495 | 6.5 | 0.94
8496 | 5.7 | 0.95
8497 | 5.3 | 0.95
8498 | 4.1 | 0.97
8499 | 3.7 | 0.98
8500 | 4.4 | 0.97
8501 | 3.5 | 0.97
8502 | 3 | 0.95
8503 | 3.7 | 0.93
8504 | 2.9 | 0.95
8505 | 4.2 | 0.92
8506 | 2.7 | 0.95
8507 | 3.4 | 0.95
8508 | 3.8 | 0.97
8509 | 3.8 | 0.97
8510 | 4.7 | 0.98
8511 | 5.1 | 0.98
8512 | 5.6 | 0.98
8513 | 5.5 | 1
8514 | 4.8 | 0.97
8515 | 4.2 | 0.98
8516 | 4.4 | 0.98
8517 | 4.1 | 0.98
8518 | 3.8 | 0.98
8519 | 4.2 | 0.95
8520 | 4.5 | 0.9
8521 | 4.7 | 0.92
8522 | 4.4 | 0.92
8523 | 4.9 | 0.94
8524 | 4.3 | 0.93
8525 | 3.4 | 0.95
8526 | 4.2 | 0.93
8527 | 4.3 | 0.95
8528 | 4 | 0.95
8529 | 4 | 0.95
8530 | 4.4 | 0.93
8531 | 4.3 | 0.95
8532 | 6.8 | 0.9
8533 | 8 | 0.86
8534 | 8.1 | 0.81
8535 | 8.5 | 0.78
8536 | 7.5 | 0.86
8537 | 7.4 | 0.84
8538 | 6.4 | 0.86
8539 | 5.9 | 0.88
8540 | 6.6 | 0.9
8541 | 6.7 | 0.82
8542 | 6 | 0.88
8543 | 6.2 | 0.85
8544 | 5.9 | 0.86
8545 | 5.5 | 0.86
8546 | 5.7 | 0.86
8547 | 6.1 | 0.86
8548 | 5.2 | 0.89
8549 | 6 | 0.86
8550 | 5.1 | 0.87
8551 | 4.1 | 0.9
8552 | 5 | 0.86
8553 | 4.1 | 0.9
8554 | 4.5 | 0.89
8555 | 5.2 | 0.87
8556 | 5.6 | 0.91
8557 | 6.1 | 0.89
8558 | 6.5 | 0.91
8559 | 7.7 | 0.87
8560 | 7 | 0.91
8561 | 6.6 | 0.9
8562 | 6.3 | 0.91
8563 | 6.2 | 0.83
8564 | 5.1 | 0.89
8565 | 5.5 | 0.91
8566 | 5.8 | 0.98
8567 | 6.9 | 0.99
8568 | 6.9 | 0.99
8569 | 7.4 | 0.97
8570 | 8 | 0.94
8571 | 8.8 | 0.93
8572 | 8.4 | 0.9
8573 | 6.6 | 0.94
8574 | 6.8 | 0.94
8575 | 7.7 | 0.91
8576 | 7.6 | 0.87
8577 | 6.9 | 0.94
8578 | 7.1 | 0.94
8579 | 7.5 | 0.93
8580 | 8.5 | 0.86
8581 | 8.9 | 0.84
8582 | 9.1 | 0.84
8583 | 8.2 | 0.79
8584 | 7.3 | 0.8
8585 | 6.5 | 0.81
8586 | 6.3 | 0.8
8587 | 5.6 | 0.83
8588 | 4.9 | 0.87
8589 | 4.9 | 0.87
8590 | 5.3 | 0.83
8591 | 4.9 | 0.84
8592 | 4 | 0.87
8593 | 4 | 0.85
8594 | 3.8 | 0.85
8595 | 4.2 | 0.84
8596 | 4 | 0.85
8597 | 3 | 0.86
8598 | 2.7 | 0.89
8599 | 2.8 | 0.89
8600 | 1.9 | 0.93
8601 | 3.1 | 0.9
8602 | 2.9 | 0.89
8603 | 4 | 0.85
8604 | 4.7 | 0.92
8605 | 6.3 | 0.86
8606 | 6.9 | 0.84
8607 | 7.1 | 0.83
8608 | 7.3 | 0.81
8609 | 7.4 | 0.84
8610 | 7.4 | 0.81
8611 | 7.5 | 0.86
8612 | 7.8 | 0.87
8613 | 8 | 0.86
8614 | 8.1 | 0.89
8615 | 8.4 | 0.9
8616 | 8.7 | 0.92
8617 | 8.8 | 0.95
8618 | 8.9 | 0.95
8619 | 8.8 | 0.96
8620 | 8.9 | 0.97
8621 | 9.1 | 0.99
8622 | 8 | 0.96
8623 | 7.9 | 0.99
8624 | 8 | 0.97
8625 | 7.8 | 0.94
8626 | 8 | 0.96
8627 | 8.5 | 0.92
8628 | 9 | 0.88
8629 | 9.6 | 0.95
8630 | 10 | 0.96
8631 | 10.1 | 0.97
8632 | 10.6 | 0.99
8633 | 11.2 | 0.97
8634 | 11.3 | 0.95
8635 | 11.6 | 0.93
8636 | 11.4 | 0.95
8637 | 11.3 | 0.95
8638 | 11.3 | 0.96
8639 | 11.2 | 0.97
8640 | 11 | 0.97
8641 | 10.9 | 0.99
8642 | 10.9 | 0.99
8643 | 10.9 | 0.99
8644 | 10.6 | 0.99
8645 | 10.5 | 0.99
8646 | 10.3 | 0.99
8647 | 10.3 | 0.99
8648 | 10.2 | 0.99
8649 | 10.2 | 0.99
8650 | 10.2 | 0.99
8651 | 10.4 | 0.99
8652 | 10.4 | 1
8653 | 10.4 | 0.99
8654 | 10.3 | 0.99
8655 | 10.5 | 0.99
8656 | 10.4 | 0.99
8657 | 10.2 | 1
8658 | 10.1 | 1
8659 | 10 | 1
8660 | 9.7 | 0.97
8661 | 9.6 | 0.97
8662 | 9.4 | 0.96
8663 | 9.3 | 0.96
8664 | 9.1 | 0.96
8665 | 8.9 | 0.96
8666 | 9 | 0.92
8667 | 8.9 | 0.93
8668 | 8.9 | 0.93
8669 | 9 | 0.93
8670 | 9.1 | 0.93
8671 | 9.1 | 0.93
8672 | 9.2 | 0.92
8673 | 9.3 | 0.93
8674 | 9.4 | 0.91
8675 | 9.4 | 0.91
8676 | 9.8 | 0.91
8677 | 9.9 | 0.92
8678 | 9.9 | 0.91
8679 | 9.8 | 0.91
8680 | 9.8 | 0.93
8681 | 9.7 | 0.95
8682 | 9.6 | 0.93
8683 | 9.5 | 0.95
8684 | 9.4 | 0.96
8685 | 9.3 | 0.96
8686 | 9.4 | 0.97
8687 | 9.4 | 0.97
8688 | 9.4 | 0.99
8689 | 9.4 | 0.99
8690 | 9.3 | 0.96
8691 | 9.4 | 0.95
8692 | 9.4 | 0.95
8693 | 9.4 | 0.95
8694 | 9.4 | 0.95
8695 | 9.3 | 0.95
8696 | 9.4 | 0.96
8697 | 9.4 | 0.95
8698 | 9.4 | 0.95
8699 | 9.5 | 0.96
8700 | 9.5 | 0.95
8701 | 9.5 | 0.96
8702 | 9.8 | 0.95
8703 | 9.8 | 0.95
8704 | 9.5 | 0.96
8705 | 9.1 | 0.96
8706 | 8.8 | 0.97
8707 | 8.6 | 0.99
8708 | 8.5 | 0.97
8709 | 8.4 | 0.99
8710 | 8.4 | 0.99
8711 | 8.3 | 0.99
8712 | 8.3 | 0.99
8713 | 8.1 | 0.99
8714 | 8.2 | 0.99
8715 | 8.3 | 0.99
8716 | 8.4 | 0.99
8717 | 8.4 | 1
8718 | 8.6 | 0.99
8719 | 8.8 | 0.99
8720 | 9.1 | 0.97
8721 | 9.2 | 0.96
8722 | 9.3 | 0.97
8723 | 9.6 | 0.96
8724 | 9.8 | 0.96
8725 | 9.9 | 0.95
8726 | 9.8 | 0.96
8727 | 9.7 | 0.97
8728 | 9.7 | 0.97
8729 | 9.5 | 0.99
8730 | 9.3 | 0.99
8731 | 9.3 | 0.97
8732 | 9.2 | 1
8733 | 9.1 | 0.99
8734 | 9.1 | 0.99
8735 | 9.1 | 0.99
8736 | 8.9 | 1
8737 | 8.7 | 0.99
8738 | 8.5 | 0.99
8739 | 8.3 | 0.97
8740 | 8.2 | 0.97
8741 | 7.9 | 0.97
8742 | 8 | 0.96
8743 | 8.1 | 0.96
8744 | 8.1 | 0.96
8745 | 8.1 | 0.97
8746 | 7.9 | 0.96
8747 | 8 | 0.96
8748 | 7.9 | 0.91
8749 | 7.9 | 0.91
8750 | 8.2 | 0.89
8751 | 8.2 | 0.89
8752 | 8 | 0.89
8753 | 7.8 | 0.89
8754 | 7.6 | 0.9
8755 | 7.3 | 0.91
8756 | 6.7 | 0.94
8757 | 6.1 | 0.95
8758 | 6 | 0.95
8759 | 5.8 | 0.95
8760 | 5.8 | 0.97